## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1212-ITP-023 Earthing & Bonding | itp |  |  |  |  | DN1212-ITP-023 Earthing & Bonding
section | 1.0 - OH &S
checkpoint | 1.1 - The following document is to be submitted for review/approval: Safe Work Method Statement (SWMS)
label | Application Std. & Acceptance Criteria - AS/NZS ISO 480-1-2001 & project OH&S Management Plan
label | Timing or Frequency - Prior to commencement
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - R
section | 2.0 - ENVIRONMENTAL
checkpoint | 2.1 - Environmental: Environmental Control Plan
label | Application Std. & Acceptance Criteria - AS/NZS ISO 14001-2000. Project Environmental Management Plan & Associated Sub-Plans.
label | Timing or Frequency - Continuous
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - R
section | 3.0 - MATERIAL RECEIPT
checkpoint | 3.1 - All major product items delivered to site shall be : Inspected on receipt then stored in designated area(s)
label | Application Std. & Acceptance Criteria - Construction Management Plan.
label | Timing or Frequency - On receipt & Continuous
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - W
section | 4.0 - BONDING INSTALLATION
checkpoint | 4.1 - Balustrade Guard Conductor to PET Equpotential Earth Bar 35 mm2 Cu cable bonds
label | Application Std. & Acceptance Criteria - IFC Bonding Plans; AKL Basic Design Drawings; Extraneous Bonding Layouts
label | Timing or Frequency - PET Cabinet Bonds
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - X
checkpoint | 4.2 - Girder to Girder Bonds 50 mm2 Cu cable bonds
label | Application Std. & Acceptance Criteria - IFC Bonding Plans; AKL Basic Design Drawings; Extraneous Bonding Layouts
label | Timing or Frequency - Girder Bonds
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - X
checkpoint | 4.3 - Balustrade Guard Conductor to Balustrade Guard Conductor Bond 35 mm2 Cu cable bonds
label | Application Std. & Acceptance Criteria - IFC Bonding Plans; AKL Basic Design Drawings; Extraneous Bonding Layouts
label | Timing or Frequency - Ballustrades Guard Conductor Bonds
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - X
checkpoint | 4.4 - Connections & Terminations
label | Application Std. & Acceptance Criteria - AKL Basic Design Drawings
label | Timing or Frequency - At Procurement
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - X
section | 5.0 - BONDING CONTINUITY TESTS
checkpoint | 5.1 - Ensure correct Contnuity tester is used. DLRO (Digital Low Resistance Ohmmeter).
label | Application Std. & Acceptance Criteria - E-SP-AE-61318 AEA Earthing and Bonding
label | ○ E-ST-AE-0101 AEA Earthing and Bonding Design Standards
label | Timing or Frequency - Prior to test
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - R
checkpoint | 5.2 - Ensure testing equipment is calibrated for use with photo evidence.
label | Application Std. & Acceptance Criteria - E-SP-AE-61318 AEA Earthing and Bonding
label | ○ E-ST-AE-0101 AEA Earthing and Bonding Design Standards
label | Timing or Frequency - Prior to test
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - R
checkpoint | 5.3 - Tests shall be conduted at 10 amps and readings should be less than 0.5 ohms.
label | Application Std. & Acceptance Criteria - ≤ 0.5 ohms, AS/NZS 3000:2007
label | Timing or Frequency - After Bonding
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - R
checkpoint | 5.4 - Record Test results on ITR Bonding testing sheet.
label | Application Std. & Acceptance Criteria - DNR-43032-NIMT-CHK-001-Rev0 - Homai Bonding Check Sheet
label | Timing or Frequency - After Bonding
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - R
label | Comments - Test Failed.
label | ○ Need to retest once mortar has cured
section | 6.0 - Insulation Resistance Tests
checkpoint | 6.1 - Insulation Resistance test between bridge screen and concrete barrier at 1000V DC to provied result greater than 1M ohm.
label | Application Std. & Acceptance Criteria - BECA-4323-10-HOMAI-RPT-001
label | Timing or Frequency - After Installation
label | Records & Remarks: Downer - W
label | Records & Remarks: Alpha Rail - R
checkpoint | 6.2 - Ensure testing equipment is calibrated for use with photo evidence.
label | Application Std. & Acceptance Criteria - E-SP-AE-61318 AEA Earthing and Bonding
label | ○ E-ST-AE-0101 AEA Earthing and Bonding Design Standards
label | Timing or Frequency - Prior to test
label | Records & Remarks: Downer - W
label | Records & Remarks: Alpha Rail - R
checkpoint | 6.3 - Record Test results on ITR Bonding testing sheet.
label | Application Std. & Acceptance Criteria - KR-43029-NAL-ITR-005-Rev0 - OLE Bonding Test Sheet
label | ○ KR-43029-NAL-ITR-028-Rev0 - OLE Bonding Check Sheet
label | Timing or Frequency - After Bonding
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - R
checkpoint | 6.4 - Record Test results on ITR Bonding testing sheet.
label | Application Std. & Acceptance Criteria - DNR-43032-NIMT-CHK-002-Rev0 - Homai IR Check Sheet
label | Timing or Frequency - After Bonding
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - R
section | 7.0 - AS CONSTRUCTED RECORDS
checkpoint | 7.1 - Relevant RFI(s).
label | Application Std. & Acceptance Criteria - All RFIs closed
label | Records & Remarks: Downer - R
label | Records & Remarks: Alpha Rail - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.2 - Snags
label | Application Std. & Acceptance Criteria - Snags to be rectified/addressed with evidence to be sent to engineer for confirmation to allow for close out
checkpoint | 7.3 - Record on Bonding Plans.
label | Application Std. & Acceptance Criteria - IFC Bonding Plans
label | Timing or Frequency - After Installation
label | Records & Remarks: Downer - W
label | Records & Remarks: Alpha Rail - W
checkpoint | 7.4 - COC issued no more than 20 days after works are completed.
label | Application Std. & Acceptance Criteria - AS/NZS 3000:2007
label | Timing or Frequency - After Installation
label | Records & Remarks: Downer - H
label | Records & Remarks: Alpha Rail - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.5 - ROI Issued no more than 20 working days after works completed.
label | Application Std. & Acceptance Criteria - AS/NZS 3000:2007
label | Timing or Frequency - After Installation
checkpoint | 7.6 - EAC part 1&2 signed 20 working days after works completed.
label | Application Std. & Acceptance Criteria - E-ST-AL-0183-FO EAC Certificate
label | Timing or Frequency - After Installation
section | ITP APPROVAL PROCESS
checkpoint-no-status | Works completed satisfactorily in accordance with relevant Sandards & Specifications as indicated above
label | Prepared by: Alan Twine
label | Approved by: Tab Kilisimasi
label | Distributed: Danny Cox
holdpoint | Signed on behalf of Installer : Alpha Rail
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature