## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | FHC-ITP-030 - DDA Compliant Hand Railing (Supply & Installation) | itp |  |  |  |  | FHC-ITP-030 - DDA Compliant Hand Railing (Supply & Installation) Rev 0
section | Preliminaries
checkpoint | 1.1 Railing Components - Proprietary System
label | REFERENCE: IFC Drawings
label | ○ Manufacturer's Drawings & Installation Recommendations
label | ○ Fulton Hogan Quality Management Plan
label | ACCEPTANCE CRITERIA: Where applicable, product to be selected based on the following criteria:
label | i. Certified or nominated as compliant to AS1428.1
label | ii. Able to be erected with top of hand rail between 865mm (min.) & 1000mm (max.)
label | iii. Extend beyond landings with rounded end or closed loop by 300mm (min.)
label | iv. Able to withstand the load conditions (where specified)
label | v. Have a protective coating that aligns with the atmosphere it will be erected in
label | ○ Details of the nominated proprietary system to be submitted for review to the Superintendent.
textbox | Enter: Teambinder Material Approval number
label | METHOD: Document Review
label | FREQUENCY: Each component
label | IP
label | RESPONSIBILITY: PE/SE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
checkpoint | 1.2 Railing Components - Fabricated System
label | REFERENCE: IFC Drawings
label | ○ Fulton Hogan Quality Management Plan
label | ACCEPTANCE CRITERIA: Fabricator is required to provide the Manufacturer's Data Record (MDR) for each component.
label | ○ Typically this consists of but is not limited to:
label | i. Certificate of Compliance
label | ii. Completed ITP
label | iii. Weld Procedure Specifications
label | iv. Weld Procedure Qualifications
label | v. Welder Qualifications
label | vi. Material Certificates and traceability
label | vii. Quality Assurance check sheets
label | viii. Welding Consumable batch certificates
label | ix. Coating certificate(s)
label | x. Non-destructive Testing (NDT) Reports
label | xi. As-built Drawings to demonstrate compliance with dimensional tolerances of structural steel
label | ○ Collate: Structural Steel Quality Assurance Documentation so it can be uploaded into Teambinder (don't attach it here)
label | METHOD: Document Review
label | FREQUENCY: Each component
label | IP
label | RESPONSIBILITY: PE/SE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
checkpoint | 1.3 Fixing Detail
label | REFERENCE: IFC Drawings
label | ○ Manufacturer's Drawings & Installation Recommendations
label | ACCEPTANCE CRITERIA: Fixing detail to be either positive connection via cast-in ferrules or similar.
label | ○ Changes to the approved Drawings shall be accompanied with a PE Certificate.
textbox | Enter: Teambinder Approval number
label | or
label | ○ Attach: PE Certificate of Compliance
label | METHOD: Document Review
label | FREQUENCY: Each component
label | IP
label | RESPONSIBILITY: PE/SE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
section | Pre-installation Activities
checkpoint | 2.1 IFC Drawings
label | REFERENCE: Fulton Hogan Quality Management Plan
label | ACCEPTANCE CRITERIA: Check the revision of the IFC drawings are current as per the drawing register (on Teambinder)
label | METHOD: Document Review
label | FREQUENCY: Prior to starting Works and at regular intervals
label | HP*
label | RESPONSIBILITY: All
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
checkpoint | 2.2 Materials Inspection Checklist
label | REFERENCE: IFC Drawings
label | ○ Fulton Hogan Quality Management Plan
label | ACCEPTANCE CRITERIA: General inspection of railing components for defects including cracks, handling and storage damage & distortion.
label | ○ Bolts, nuts and washers shall be the size, material, strength grade and coating as noted on the IFC Drawings.
label | ○ Galvanised coating - no loss of adhesion, damage, blisters, roughness, sharp points and flux residues.
label | ○ Complete: Materials Inspection Checklist in ConQA
label | METHOD: Measure, Visual
label | FREQUENCY: Each component
label | IP
label | RESPONSIBILITY: SE/PE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
section | Installation Activities
checkpoint | 3.1 Bearing / Mounting Surface Preparation
label | REFERENCE: Manufacturer's Drawings & Installation Recommendations
label | ACCEPTANCE CRITERIA: As a minimum, ensure that the bearing surface is clean and free from loose particles and laitance.
label | METHOD: Visual
label | FREQUENCY: Each post location
label | IP
label | RESPONSIBILITY: SE/PE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
checkpoint | 3.2 Railing Handling
label | REFERENCE: Manufacturer's Drawings & Installation Recommendations
label | ACCEPTANCE CRITERIA: The method of handling and erection of the railing shall ensure that the components are not stressed or deformed beyond the design limit and that there is no damage to the protective coating during these operations.
label | ○ Where damage exists, it shall be repaired using an approved repair procedure for both steelwork and coatings.
label | METHOD: Visual
label | FREQUENCY: Each component
label | IP
label | RESPONSIBILITY: SE/PE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
checkpoint | 3.3 Railing Erection
label | REFERENCE: Manufacturer's Drawings & Installation Recommendations
label | ○ AS4100, Clause 15.2
label | ○ AS4100, Clause 15.3
label | ACCEPTANCE CRITERIA: Place raill component into position, ensuring that it is plumb, level, square and within tolerances shown on the IFC drawings or Manufacturer's Drawings and installation recommendations.
label | ○ Where mounting to supports or foundations, adjust RL accordingly using suitably sized shims, levelling or jacking nuts (where applicable).
label | ○ Where steel to steel connections exist, holes shall be aligned so that a drift pin equal in diameter of the bolts can pass through freely.
label | ○ Where a misalignment is found, heating of bolts, hand flame-cutting of holes or (heat) drifting of holes shall not be permitted, only reaming, milling, drilling or machine flame or plasma cut. Internal surface of the hole to remain smooth and free from burrs.
label | ○ Holes shall not exceed the greater of: 1.25 x bolt dia. OR bolt dia. + 8mm
label | ○ Slots shall not exceed the greater of: 1.33 x (bolt dia. + 10mm) OR 2.5 x bolt dia
label | METHOD: Measure, Visual
label | FREQUENCY: Each component
label | IP
label | RESPONSIBILITY: SE/PE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
checkpoint | 3.4 Fastener Tightening - Snug Tight Condition (4.6/S & 8.8/S)
label | REFERENCE: IFC Drawings
label | ○ Manufacturer's Drawings & Installation Recommendations AS4100, Clause 14.3.3.1
label | ACCEPTANCE CRITERIA: Place bolts, washers and nuts as detailed on the drawings.
label | ○ At least 1 no. washer shall be used underneath the rotating part unless this is not part of the hand rail system.
label | ○ Washers shall cover the hole or slotted hole completely by 0.5 x bolt diameter.
label | ○ Tapered washers shall be positioned if the surfaces are on a slope of 1:20 or greater.
label | ○ Tighten from the stiffest section working towards the free edges with a few impacts of an impact wrench or the full effort of a person using a podger spanner.
label | ○ Protrusion to be at least 1 clear thread pitch and any thread run-off beyond the nut.
label | ○ Note: No maximum projection length is stated in the Australian Standards.○
label | METHOD: Measure, Visual
label | FREQUENCY: Where applicable, each bolted connection
label | IP
label | RESPONSIBILITY: SE/PE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
section | Post-installation Activities
checkpoint | 4.1 Inspection of Coating
label | REFERENCE: IFC Drawings
label | ○ Manufacturer's Drawings & Installation Recommendations
label | ACCEPTANCE CRITERIA: After installation Works are complete, inspect the steel element for damage to the coatings.
label | ○ Where damage exists, it shall be repaired using an approved repair procedure.
label | METHOD: Visual
label | FREQUENCY: Each component
label | IP
label | RESPONSIBILITY: SE/PE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
checkpoint | 4.2 As-built Survey
label | REFERENCE: IFC Drawings
label | ○ Manufacturer's Drawings & Installation Recommendations
label | ○ Fulton Hogan Quality Management Plan
label | ACCEPTANCE CRITERIA: Provide record of dimensional measurements to demonstrate that all Works meet level and location requirements within the tolerances below:
label | i. Top railing height = 865mm (min.) &1000mm (max.)
label | ii. Rounded end o closed loop = extend beyond landings 300mm (min.)
label | ○ Attach: Survey As-builts / Survey Report / Photos
label | METHOD: Document Review
label | FREQUENCY: Each component
label | IP
label | RESPONSIBILITY: Surveyor, SE/PE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
checkpoint | 4.3 Non-conformance Report (NCR) Closure
label | REFERENCE: Fulton Hogan Quality Management Plan
label | ACCEPTANCE CRITERIA: Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
label | METHOD: Document Review
label | FREQUENCY: Once, prior to closure of this lot / element / Work area
label | HP*
label | RESPONSIBILITY: SE/PE/SPE
label | VERIFYING DOCUMENTS: This ITP
textbox | Date Completed:
checkpoint | Final Inspection
note | On behalf of Fulton Hogan, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
textbox | Print Name:
textbox | Position:
textbox | Date: