## Table 1
SPARK – North East Link – Primary Package Inspection and Test Plan (ITP)
ITP Title: Street Lighting Installation ITP Number: NEL-CNT-SDC-2990-PQA-ITP-0068 Rev 0
LOT Number:
Primary Asset Location Code:
Discipline:
OFFICIAL: Sensitive Spark NELP Approval Record
Function |  |  |  | Position |  |  | Name |  | Signature | [5 empty] | Date
Prepared By |  |  |  | Quality Representative |  |  | Joe Failla |  | Digitally Joe Failla Failla 202 Date: +11'00' | [5 empty] | signed by Joe 2.10.28 15:38:01
Reviewed By |  |  |  | Project Engineer |  |  | Geoffrey Britto | [7 empty] | 2022-10-28
Approved By |  |  |  | Zone Quality Manager |  |  | Greg Iro |  | Digital Date: +11'00 | [5 empty] | ly signed by Greg Iro 2022.10.28 15:31:50 '
Note:
1. Ensure all Records or Checklist References are attached and that each Inspection Requirement is clearly named, signed, and dated. 2. Ensure every Records or Checklist References attached are legible 3. This Inspection Test Plan may be generic – ensure the requirement is demographically clear to your scope of work 4. Verification Inspections where applicable for the IREA stated as “Witness” or “Hold” shall be formally notified for their engagement and with sufficient advance notice time (i.e. 3 days or as agreed with the Sub-IREA Representative and/or the Nominated Authority) 5. All Nominated Authority Hold Points are Witness Points for Sub-IREA 6. The Sub-IREA representative is not required to physically sign-off on ITPs
ITP – Street Lighting Installation Spark PMS Doc# MSF28-2-NEL Rev 3 Document Number: NEL-CNT-SDC-2990-PQA-ITP-0068 Revision: 0 Management System - Uncontrolled Document when Printed Webuild Source Doc# MSF28-2
Page 1 of 5 OFFICIAL - Sensitive
Project: SPARK – North East Link Primary Package Client: State of Victoria and the North East Link State Tolling Corporation
ITP Title: Street Lighting Installation | [11 empty] | References: VicRoads Specification 731, PSDR Standards:
Description: This ITP covers Street Lighting Installation on Spark sites
ITP No: NEL-CNT-SDC-2990-PQA-ITP-0068 Rev No: 0
Lot No: Location: Ch: to Offset: to Layer:
Item No. | Resp. Person |  | Inspection and Test Activity |  | Specification Reference | Acceptance Criteria | [6 empty] | Test Method | Test Freq. |  | Inspection/Verification (Name, signature & date) |  |  |  | Records/ Documents | Field Notes / Comments
[16 empty] | Sub- Contractor | Spark NEL Engineer | Nominated Authority | IREA
1 | Preliminaries (Include all aspects of Materials, Approvals, IFC Drawings, etc. Ensure all required permits have been raised prior to commencing works)
1.1 | PE |  | IFC Drawings Issued |  | PSDR Part F6 | IFC Drawings, approved plans, technical specification issued for construction | [6 empty] | V | PW |  | NR | HP | NR | NR | IFC Drawings
1.2 | PE |  | Approved Methodology |  | Construction Package | All required documents are approved Lot area is clearly defined | [6 empty] | R | PW |  | NR | WP | NR | NR | Construction Package
1.3 | PE |  | Survey Set Out |  | IFC Drawings | Setout points are in accordance with IFC drawings and specifications. Light pole location is set out by surveyor as per the lighting schedule | [6 empty] | R | PW |  | NR | WP | NR | NR | Survey Record
1.4 | PE |  | All equipment calibrated (NATA Approved) |  | VicRoads 731.06 | All equipment associated with relevant works are calibrated Torque Wrench used to tighten the bolts and nuts shall hold a current calibration certificate not more than 12 months old. | [6 empty] | R | PW |  | NR | WP | NR | NR | Calibration Certificate
1.5 | PE |  | Material Conformance |  | VicRoads 731 AS 3000 AS 4680 IFC Drawings | All materials supplied on-site are free of defects and damage Light poles are VicRoads approved and comply with VicRoads section 731 Galvanizing to comply with AS4680 (certificates to be provided) | [6 empty] | V | PW |  | NR | HP | NR | NR | PDS, Manuf. Specif.ns DD’s Galvanizing Certificates / Test Reports
1.6 | PE |  | Electrical Contractor |  | VicRoads 731.11 | Electrical contractor is a VicRoads Electrical Contractor, in accordance with: - Part 3 of the Electrical Safety Act 1998 - Electrical Safety Regulations 2009 Electrical contractor is also prequalified within the VicRoads prequalification scheme at the level of STCE | [6 empty] | R | PW |  | NR | WP | NR | NR | Registered Electrical Contractor Certificate
2 | Operations (Include Work Execution – Installation / Manufacturing Process step-by-step)
2.1 | SE |  | Wiring Works |  | VicRoads 731.08, 731.10, 731.11,(g) IFC Drawings | All electrical works conform to AS/NZS 3000 and Energy Safe Victoria | [6 empty] | V | PL |  | WP | WP | NR | NR | This ITP
Project: SPARK – North East Link Primary Package Client: State of Victoria and the North East Link State Tolling Corporation
ITP Title: Street Lighting Installation | [11 empty] | References: VicRoads Specification 731, PSDR Standards:
Description: This ITP covers Street Lighting Installation on Spark sites
ITP No: NEL-CNT-SDC-2990-PQA-ITP-0068 Rev No: 0
Lot No: Location: Ch: to Offset: to Layer:
Item No. | Resp. Person |  | Inspection and Test Activity |  | Specification Reference | Acceptance Criteria | [6 empty] | Test Method | Test Freq. |  | Inspection/Verification (Name, signature & date) |  |  |  | Records/ Documents | Field Notes / Comments
[16 empty] | Sub- Contractor | Spark NEL Engineer | Nominated Authority | IREA
2.2 | SE |  | Power Supply Conduits |  | VicRoads 731.08, 731.10, 731.11(g) IFC Drawings | Power supply installed in accordance with AS/NZS 3000 Supply conduits located at least 1200mm below FSL of any freeway/highway or arterial road At least 600mm below FSL in other locations | [6 empty] | V | PL |  | WP | WP | NR | NR | This ITP
2.3 | SE |  | Earthing requirements |  | VicRoads 731.11 IFC Drawings | All poles individually earthed to earth cable in the pit of frangible poles or in the pole of rigid poles | [6 empty] | I | PL |  | WP | WP | NR | NR | Each pole
2.4 | SE |  | Trunk Cabling |  | VicRoads 731.11 (h) | A minimum of 2m of spare cable is coiled and left in each cable pit for maintenance purposes | [6 empty] | I | PL |  | WP | WP | NR | NR | Each cable pit
2.5 | SE |  | Distribution Cabinet Labelling |  | VicRoads 731.12 | Site Number to be provided by Design on Drawings Label is affixed to the distribution cabinet in a location viewable from the roadway. | [6 empty] | I | PL |  | WP | WP | HP | WP | Each cabinet
2.6 | SE |  | Pole Labelling |  | VicRoads 731.12 | Asset & poles number to be provided by Design on Drawings. Label directly faces oncoming traffic at approx 45-degree angle and 2.5m-3m above ground level. One label for single outreach. Two labels for double outreach. | [6 empty] | I | PL |  | WP | WP | HP | WP | Each pole
3 | Post Operations (Include Inspection and Testing)
3.1 | SE |  | Data Collection of Assets |  | VicRoads 731.13 | All assets have GPS co-ordinates of their location in decimal degrees to 6 decimal places Site Information: • Site Number • Site name • Start Road • End Road • Owner • Municipality • VicRoads Region • Meter Number • NMI Number • Cabinet GPS co-ordinates Cabinet Information: • Circuit No • Phase circuit connected to • Circuit breaker rating • Pole numbers connected to circuit Poles and Luminaires: • Pole number • Road name • Near Reference • Position (e.g. left, centre median) • Pole location using GPS co-ordinates • Pole height • Outreach type (single or double) • Outreach length • Luminaire brand • Luminaire Type (LED T1, T2 or T4) | [6 empty] | R | PL |  | NR | WP | NR | NR | World Geodetic System WGS84 Excel spreadsheet
Project: SPARK – North East Link Primary Package Client: State of Victoria and the North East Link State Tolling Corporation
ITP Title: Street Lighting Installation | [11 empty] | References: VicRoads Specification 731, PSDR Standards:
Description: |  | This ITP covers Street Lighting Installation on Spark sites
ITP No: NEL-CNT-SDC-2990-PQA-ITP-0068 Rev No: 0
Lot No: Location: Ch: to Offset: to Layer:
Item No. | Resp. Person |  | Inspection and Test Activity |  | Specification Reference | Acceptance Criteria | [6 empty] | Test Method | Test Freq. |  | Inspection/Verification (Name, signature & date) |  |  |  | Records/ Documents | Field Notes / Comments
[16 empty] | Sub- Contractor | Spark NEL Engineer | Nominated Authority | IREA
3.2 | SE |  | Torque of nuts and bolts |  | VicRoads 371.16 | One week prior to PC, the torque in the slip base pole slipe plane holding down nuts and bolts on the flange to be checked with calibrated torque wrench | [6 empty] | I |  |  | NR | WP | NR | NR | This ITP
3.3 | SE |  | Testing and Certificate of Electrical Safety |  | VicRoads 731.16 | Testing of all distribution cabinets, circuits, switches, PE cells, luminaires, and all other electrical components Compliance with AS/NZS 3000 | [6 empty] | T |  |  | NR | HP | NR | NR | Cert of Electrical Safety
4 | Quality
4.1 | QSR |  | Identification and control of non-conforming products or services (if applicable) |  | CQMP Section 8.3 | Review and confirm closure of NCR’s and associated RFI’s prior to closing of construction lot | [6 empty] | R | PL |  | NR | HP | NR | NR | NCR closed with related documentati on
4.2 | QSR |  | Check all quality records for lot closure |  | CQMP Section 8.3 | All applicable quality records are complete | [6 empty] | R | PL |  | NR | HP | NR | NR | Compiled documents (all data reports and records)
Legend:
Responsibility | [7 empty] | Method |  |  | Inspection / Verification |  |  | Test Frequency |  |  |  |  | Other
SS: Site Supervisor SE: Site Engineer PE: Project Engineer SPE: Senior Project Engineer GE: Geotechnical Engineer PS: Project Surveyor |  |  |  |  | PSM: Project Systems Manager QSR: Quality Site Rep. STR: Structural Engineer SSR: Site Safety Rep. EMR: Environmental Management Rep. NA: Nominated Authority (Release of HP) IREA: Independent Reviewer (Observer) |  |  | V: Verify I: Inspection R: Review T: Test |  |  | HP: Hold Point WP: Witness Point NR: Not Required |  |  | PW: Prior to Works PL: Per Lot F: Full or 100% Inspection or Testing X1: Inspect or Test at Specified Frequency X2: Random Inspection or Test |  |  |  |  | QP: Quality Plan RFI: Request for Information NCR: Non-Conformance VC: Verification Checklist XXXX: Sequential Number from Doc Control
DDD – Types: |  |  | B – Building, C – Civil, G – General, M – Mechanical & Electrical, I – Motorway Operations System (ITS), S – Structure, O – Tolling, T – Tunnel, U – Urban Design & Landscape
Supplier/Subcon tractor: (If applicable) |  |  | Name |  |  | Signature and Date |  |  |  | Spark-NELP REP |  |  |  | Name | [6 empty] | Signature and Date
Lot closure comments:
Spark NELP QA Rep:
Name Signature: Date: