## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | NEL-CNT-SDC-2990-PQA-ITP-0068 Rev 0 - Street Lighting Installation | itp |  |  |  |  | NEL-CNT-SDC-2990-PQA-ITP-0068 Rev 0 - Street Lighting Installation
section | 1.0 Preliminaries (Include all aspects of Materials, Approvals, IFC Drawings, etc. Ensure all required permits have been raised prior to commencing works)
checkpoint | 1.1 - IFC Drawings Issued
label | Resp. Person - PE
label | Specification Reference - PSDR Part F6
label | Acceptance Criteria - IFC Drawings, approved plans, technical specification issued for construction
label | Test Method - V
label | Test Freq. - PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - HP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - IFC Drawings
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.2 - Approved Methodology
label | Resp. Person - PE
label | Specification Reference - Construction Package
label | Acceptance Criteria - All required documents are approved
label | • Lot area is clearly defined
label | Test Method - R
label | Test Freq. - PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Construction Package
checkpoint | 1.3 - Survey Set Out
label | Resp. Person - PE
label | Specification Reference - IFC Drawings
label | Acceptance Criteria - Setout points are in accordance with IFC drawings and specifications.
label | • Light pole location is set out by surveyor as per the lighting schedule
label | Test Method - R
label | Test Freq. - PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Survey Record
checkpoint | 1.4 - All equipment calibrated (NATA Approved)
label | Resp. Person - PE
label | Specification Reference - VicRoads 731.06
label | Acceptance Criteria - All equipment associated with relevant works are calibrated
label | • Torque Wrench used to tighten the bolts and nuts shall hold a current calibration certificate not more than 12 months old.
label | Test Method - R
label | Test Freq. - PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Calibration Certificate
checkpoint | 1.5 - Material Conformance
label | Resp. Person - PE
label | Specification Reference - VicRoads 731 AS 3000 AS 4680 IFC Drawings
label | Acceptance Criteria - All materials supplied on-site are free of defects and damage Light poles are VicRoads approved and comply with VicRoads section 731
label | • Galvanizing to comply with AS4680 (certificates to be provided)
label | Test Method - V
label | Test Freq. - PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - HP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - PDS
label | • Manuf. Specif.ns DD’s
label | • Galvanizing Certificates / Test Reports
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.6 - Electrical Contractor
label | Resp. Person - PE
label | Specification Reference - VicRoads 731.11
label | Acceptance Criteria - Electrical contractor is a VicRoads Electrical Contractor, in accordance with:
label | – Part 3 of the Electrical Safety Act 1998
label | – Electrical Safety Regulations 2009
label | • Electrical contractor is also prequalified within the VicRoads prequalification scheme at the level of STCE
label | Test Method - R
label | Test Freq. - PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Registered Electrical Contractor Certificate
section | 2.0 Operations (Include Work Execution – Installation / Manufacturing Process step-by-step)
checkpoint | 2.1 - Wiring Works
label | Resp. Person - SE
label | Specification Reference - VicRoads 731.08, 731.10, 731.11,(g) IFC Drawings
label | Acceptance Criteria - All electrical works conform to AS/NZS 3000 and Energy Safe Victoria
label | Test Method - V
label | Test Freq. - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - WP
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - This ITP
checkpoint | 2.2 - Power Supply Conduits
label | Resp. Person - SE
label | Specification Reference - VicRoads 731.08, 731.10, 731.11(g) IFC Drawings
label | Acceptance Criteria - Power supply installed in accordance with AS/NZS 3000 Supply conduits located at least 1200mm below FSL of any freeway/highway or arterial road
label | • At least 600mm below FSL in other locations
label | Test Method - V
label | Test Freq. - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - WP
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - This ITP
checkpoint | 2.3 - Earthing requirements
label | Resp. Person - SE
label | Specification Reference - VicRoads 731.11 IFC Drawings
label | Acceptance Criteria - All poles individually earthed to earth cable in the pit of frangible poles or in the pole of rigid poles
label | Test Method - I
label | Test Freq. - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - WP
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Each pole
checkpoint | 2.4 - Trunk Cabling
label | Resp. Person - SE
label | Specification Reference - VicRoads 731.11 (h)
label | Acceptance Criteria - A minimum of 2m of spare cable is coiled and left in each cable pit for maintenance purposes
label | Test Method - I
label | Test Freq. - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - WP
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Each cable pit
checkpoint | 2.5 - Distribution Cabinet Labelling
label | Resp. Person - SE
label | Specification Reference - VicRoads 731.12
label | Acceptance Criteria - Site Number to be provided by Design on Drawings
label | • Label is affixed to the distribution cabinet in a location viewable from the roadway.
label | Test Method - I
label | Test Freq. - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - WP
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - HP
label | Inspection/Verification (Name, signature & date): IREA - WP
label | Records/Documents - Each cabinet
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.6 - Pole Labelling
label | Resp. Person - SE
label | Specification Reference - VicRoads 731.12
label | Acceptance Criteria - Asset & poles number to be provided by Design on Drawings. Label directly faces oncoming traffic at approx 45-degree angle and 2.5m-3m above ground level.
label | • One label for single outreach. Two labels for double outreach.
label | Test Method - I
label | Test Freq. - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - WP
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - HP
label | Inspection/Verification (Name, signature & date): IREA - WP
label | Records/Documents - Each pole
holdpoint | AUTHORITY HOLDPOINT
section | 3.0 Post Operations (Include Inspection and Testing)
checkpoint | 3.1 - Data Collection of Assets
label | Resp. Person - SE
label | Specification Reference - VicRoads 731.13
label | Acceptance Criteria - All assets have GPS co-ordinates of their location in decimal degrees to 6 decimal places
label | ○ Site Information:
label | • Site Number
label | • Site name
label | • Start Road
label | • End Road
label | • Owner
label | • Municipality
label | • VicRoads Region
label | • Meter Number
label | • NMI Number
label | • Cabinet GPS co-ordinates
label | ○ Cabinet Information:
label | • Circuit No
label | • Phase circuit connected to
label | • Circuit breaker rating
label | • Pole numbers connected to circuit
label | ○ Poles and Luminaires:
label | • Pole number
label | • Road name
label | • Near Reference
label | • Position (e.g. left, centre median)
label | • Pole location using GPS co-ordinates
label | • Pole height
label | • Outreach type (single or double)
label | • Outreach length
label | • Luminaire brand
label | • Luminaire Type (LED T1, T2 or T4)
label | Test Method - R
label | Test Freq. - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - World Geodetic System WGS84 Excel spreadsheet
checkpoint | 3.2 - Torque of nuts and bolts
label | Resp. Person - SE
label | Specification Reference - VicRoads 371.16
label | Acceptance Criteria - One week prior to PC, the torque in the slip base pole slipe plane holding down nuts and bolts on the flange to be checked with calibrated torque wrench
label | Test Method - I
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - This ITP
checkpoint | 3.3 - Testing and Certificate of Electrical Safety
label | Resp. Person - SE
label | Specification Reference - VicRoads 731.16
label | Acceptance Criteria - Testing of all distribution cabinets, circuits, switches, PE cells, luminaires, and all other electrical components Compliance with AS/NZS 3000
label | Test Method - T
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - HP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Cert of Electrical Safety
holdpoint | AUTHORITY HOLDPOINT
section | 4.0 Quality
checkpoint | 4.1 - Identification and control of non-conforming products or services (if applicable)
label | Resp. Person - QSR
label | Specification Reference - CQMP Section 8.3
label | Acceptance Criteria - Review and confirm closure of NCR’s and associated RFI’s prior to closing of construction lot
label | Test Method - R
label | Test Freq. - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - HP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - NCR closed with related documentati on
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Check all quality records for lot closure
label | Resp. Person - QSR
label | Specification Reference - CQMP Section 8.3
label | Acceptance Criteria - All applicable quality records are complete
label | Test Method - R
label | Test Freq. - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - HP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Compiled documents (all data reports and records)
holdpoint | AUTHORITY HOLDPOINT