## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP - Manhole with PVC Installation | itp |  |  |  |  | ITP - Manhole with PVC Installation
section | Manhole with PVC Installation
checkpoint | 1 - PRE-CAST BASES AND RISERS
label | Inspection / Test Point: Sign off
label | ACTION: H
label | Conformance Criteria (Whats Required): Inspection of concrete product upon delivery to site. Ensure there is no damage or cracking to the precast unit.
label | Frequency: Prior to commencement
label | Inspection / Test Method: Visual
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman, Engineer's Representative
holdpoint | HOLD POINT
checkpoint | 2 - uPVC MAINS AND FITTINGS
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign Off
label | ACTION: H
label | Conformance Criteria (Whats Required): Shall be SN8 and rubber ring jointed, with no damage or deformities.
label | Frequency: Prior to commencement/upon delivery of materials
label | Inspection / Test Method: Visual
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman Engineer's Representative
holdpoint | HOLD POINT
checkpoint | 3 - CONCRETE PRE-POUR INSPECTION
label | Inspection / Test Point: Sign off
label | ACTION: H
label | Conformance Criteria (Whats Required): Site representative to inspect prior to pouring any concrete and sign off
label | Frequency: During Installation
label | Inspection / Test Method: Visual
label | Verification Records: Sign This ITP
label | Signatory: Site Representative
holdpoint | HOLD POINT
checkpoint | 4 - BENCHING AND OTHER MASS POURS FOR MANHOLE
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign off
label | ACTION: H
label | Conformance Criteria (Whats Required): Minimum 1:4 crossfall grade towards formed channel, all surfaces finished smooth, no benching shall hold water
label | Frequency: During Installation
label | Inspection / Test Method: Visual
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman
holdpoint | HOLD POINT
checkpoint | 5 - BASE PREPARATION FOR MANHOLE
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign off
label | ACTION: M
label | Conformance Criteria (Whats Required): A level 150mm AP65 compacted base.
label | Frequency: Prior to installation
label | Inspection / Test Method: Review
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman
checkpoint | 6 - BACKFILLING AND COMPACTION ROADWAY
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign off
label | ACTION: M
label | Conformance Criteria (Whats Required): All backfilled material shall be compaction tested at a maximum of 20m intervals longitudinally with an NDM.
label | Frequency: During Installation
label | Inspection / Test Method: NDM
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman
checklist | ITP - Manhole with RCRRJ Installation | itp |  |  |  |  | ITP - Manhole with RCRRJ Installation
section | Manhole with RCRRJ Installation
checkpoint | 1 - PRE-CAST BASES AND RISERS
label | Inspection / Test Point: Sign off
label | ACTION: H
label | Conformance Criteria (Whats Required): Inspection of concrete product upon delivery to site. Ensure there is no damage or cracking to the precast unit.
label | Frequency: Prior to commencement
label | Inspection / Test Method: Visual
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman, Engineer's Representative
holdpoint | HOLD POINT
checkpoint | 2 - RCRRJ PIPE AND FITTINGS
label | Specification / Standard: SR10.103 SR10.105
label | Inspection / Test Point: Sign off
label | ACTION: H
label | Conformance Criteria (Whats Required): Class 2 RCRRJ pipe, pipe to be inspected upon delivery and have no damage or deformities
label | Frequency: Prior to installation
label | Inspection / Test Method: Visual
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman, Engineer's Representative
holdpoint | HOLD POINT
checkpoint | 3 - CONCRETE PRE-POUR INSPECTION
label | Inspection / Test Point: Sign off
label | ACTION: H
label | Conformance Criteria (Whats Required): Site representative to inspect prior to pouring any concrete and sign off
label | Frequency: During Installation
label | Inspection / Test Method: Visual
label | Verification Records: Sign This ITP
label | Signatory: Site Representative
holdpoint | HOLD POINT
checkpoint | 4 - BENCHING AND OTHER MASS POURS FOR MANHOLE
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign off
label | ACTION: H
label | Conformance Criteria (Whats Required): Minimum 1:4 crossfall grade towards formed channel, all surfaces finished smooth, no benching shall hold water
label | Frequency: During Installation
label | Inspection / Test Method: Visual
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman
holdpoint | HOLD POINT
checkpoint | 5 - BASE PREPARATION FOR MANHOLE
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign off
label | ACTION: M
label | Conformance Criteria (Whats Required): A level 150mm AP65 compacted base.
label | Frequency: Prior to installation
label | Inspection / Test Method: Review
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman
checkpoint | 6 - BACKFILLING AND COMPACTION ROADWAY
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign off
label | ACTION: M
label | Conformance Criteria (Whats Required): All backfilled material shall be compaction tested at a maximum of 20m intervals longitudinally with an NDM.
label | Frequency: During Installation
label | Inspection / Test Method: NDM
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman
checklist | ITP - PVC Installation | itp |  |  |  |  | ITP - PVC Installation
section | PVC Installation
checkpoint | 1 - uPVC MAINS AND FITTINGS
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign Off
label | ACTION: H
label | Conformance Criteria (Whats Required): Shall be SN8 and rubber ring jointed, with no damage or deformities.
label | Frequency: Prior to commencement/upon delivery of materials
label | Inspection / Test Method: Visual
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman Engineer's Representative
holdpoint | HOLD POINT
checkpoint | 2 - PLATEAU TEST ON MATERIALS
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Aggregate Certification
label | ACTION: H
label | Conformance Criteria (Whats Required): Plateau test for aggregates to be done at beginning of job. This only needs to be done once to find compaction ideals.
label | Frequency: Prior to compaction
label | Inspection / Test Method: Visual
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman
holdpoint | HOLD POINT
checkpoint | 3 - BEDDING MATERIAL
label | Specification / Standard: AS/NZS 2566.2
label | Inspection / Test Point: Aggregate Certification
label | ACTION: M
label | Conformance Criteria (Whats Required): Clean granular non-cohesive material with a maximum particle size of 20mm
label | Frequency: Continuous for pipe length
label | Inspection / Test Method: Visual
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman
checkpoint | 4 - OPEN TRENCHING ALIGNMENT, DEPTH AND ACCURACY
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Witness & Record
label | ACTION: M
label | Conformance Criteria (Whats Required): Undertake scalas on base of trench. Minimum of 3 blows per 100mm (to be clarified in spec). Pipe installed within +/- 10mm accuracy from design datum. Installed as per design grade and recorded on pipe laying form. Daily checks to make sure pipe is laid to design.
label | Frequency: Prior to commencement and every two lengths
label | Inspection / Test Method: Review
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman
checkpoint | 5 - BACKFILLING AND COMPACTION ROADWAY
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign off
label | ACTION: M
label | Conformance Criteria (Whats Required): Trench backfill to be carried out with imported AP65 gravel in 250mm lifts. The subbase material shall achieve an average of 95% of the MDD. Plateau test to be undertaken on AP65 and M4AP40. All backfilled material shall be compaction tested at a maximum of 20m intervals longitudinally and 1m vertically with an NDM. All basecourse material shall be M4AP40.
label | Frequency: During Installation
label | Inspection / Test Method: NDM
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman
checkpoint | 6 - CCTV
label | Specification / Standard: Contract Document
label | Inspection / Test Point: CCTV Footage
label | ACTION: H
label | Conformance Criteria (Whats Required): Clear new pipeline of any debris prior to CCTV. CCTV inspection of gravity to be as per the New Zealand Pipe Inspection manual.
label | Frequency: Once pipeline is installed
label | Inspection / Test Method: CCTV
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman
holdpoint | HOLD POINT
checklist | ITP - RCRRJ Installation | itp |  |  |  |  | ITP - RCRRJ Installation
section | RCRRJ Installation
checkpoint | 1 - CLASS 2 RCRRJ PIPE AND FITTINGS
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign Off
label | ACTION: H
label | Conformance Criteria (Whats Required): Class 2 RCRRJ pipe, pipe to be inspected upon delivery and have no damage or deformities
label | Frequency: Prior to commencement/upon delivery of materials
label | Inspection / Test Method: Visual
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman Engineer's Representative
holdpoint | HOLD POINT
checkpoint | 2 - PLATEAU TEST ON MATERIALS
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Aggregate Certification
label | ACTION: H
label | Conformance Criteria (Whats Required): Plateau test for aggregates to be done at beginning of job. This only needs to be done once to find compaction ideals.
label | Frequency: Prior to compaction
label | Inspection / Test Method: Visual
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman
holdpoint | HOLD POINT
checkpoint | 3 - BEDDING MATERIAL
label | Specification / Standard: AS/NZS 2566.2
label | Inspection / Test Point: Aggregate Certification
label | ACTION: M
label | Conformance Criteria (Whats Required): Clean granular non-cohesive material with a maximum particle size of 20mm
label | Frequency: Continuous for pipe length
label | Inspection / Test Method: Visual
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman
checkpoint | 4 - OPEN TRENCHING ALIGNMENT, DEPTH AND ACCURACY
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Witness & Record
label | ACTION: M
label | Conformance Criteria (Whats Required): Undertake scalas on base of trench. Minimum of 3 blows per 100mm (to be clarified in spec). Pipe installed within +/- 10mm accuracy from design datum. Installed as per design grade and recorded on pipe laying form. Daily checks to make sure pipe is laid to design.
label | Frequency: Prior to commencement and every two lengths
label | Inspection / Test Method: Review
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman
checkpoint | 5 - BACKFILLING AND COMPACTION ROADWAY
label | Specification / Standard: Contract Document
label | Inspection / Test Point: Sign off
label | ACTION: M
label | Conformance Criteria (Whats Required): Trench backfill to be carried out with imported AP65 gravel in 250mm lifts. The subbase material shall achieve an average of 95% of the MDD. Plateau test to be undertaken on AP65 and M4AP40. All backfilled material shall be compaction tested at a maximum of 20m intervals longitudinally and 1m vertically with an NDM. All basecourse material shall be M4AP40.
label | Frequency: During Installation
label | Inspection / Test Method: NDM
label | Verification Records: Sign This ITP
label | Signatory: Site Foreman
checkpoint | 6 - CCTV
label | Specification / Standard: Contract Document
label | Inspection / Test Point: CCTV Footage
label | ACTION: H
label | Conformance Criteria (Whats Required): Clear new pipeline of any debris prior to CCTV. CCTV inspection of gravity to be as per the New Zealand Pipe Inspection manual.
label | Frequency: Once pipeline is installed
label | Inspection / Test Method: CCTV
label | Verification Records: Sign this ITP
label | Signatory: Site Foreman
holdpoint | HOLD POINT