## ITP - PCR Precast Panels
INSPECTION & TEST PLAN
|  | Contract Name: | [6 empty] | Rev: | Originator | Date | Approved | Date
|  | 7020 Civil Works |  |  | Hold Point (H) | Verify (V) |  |  | 0 | Michael Polglase | 2023-11-15
ITP03 PCS Slab |  |  |  |  | Submit (S) | Review (R)
[5 empty] | Approve(A) | Witness (W)
Surveillance (SU)
TASK | SPECIFICATION REFERENCE | TEST REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL Signature | Client Signature | UCCL | Client | DATE | COMMENTS
Pre Construction
Site Concrete |  | Visual Inspection | UCCL | Prior to survey setout | Site concrete at correct level, and surfacewithin accepted tolerances (+/- 10mm). |  |  | V
Survey Setout |  | Surveyor to set out PCS slab including duct recesses and bolt positions | UCCL | Prior to steel reinforcing and formwork construction | Foundations shall be set out as per IFC drawings. |  |  | V | W
Materials
Concrete Mix Design | Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03 | Mix Design to be approved by Meridian prior to use | UCCL/MEL | Prior to use on site | Mix Deisgn as per specification (30MPa, 19mm) and approved by Meridian. |  |  | S | H
Steel Reinforcing | Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03 | Supplier documentation, photos | UCCL | Prior to | Steel reinforcing comlies to specifications/IFC drawings/ |  |  | V | W
Prepour
Formwork |  | Visual Inspection | UCCL | Prior to placing concrete | Dimensional check completed and within tolerances. Formwork installed inspected as being suitable for pouring concrete. |  |  | H | H
Steel Reinforcing |  | Visual Inspection | UCCL/MEL | Prior to placing concrete | Steel installed as per IFC drawings. Grade of steel as specified. Number, size and spacing of bars as per IFC drawings. |  |  | H | H
Foundation Earth |  | Visual Inspection, Continuity Test | UCCL, MEL | Prior to placing concrete | Earth bars and cables installed as per IFC drawings. Continuity test completed and passed by MEL. |  |  | H | H
Postpour
Post pour inspection |  | Visual Inspection | UCCL | Following placement of concrete | Post pour inspection sheet to be completed following each PCS slab pour |  |  | A | W
Post Construction
As-Built Drawings |  | Survey as-nuilt drawings | UCCL | On completion of Separable Portions | As-built drawings submitted to MEL. |  |  | S | R