## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Ducting Inspection Record |  |  |  |  | Yes | Ducting Inspection Record | 39301e7c-93c6-4d8c-bf9a-77e4e816b6a3
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Details:
text | 88730f1b-4d27-55a0-bdeb-99273c0332b8 |  | textbox | Contract Name:
text | d47a87c9-8824-57a9-bbd9-7ee0e879bf6c |  | textbox | Contract No:
text | a17477ee-612f-5db6-9195-2cc8b71de68f |  | textbox | Location:
text | 8aa2ba91-90e9-518d-bd54-c770fce6629c |  | textbox | Other:
text | 1bd3ceeb-0a0c-5a66-8664-a6cdb1d53526 |  | textbox | Drawings & Revision No.:
date | 45e822f6-34e6-5a64-85a8-05652162bb5c |  | date | Date:
text | 2eef4b6f-e28b-5450-86dd-9e3260d2c457 |  | textbox | Duct Descriptions:
checkpoint-group |  |  | section | Preliminary
checkpoint-status |  |  | checkpoint | IFC Drawings Available
checkpoint-status |  |  | checkpoint | Setout Completed
checkpoint-group |  |  | section | Excavation/Trenching
checkpoint-status |  |  | checkpoint | Excavation/Trench to Correct Line and Level
checkpoint-status |  |  | checkpoint | Subgrade in Trench Tested and Passed
checkpoint-group |  |  | section | Ducting Inspection Record
checkpoint-status |  |  | checkpoint | Ducts Installed as Per IFC Drawings
checkpoint-status |  |  | checkpoint | Any Additional Ducts not on IFC Drawing
checkpoint-status |  |  | checkpoint | Minimum Duct Separation Maintained
checkpoint-status |  |  | checkpoint | Joints Cleaned and Glued Correctly
checkpoint-status |  |  | checkpoint | Ducts Installed to Correct Line and Level
checkpoint-status |  |  | checkpoint | Installed Ducts Recorded by GPS
checkpoint-group |  |  | section | Backfill
checkpoint-status |  |  | checkpoint | Thermal Bedding Under Ducts as Required
checkpoint-status |  |  | checkpoint | Thermal Bedding Backfilled to Correct Level
checkpoint-status |  |  | checkpoint | Compaction of Thermal Bedding as Per Agreed Methodology and Passed
checkpoint-status |  |  | checkpoint | Marking Tape Installed Over Ducts Correctly
checkpoint-status |  |  | checkpoint | End of Ducts Capped/Taped
checkpoint-no-status |  |  | checkpoint | Comments:
checkpoint-status |  |  | checkpoint | Ducts and Backfill Checked and Accepted
text | cb4ddbed-fc6d-56cf-89c7-6941d5e1e9bf |  | textbox | Name:
date | b97a8e86-1c13-55f6-9388-1228af8237d4 |  | date | Date:
holdpoint |  |  | signoff | Sign:
checklist-sectioned |  |  | checklist | ITP 02 - Duct Installation | itp |  |  |  | Yes | ITP 02 - Duct Installation | 66ddc652-ca02-437f-a54a-9bd58409a887
checkpoint-group |  |  | section | Preconstruction
checkpoint-status |  |  | checkpoint | Review of proposed work
label | 19b45186-6d75-5342-9519-9c8749006daf |  | note | TEST/TASK REQUIRED - Drawings to be reviewed and permission to proceed given.
label | 218de57d-3f30-521e-a763-e10d57a2956f |  | note | INSPECTION BY - UCCL, MEL
label | d2b285b6-16cb-5b5d-b318-51b6a556a48f |  | note | TASK TIMING OR TASK FREQUENCY - Prior to Ordering Materials
label | f4109371-f3a2-5add-b87d-27eea2b42f31 |  | note | ACCEPTANCE CRITERIA - Drawings to be IFC
label | 38cce9a1-f486-563f-8007-cb24a811262d |  | note | UCCL - R
label | 402f0dee-326f-52de-a236-baa26890b48b |  | note | Client - A
checkpoint-status |  |  | checkpoint | Survey Setout
label | 840e8bf2-fb08-5520-9275-2fe3185d5a73 |  | note | TEST/TASK REQUIRED - Initial Setout by Surveyor
label | 62a4440d-a3d0-5aaf-9d02-779eb0f4a1b9 |  | note | INSPECTION BY - UCCL
label | 852155be-d299-556c-9c2e-90e80432f234 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to Installation
label | 90a78515-5437-562b-99f7-d0ab3848c4e8 |  | note | ACCEPTANCE CRITERIA - Surveyor to set out prior to construction
label | 2184735e-68e9-5205-9e8c-d8de69311054 |  | note | UCCL - V
label | af316919-90b5-534b-8234-604eecec133b |  | note | Client - A
checkpoint-status |  |  | checkpoint | Service Ducts
label | b16db5ad-c62f-5094-ae6a-8d0e834c164b |  | note | SPECIFICATION REFERENCE - 14.4 Specification for laying Cable Ducts
label | 4adde750-e4a2-5360-9440-9819038aa49b |  | note | TEST/TASK REQUIRED - PVC Heavy Duty Electrical Ducts 50mm, 100mm and 150mm diameter. Colours as specified on drawings
label | 51afe042-265b-528b-9514-a5236229d6f5 |  | note | INSPECTION BY - UCCL
label | 8c13edf9-1f36-5b5d-adde-09f2c9e5d6ed |  | note | TASK TIMING OR TASK FREQUENCY - Prior to Installation
label | e0f585ac-c532-5cde-961b-862e861f0d17 |  | note | ACCEPTANCE CRITERIA - Supplier Documentation
label | f92b2780-9896-5fde-b110-4142318e8334 |  | note | UCCL - S
label | c39305aa-4f76-514a-9269-518ee5b3597a |  | note | Client - A
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Installation of 100mm Ducts Between PCS Slab and Containers
label | c117f991-932a-504b-9917-c6e5604d4712 |  | note | SPECIFICATION REFERENCE -
label | d50ecbbb-9361-52d2-b7ce-182570a0a751 |  | note | TEST/TASK REQUIRED - Visual Inspection
label | 62a1623a-8ff5-526a-b5a5-f0a6e44b5017 |  | note | INSPECTION BY - Meridian
label | 8a03d01f-80dd-5f40-bf71-51d1d2754db5 |  | note | TASK TIMING OR TASK FREQUENCY - On completion of the installation of each set of 100mm ducts.
label | 83cea5fc-c8ad-514b-a54e-ca45c6ef1571 |  | note | ACCEPTANCE CRITERIA - Orange 100mm ducts from PCS slab to container installed to correct line and depth.
label | d7aa7bb0-d757-57bb-8aa9-4a184afc0f98 |  | note | UCCL - V
label | f9729028-0964-503d-a2e5-54d9c4aaabc6 |  | note | Client - A
checkpoint-status |  |  | checkpoint | Installation of 50mm Ducts Between PCS Slab and Containers
label | 5a6b7ca5-f404-5212-abf5-48846f0eb1c3 |  | note | SPECIFICATION REFERENCE -
label | ef5fd480-57cb-538d-a32a-0138df4a68b8 |  | note | TEST/TASK REQUIRED - Visual Inspection
label | 7f8f88d2-b2ab-5420-9507-846e26036b97 |  | note | INSPECTION BY - Meridian
label | 50e1fd72-33fe-529f-9d54-ce73dcfba3c6 |  | note | TASK TIMING OR TASK FREQUENCY - On completion of the installation of each set of 50mm coloured ducts.
label | 1315dd27-e083-5622-936b-2464c1bf5328 |  | note | ACCEPTANCE CRITERIA - Coloured 50mm ducts from PCS slab to containers installed to correct line and depth.
label | cb2d71bb-31a9-5424-b04a-1ae4d7f20436 |  | note | UCCL - H
label | e2cc7b5e-dbaf-56e8-a38e-5128c54415ab |  | note | Client - V
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Thermal Backfill (as directed by principal)
label | 68e7ace7-d091-52aa-af2b-af26aba6d9de |  | note | SPECIFICATION REFERENCE - Civil Works Specification 6.4 Amended to pleatu test for accepted MDD Refer MAIL NUMBER WSP-CONSC-000319 REFERENCE NUMBER MELNZ-RFI-000265
label | 4997e250-544f-5d09-8f23-ee930bb2bad8 |  | note | TEST/TASK REQUIRED - Visual Inspection
label | 27b674e0-85ab-569c-a8e0-e80932a4d2fd |  | note | INSPECTION BY - UCCL
label | 0d5c5cdb-61df-50b1-98d9-796ec70df0eb |  | note | TASK TIMING OR TASK FREQUENCY - Following instalaltion of ducts, where specified
label | 37e5119d-f239-57f3-a46f-ab1d5d819aa2 |  | note | ACCEPTANCE CRITERIA - 10 passes with plate compactor, per MELNZ-RFI-000310
label | 15126df3-8a05-5c11-982c-27d6396a77ff |  | note | UCCL - V
label | 7c291a3f-daee-53fe-b244-d8fc8b83e983 |  | note | Client - A
checkpoint-status |  |  | checkpoint | Sand Backfill
label | 71f2c402-a26d-5b40-a2b6-ecd41ee7530b |  | note | SPECIFICATION REFERENCE - Civil Works Specification 6.4 Amended to pleatu test for accepted MDD Refer MAIL NUMBER WSP-CONSC-000319 REFERENCE NUMBER MELNZ-RFI-000265
label | 2403c26f-2955-519c-b6eb-a0b1c5d3922f |  | note | TEST/TASK REQUIRED - Visual Inspection
label | 3ecb5d4d-9709-5be8-8057-f4bfeb2c22e3 |  | note | INSPECTION BY - UCCL
label | 7df97b0b-f90c-551e-86ed-f3ec46ed37df |  | note | TASK TIMING OR TASK FREQUENCY - Following installation of ducts, where specified.
label | e9dc6948-ae60-5968-9673-277f8e727455 |  | note | ACCEPTANCE CRITERIA - Self compaction of sand, as per MELNZ-RFI-000310
label | 50d46d35-cbda-5783-b891-dc205c3a2b24 |  | note | UCCL - V
label | 9488f4cb-ad96-5358-9813-68ad5abd50f1 |  | note | Client - A
checkpoint-status |  |  | checkpoint | Flowable Fill
label | 9982be00-2157-59a7-8f02-426fd358a7a0 |  | note | SPECIFICATION REFERENCE - Refer MAIL NUMBER MELNZ-RFI-000393 (Ducting at 101A, 201A, 301A, 401A and 501A requires flowable fill as per drawings supplied)
label | 70049592-e885-5ab1-bcc8-e3d6d99693a5 |  | note | TEST/TASK REQUIRED - Visual Inspection
label | e488808f-1c59-5bdc-9179-48f0edaee540 |  | note | INSPECTION BY - Meridian
label | 1c1990e5-eef3-5ca9-a487-1745349f4d81 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to pouring flowable fill over 100mm orande ducts at 101A, 201A, 301A, 401A and 501A.
label | 661c4b0d-7ab6-5c52-9ade-b62c420ddc58 |  | note | ACCEPTANCE CRITERIA - Orange 100mm ducts from PCS slab to container installed to correct line and depth. Ducts braced and height pegs set for correct cover.
label | 805fa291-4cae-56c1-b7e2-fdc0b5da18c6 |  | note | UCCL - H
label | f8bd0dda-0fee-5f10-9228-7ff49a4dce4d |  | note | Client - V
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | AP40 Hardfill Layer
label | 46db4cc0-abc2-5397-af54-01be9e9fe3db |  | note | SPECIFICATION REFERENCE - Construction Drawing Set RUK-UMC-DS-01. Also refer MAIL NUMBER MELNZ-CA-000290.
label | c757b580-7054-5f54-956d-cb65d723ba43 |  | note | TEST/TASK REQUIRED - Visual inspection. Cleeg test with minimum CIV value of 25.
label | c8972f7c-63dc-5fc6-8678-d27e2ae4222c |  | note | INSPECTION BY - UCCL
label | 04070ed6-58f7-5f73-beab-ed9d164565cf |  | note | TASK TIMING OR TASK FREQUENCY - On completion of AP40 hardfill layer, prior to site concrete.
label | 37d00198-5930-5516-a75e-5d34991ea1a1 |  | note | ACCEPTANCE CRITERIA - Minimum CIV of 25.
label | ec207812-f7a0-55a3-9d06-c0b566546dd2 |  | note | UCCL - V
label | 5e805e68-42af-54b7-985b-f61eb5f50227 |  | note | Client - A
checkpoint-status |  |  | checkpoint | Cable Pits
label | 9d20f8da-2741-565d-a3c1-a51f9c5a59b1 |  | note | SPECIFICATION REFERENCE - 14.4 3 Specification for laying Cable Ducts
label | fde25a45-882c-5796-8c08-3ee9410f2319 |  | note | TEST/TASK REQUIRED - Supplier Documentation
label | f68b94ad-aad9-55c1-91c4-6c5762d20bad |  | note | INSPECTION BY - UCCL
label | bd56e39e-cca7-560c-ba90-1063e55cbbcb |  | note | TASK TIMING OR TASK FREQUENCY -
label | a6ccb820-78bc-530b-ba97-b520ced0e315 |  | note | ACCEPTANCE CRITERIA - Cable pull pits to the dimensions shown on drawings
label | ddc1a157-d1fd-50c1-a0eb-be0244dd9d7f |  | note | UCCL - V
label | 9a319dcb-613f-5d96-a9bc-07299305fab5 |  | note | Client - A
checkpoint-group |  |  | section | Post Construction
checkpoint-status |  |  | checkpoint | As Built & Final Design Documentation
label | 5b9bf436-8f3d-5df9-9d05-e3ed77ba249d |  | note | SPECIFICATION REFERENCE - 14.4 2.3 Specification for laying Cable Ducts
label | 5755a341-c9cc-59ce-b3e7-1a5c57639370 |  | note | TEST/TASK REQUIRED - Surveying
label | e5bc8bd3-8deb-57ba-9536-63983667f995 |  | note | INSPECTION BY - UCCL
label | 19433b00-4177-5d5f-a6c2-d2214a845e60 |  | note | TASK TIMING OR TASK FREQUENCY - As constructed
label | 1f45c529-314a-5277-a42c-99b4ccf714dc |  | note | ACCEPTANCE CRITERIA - The contractor shall undertake site survey of all duct ends so that they are installed within +/- 15mm of their design location
label | 2084e0e1-3f6d-519e-b341-090c68a44d30 |  | note | UCCL - S
label | 1b48e617-f81d-59c4-aba0-70759f46bf1d |  | note | Client - A
checkpoint-status |  |  | checkpoint | Ducting QA
label | b0d6c845-638b-584f-9090-d5cb9961c640 |  | note | SPECIFICATION REFERENCE - 14.4 Specification for laying Cable Ducts
label | a2cf2432-8b84-5b4a-a02a-d34fac590dac |  | note | TEST/TASK REQUIRED - Duct Inspection Record
label | 583a149f-5634-518d-a1f5-8630fc6bb315 |  | note | INSPECTION BY - UCCL
label | 9532d9f1-2089-57b5-a24e-e50336f5adc4 |  | note | TASK TIMING OR TASK FREQUENCY - Per trench
label | 67201a61-e3d2-588b-bf18-a57843728013 |  | note | ACCEPTANCE CRITERIA - Duct Inspection Checklist completed per trench
label | 78d6f769-8dd1-5088-bb2a-c37495b9c85c |  | note | UCCL - S
label | 53e3ead3-488b-5fbf-8433-4c9b843debb4 |  | note | Client - A
checkpoint-status |  |  | checkpoint | Completion of Ducts for Handover
label | 0c1e541f-3761-5239-b7c8-83a71f9bb288 |  | note | SPECIFICATION REFERENCE -
label | f59428f3-ecb2-5875-85ff-1636587cc284 |  | note | TEST/TASK REQUIRED - Handover Record - Handover of Ducts to Electrical
label | 4eecca87-9070-57b2-a825-e111cc48a8f9 |  | note | INSPECTION BY - UCCL
label | f37185ee-5ae0-5817-89fe-6d6f4876262d |  | note | TASK TIMING OR TASK FREQUENCY - On the completion of duct installation at handover for electrical installation.
label | d7032c2d-38f2-50a3-ac2d-bb808f809c25 |  | note | ACCEPTANCE CRITERIA - Handover record sign by UCCL, Meridian, and Electrical Department. Ducts installation completed, and ducts cleaned ready for electrical installation.
label | aa39da1d-adc2-5be4-9f08-ccdf759138fc |  | note | UCCL - H
label | eca05d81-670e-5dfc-85ad-502c9918924a |  | note | Client - V
holdpoint |  |  | signoff | HOLD POINT
checklist-sectioned |  |  | checklist | PCS Foundations |  |  |  |  | Yes | ITP 01 - PCS Foundations | dc37db2b-ed8d-4af2-ad41-deab064829df
checkpoint-group |  |  | section | Pre Construction
checkpoint-status |  |  | checkpoint | Review of proposed work
label | a015857a-71d5-5832-af51-7d6ef368be0c |  | note | SPECIFICATION REFERENCE - 1235 SHOP DRAWINGS - ITEM 1.10
label | ef6c6de1-ee59-5ee5-a429-24e7eaf63309 |  | note | TEST REQUIRED - Shop drawings to be reviewed and permission to proceed given.
label | 154e7045-facf-5dff-bbd6-adaf0b7b27c7 |  | note | INSPECTION BY - Named reviewer or contract administrator
label | b80015e9-965f-5c56-97ba-c9f5bbfbe1af |  | note | TASK TIMING OR TASK FREQUENCY - Start of task
label | 01b7eda7-c416-5a85-9668-3f87820e9018 |  | note | ACCEPTANCE CRITERIA - Shop drawings to be accepted by the reviewer. Building Information Model (BIM) is being used for the construction works.
label | a14759cf-37fa-5c62-a4ee-085b9c2d8059 |  | note | UCCL - H
label | 102e5c1a-6d9f-5324-9fbd-1e30888e6301 |  | note | Client - A
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Materials
checkpoint-status |  |  | checkpoint | Concrete Mix Design
label | 1ff17b05-ad05-519b-8bb0-633ac33753bc |  | note | SPECIFICATION REFERENCE - Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03
label | a97a66fb-6048-505d-9577-044ae72fa206 |  | note | TEST REQUIRED - Supplier Documentation
label | 19053180-29e3-5142-bb96-ec69b2746d52 |  | note | INSPECTION BY - UCCL, MEL
label | 6e1d0e1e-e0a6-548b-8a20-77e919d36dbb |  | note | TASK TIMING OR TASK FREQUENCY - Each Mix Design used prior to use
label | 7cf45f41-f19b-567b-adf7-c19477e09adc |  | note | ACCEPTANCE CRITERIA -
label | 784760dc-6471-5854-9bb7-169773a952c7 |  | note | Foundations (including retaining wall footing) -
label | f41ee08c-ccd7-537d-835f-dbf98dd3b45e |  | note | ○ Aggregate: 19mm
label | a96be871-a299-5bba-b467-7a3fa0f91799 |  | note | ○ 28 day strength: 35MPa
label | 218d7da3-68d8-552d-b337-0ef392350e92 |  | note | Precast retaining wall -
label | 81f3773d-63ee-5d7a-86d0-a28f1edd7909 |  | note | ○ Aggregate size: 19mm
label | d84c6630-bdb4-552f-b2f0-82858c4c4f0f |  | note | ○ 28 day strength: 35MPa
label | b1bbf60d-f1fa-5abe-85df-986361ab9375 |  | note | UCCL - S
label | 742f6370-e41b-5bc0-b3a7-04d65bff03cb |  | note | Client - R
checkpoint-status |  |  | checkpoint | Certificates
label | 7b0ebe92-d0e8-56d9-96e0-7714567f4052 |  | note | SPECIFICATION REFERENCE - 1.12 Certificates
label | acbe2368-d88f-53b7-8c03-c375576d52bb |  | note | TEST REQUIRED - Portland cement to NZS3121,
label | f838c7b4-d67c-53d3-912e-e1aef33f670e |  | note | INSPECTION BY - UCCL
label | 5c21c7de-3680-5303-80a5-55fa6b07158a |  | note | TASK TIMING OR TASK FREQUENCY - Each Batch
label | 165ace66-0be6-5fa8-ace6-90b106e520c6 |  | note | ACCEPTANCE CRITERIA - NZS 3122
label | 5ee59556-dd41-57ea-81c9-d5eb6b6e3890 |  | note | UCCL - S
label | 2b3f94ef-9938-5352-899d-da864a02cb24 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Reinforcement
label | c3148d81-749a-514d-b3fd-f91ef51bb6f9 |  | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-12
label | 4dbe8d17-c8d0-519c-95f9-628dae26e814 |  | note | TEST REQUIRED - Supplier Documentation, photos of spacings
label | 3ae3e378-ab26-5b93-8fcc-9f130e8a96e0 |  | note | INSPECTION BY - UCCL, MEL
label | f7d3a9c9-b6fd-57bb-8811-82a222db6718 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to pouring
label | bfa44109-6c4b-588b-9946-3bf5018d47c5 |  | note | ACCEPTANCE CRITERIA - Reinforcement of precast retaining wall to be YD12-200 vertical and horizontal with D12-200 starters. Reinforcement of in-situ strip footing to be 2/YD12 with R6-300 stirrups
label | 761c31ac-d8be-5118-a49b-466366c5a7d0 |  | note | UCCL - V
label | 546aed7c-8fae-578d-bef2-b75478898024 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Strip Footing
label | 60946fb8-9c9a-5fe2-84ed-d69c874b85f1 |  | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-12
label | 4d5da26e-cae4-5f25-ad5a-a35df12e4627 |  | note | TEST REQUIRED - Photos
label | 692164fc-48cb-5fd5-a003-c35658400a2a |  | note | INSPECTION BY - UCCL, MEL
label | e98962aa-a219-51df-a1a9-29c4ba1af75d |  | note | TASK TIMING OR TASK FREQUENCY - Prior to pouring
label | 4a636711-f2a7-5553-b860-961af734b14b |  | note | ACCEPTANCE CRITERIA - Reinforcement to have maximum 75mm clearance and minimum 50mm clearance.
checkpoint-status |  |  | checkpoint | Cast in Items - Nuts, Bolts and Studs
label | 28090b9a-138a-5fc3-acb1-d6daf3d28896 |  | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-10
label | 2c5cfa97-9d67-5203-99ec-6ba421522912 |  | note | TEST REQUIRED - Supplier Documentation
label | 55e1de77-fe1a-561a-886c-fc48c5a88179 |  | note | INSPECTION BY - UCCL
label | 05f3ed75-f9ba-5f52-bdef-cece9de0734a |  | note | TASK TIMING OR TASK FREQUENCY - Prior to Ordering
label | 58eb0dab-8ad9-54ac-8e28-96ff93fe5390 |  | note | ACCEPTANCE CRITERIA - EA bolts to be M16 Hilti RE-500
label | d0abf167-119c-5412-ab02-cda277d6b166 |  | note | UCCL - V
label | c9e7c594-bc0a-5d0c-b107-83e30f8d1613 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Air content test
label | e71e4264-4ee2-59ee-9e65-703476b4ee69 |  | note | SPECIFICATION REFERENCE - 1.13
label | 265ca5d3-6375-5dd6-aee1-302c2bf0456a |  | note | TEST REQUIRED - Supplier Documentation/IANZ Laboratory
label | b1c29214-691d-5f5b-bdc4-4438afc6cafa |  | note | INSPECTION BY - UCCL
label | 49e6fff7-e796-5652-9518-2256feed20e6 |  | note | TASK TIMING OR TASK FREQUENCY - Each Batch
label | acb68691-b603-5081-9d26-de7e519de028 |  | note | ACCEPTANCE CRITERIA - NZS3109
label | a73214a9-af49-552b-af6a-9a0be30cd862 |  | note | UCCL - V
label | de677fbb-78ef-502f-9833-600a89ea6d48 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Slump Test
label | cd3ad7ef-006d-54bf-bd65-44906a2c20dd |  | note | SPECIFICATION REFERENCE - 1,13
label | 3982c0cf-80d2-58b7-b2ee-83b2a089daac |  | note | TEST REQUIRED - Supplier Documentation/IANZ Laboratory
label | e148d26b-6899-5609-ab80-e89f551ebee1 |  | note | INSPECTION BY - UCCL
label | f32983b1-aaf3-55d0-a5ae-0a705e7d993e |  | note | TASK TIMING OR TASK FREQUENCY - Each Batch
label | 80471948-7ff8-57fa-8ee6-aed5e29b82b8 |  | note | ACCEPTANCE CRITERIA - NZS3109
label | 443e0c3e-59df-5c2d-bcf6-0e772d536854 |  | note | UCCL - V
label | 1f69e207-fa85-5f4e-8e6f-be93e62ea5a5 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Conduct 7 day strength test
label | 8fe6f766-0692-5a23-a8ea-b0e94b7b5bca |  | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.11
label | a98406e3-7bcc-59cd-a45d-baec1b973dc1 |  | note | TEST REQUIRED - 7 day strength test
label | 7c48a5af-d2f5-5498-b7f5-ae3772e2d5c4 |  | note | INSPECTION BY - UCCL
label | c2462735-2ebc-5691-ae75-97f9f7f74cb3 |  | note | TASK TIMING OR TASK FREQUENCY - 7 day after casting
label | 4896c328-d859-56ac-beda-7da38e6bb1c8 |  | note | ACCEPTANCE CRITERIA - 60 % of the specified strength
label | af51b19a-a39d-5c0a-9c50-a06f6a6abb76 |  | note | UCCL - V
label | 27a86699-6395-507f-bc02-2135478b07f7 |  | note | Client - SU
checkpoint-group |  |  | section | Pre Construction - Site works
checkpoint-status |  |  | checkpoint | Strip Footing
label | 97fd9e45-7600-5239-98d8-5e0b6ea92c04 |  | note | TEST REQUIRED - Photos
label | ee5e2a21-cbc9-54b9-bf45-b0a043b487b2 |  | note | INSPECTION BY - UCCL
label | 624d746a-0910-5325-9fc7-1f8ed8c4239a |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
label | fd4ac82a-f2b7-530e-b3b5-b74e445a5e24 |  | note | ACCEPTANCE CRITERIA - Strip footing to be 400mm wide and 200mm deep
label | 6ff6d2d6-995e-597f-a405-270160a74f7e |  | note | UCCL - V
label | edca2f0f-5dd5-509f-ab79-b566aa189426 |  | note | Client - Su
checkpoint-status |  |  | checkpoint | Subgrade Strength
label | 832ef7cb-d385-536c-a083-7de4b2426be7 |  | note | TEST REQUIRED - Scala Penetrometer Records
label | c3547d4a-b953-54ec-bd05-67653c21325d |  | note | INSPECTION BY - UCCL
label | 84bcf3ae-d67f-5c4c-b558-76e01f290e59 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
label | 4fb1def6-7272-586a-9a8e-4b8c06fbf852 |  | note | ACCEPTANCE CRITERIA - Subgrade to meet 3 blows/ 100mm with scala testing
label | 897f8fd4-14d8-5a85-bfec-4dd7082debb5 |  | note | UCCL - V
label | 27610774-8d12-54dc-9b76-e2c5ee633443 |  | note | Client - W
checkpoint-status |  |  | checkpoint | Formwork
label | 33d9f5e3-95a1-5db3-a693-dec849aeb1f3 |  | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.14
label | 2de8e55a-cc7e-5d3e-927c-abfca5f48583 |  | note | TEST REQUIRED - Quality shape and size of formwork
label | 5d661063-20e9-5f63-9017-f9108587ffab |  | note | INSPECTION BY - UCCL
label | 4bef5f18-7c3e-5f4d-9f5a-416954a6f7b5 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | f9fd92d0-d97c-5f61-b5be-8a69c989f294 |  | note | ACCEPTANCE CRITERIA - All formwork to meet the specification required for the unit being constructed
label | 206a427d-85f9-5261-b621-72b5a8fe4abd |  | note | UCCL - V
label | e106806e-b7f2-5384-b2e6-75bec8e00baa |  | note | Client - W
checkpoint-status |  |  | checkpoint | Site Concrete
label | 4ccaa8d5-1b08-5404-9fed-fd9c7499fe90 |  | note | TEST REQUIRED - Visual inspection
label | c09a95a8-e2aa-55e9-9123-44aefdc3b3c1 |  | note | INSPECTION BY - UCCL
label | 94e43f08-d88c-5c9b-ac72-666deb9d9d93 |  | note | TASK TIMING OR TASK FREQUENCY - Each Foundation
label | 66852368-6cf6-5f78-ba39-90b0b5d15e10 |  | note | ACCEPTANCE CRITERIA - Site concrete to be placed at the thicknesses shown on the drawings and finished to a height of +/- 10mm
label | e58d6350-7e61-53cc-a1e1-26824ede22dd |  | note | UCCL - V
label | 9ec2bcef-e924-5179-af65-778129058ea4 |  | note | Client - Su
checkpoint-status |  |  | checkpoint | Setout
label | 5e3d1f35-246f-5fc3-ac99-738eb9881095 |  | note | TEST REQUIRED - Survey
label | 9fedaf09-cf79-5507-a19d-93f597687ed1 |  | note | INSPECTION BY - UCCL
label | 32b144b7-7e58-5dbe-ab69-7fce691032cd |  | note | TASK TIMING OR TASK FREQUENCY - Each string
label | 59db3571-2a56-5a11-b072-6c0d16bf7a86 |  | note | ACCEPTANCE CRITERIA - Foundations and embedded items shall be set out following the tolerances, heights and positions shown in each foundations respective drawing.
label | 8a63898a-42c2-5474-8721-1562ee265996 |  | note | UCCL - V
label | 59681a56-b250-52e4-8772-954460f58c86 |  | note | Client - Su
checkpoint-group |  |  | section | Prepour Inspection
checkpoint-status |  |  | checkpoint | Pre pour inspection
label | 28ff528a-118b-52b0-9c82-dbff6abeb4da |  | note | TEST REQUIRED - Visual Inspection
label | 388a1272-492f-5fb0-8522-babd6d6bbde7 |  | note | INSPECTION BY - UCCL, MEL, WSP
label | de4d308d-a320-50cd-921d-9fe141f9f5e3 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing structural concrete
label | 8ebe09fb-dce3-5cd5-87c7-c21286472733 |  | note | ACCEPTANCE CRITERIA - Pre pour inspection sheet to be completed prior to placing concrete. WCL to be notified of pours for inspection at least 24 hours prior to placing concrete.
label | b156ec4c-540d-5d9a-9792-5ded84a1c158 |  | note | UCCL - H
label | 6f19ea62-2ee8-5326-adff-18ddb2752a51 |  | note | Client - W
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Postpour Inspection
checkpoint-status |  |  | checkpoint | Post pour inspection
label | 0f87c4f1-6f31-5187-b128-3651ec9b10bc |  | note | TEST REQUIRED - Visual Inspection
label | 724a37e9-0b05-5b6a-ab3f-52a2985055c0 |  | note | INSPECTION BY - UCCL
label | fb67f8f9-33f9-5c7c-82f0-e3f3c01fc721 |  | note | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
label | 05a7a0de-8265-5c98-913b-55bb0bfbd896 |  | note | ACCEPTANCE CRITERIA - Post pour inspection sheet to be completed following each pour.
label | 272c629c-97d2-544c-83ac-1fddf7c3e8ed |  | note | UCCL - A
label | f0ece2bc-9bef-57eb-85fe-1e8d39476118 |  | note | Client - Su
checkpoint-group |  |  | section | Post Construction
checkpoint-status |  |  | checkpoint | As Built & Final Design Documentation
label | 4ab69cb8-fa7b-53ed-8cd3-aa736b9a79d8 |  | note | TEST REQUIRED - Surveying
label | b389ca5f-475a-5bd4-9ac9-ac2c941eedd1 |  | note | INSPECTION BY - UCCL
label | d79d0632-032e-5cd2-b6af-a04a969cf066 |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 894f8aab-fe5c-59b3-8156-3544dfd17eb3 |  | note | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline mark ups
label | 2d8a961c-1c34-5b5e-8541-9b10c1397198 |  | note | UCCL - S
label | 0b50ff9b-4728-50a0-be0e-edbdb22bf649 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Records of:
label | 3403217d-75a8-59fb-814b-67e91f5056e0 |  | note | SPECIFICATION REFERENCE - Products and materials selected for alternatives specified, Approved substitutions and accepted alternatives, Other approved changes and deviations to items specified.
label | 245d164e-ad45-5a68-bdd3-901dda2aeeeb |  | note | INSPECTION BY - UCC
label | e3734712-a2ab-5ba1-88b3-c2f5077f25b2 |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | ac78d5f2-2a70-5ddf-bba3-9ab7f8df5622 |  | note | ACCEPTANCE CRITERIA - Confirmation From Engineer of all records
label | c50373ec-dc7f-51d8-9428-812cd6c26d7e |  | note | UCCL - S
label | 3ef35ab5-da76-563c-a0a2-9925eb196534 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Producer statement
label | 96ec4d67-a708-55b9-b649-4c89a4b06ca6 |  | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.14
label | 9842e11c-b4ff-5a51-a9dd-c4a425983eea |  | note | TEST REQUIRED - Submit a producer statement for precast units
label | 723d0dcc-a778-5d98-9706-0656b2481cff |  | note | INSPECTION BY - UCCL
label | 0f5ca29d-62c5-5978-8c93-f4c91cdc9c7f |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 1ee6a460-bf9f-54a4-a3fd-8cac62b5145f |  | note | ACCEPTANCE CRITERIA - Producer statement to verify the products meet the requirements specified.
label | c205097f-5f10-5794-9bbe-79d786037b76 |  | note | UCCL - S
label | 77398384-eb10-5406-a15c-c765197f5298 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Completion Inspection inc. Construction Defects Report
label | f7ee1f7f-2893-5b43-b468-650af138b8ba |  | note | TEST REQUIRED - Completion inspection on each foundation by CEL
label | c67cbaa4-c23b-57e8-920e-335e6b37812e |  | note | INSPECTION BY - UCCL
label | fda6f7db-8920-5b25-b095-593b9c941b7f |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | d5732374-7b88-509d-a5ba-b0bb927b8e91 |  | note | ACCEPTANCE CRITERIA - Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out
label | f8626187-16fa-57df-9f13-dd764053e012 |  | note | UCCL - S
label | 28927bce-1a14-58e2-9cc9-5dd4a3318a30 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Identification of panels
label | b0b21fd9-849e-52d9-86ea-1616d263df96 |  | note | TEST REQUIRED - Panel identification location
label | d048a50e-758c-51af-bdf5-abdb933f6b4a |  | note | INSPECTION BY - UCCL
label | 9eb1c352-0b21-5155-861c-baa51c1999d1 |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 0f8830a4-8d47-53e0-a009-0dccd2b7137b |  | note | ACCEPTANCE CRITERIA - Panels to be marked and identified as to which pour they're from and final location.
label | d7b97580-fb04-5f19-965b-0dfa0f7344bf |  | note | UCCL - V
label | 832cb9ea-a5d9-52de-8e1c-d52b5f412223 |  | note | Client - R