## res_ITP_1_Inspection_and_Test_P
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP 03 - PCS Slab | itp |  |  |  |  | ITP 03 - PCS Slab
section | Pre Construction
checkpoint | Site Concrete
label | TEST REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to survey setout
label | ACCEPTANCE CRITERIA - Site concrete at correct level, and surfacewithin accepted tolerances (+/- 10mm).
label | UCCL - V
checkpoint | Survey Setout
label | TEST REQUIRED - Surveyor to set out PCS slab including duct recesses and bolt positions
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to steel reinforcing and formwork construction
label | ACCEPTANCE CRITERIA - Foundations shall be set out as per IFC drawings.
label | UCCL - V
label | Client - W
section | Materials
checkpoint | Concrete Mix Design
label | SPECIFICATION REFERENCE - Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03
label | TEST REQUIRED - Mix Design to be approved by Meridian prior to use
label | INSPECTION BY - UCCL/MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to use on site
label | ACCEPTANCE CRITERIA - Mix Deisgn as per specification (30MPa, 19mm) and approved by Meridian.
label | UCCL - S
label | Client - H
holdpoint | HOLD POINT
checkpoint | Steel Reinforcing
label | SPECIFICATION REFERENCE - Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03
label | TEST REQUIRED - Supplier documentation, photos
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to
label | ACCEPTANCE CRITERIA - Steel reinforcing comlies to specifications/IFC drawings/
label | UCCL - V
label | Client - W
section | Prepour
checkpoint | Formwork
label | TEST REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Dimensional check completed and within tolerances. Formwork installed inspected as being suitable for pouring concrete.
label | UCCL - H
label | Client - H
holdpoint | HOLD POINT
checkpoint | Steel Reinforcing
label | TEST REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL/MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Steel installed as per IFC drawings. Grade of steel as specified. Number, size and spacing of bars as per IFC drawings.
label | UCCL - H
label | Client - H
holdpoint | HOLD POINT
checkpoint | Foundation Earth
label | TEST REQUIRED - Visual Inspection, Continuity Test
label | INSPECTION BY - UCCL, MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Earth bars and cables installed as per IFC drawings. Continuity test completed and passed by MEL.
label | UCCL - H
label | Client - H
holdpoint | HOLD POINT
section | Postpour
checkpoint | Post pour inspection
label | TEST REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
label | ACCEPTANCE CRITERIA - Post pour inspection sheet to be completed following each PCS slab pour
label | UCCL - A
label | Client - W
section | Post Construction
checkpoint | As-Built Drawings
label | TEST REQUIRED - Survey as-nuilt drawings
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of Separable Portions
label | ACCEPTANCE CRITERIA - As-built drawings submitted to MEL.
label | UCCL - S
label | Client - R