## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 1786c2dc-0e43-48d2-bd80-dc91f6098fd3 |  | checklist | ITP 180 Control Cabling |  |  |  |  | Yes | ITP 180 Control Cabling | 10670ebf-8932-4d0b-915f-e7c96b9c2052
checkpoint-status | e02dad76-81d6-4716-bedf-9ea35c76f2b0 |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status | 2abbae36-bbc8-4250-866c-a59940a02b9e |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status | 1ba00e46-7e8d-4018-8c9c-2dbb63c2d455 |  | checkpoint | Ensure all control circuits are designed to function under the necessary circumstances that they will be required to function under
checkpoint-status | 5a3792e5-ff18-4cca-b50d-aaca6415493c |  | checkpoint | Ensure segregation is maintained pending cable insulation and shielding ratings
checkpoint-status | aec2c132-a2b0-4e97-a93a-e06164204182 |  | checkpoint | Ensure cables can communicate the specific protocols over the distances installed
checkpoint-status | c32e711f-37bc-4e25-af4d-9f5e5584f1d3 |  | checkpoint | Ensure the correct amount of cores have been supplied
checkpoint-status | d313ce64-a4c5-4408-b4c4-1530a4ac9f12 |  | checkpoint | Ensure the requirements of the system and if it requires to be normally open/ normally closed for the control/status that is required
checkpoint-status | 149d9c86-181e-48f6-acd1-cebbc604cd20 |  | checkpoint | Ensure all spares are left in an open state and labelled accordingly
checkpoint-status | 40e895fb-d916-41ce-a1cb-733c7371e602 |  | checkpoint | Ensure cable/cores can be easily identified for future works and maintenance
checkpoint-status | 7930c414-574d-49bb-bb54-cf4f365a4a26 |  | checkpoint | Low Level Inputs - Point to Point test individual cores at both the origin and the destination
checkpoint-status | 1e579568-629a-4245-b3c0-020c292ebacc |  | checkpoint | High Level Inputs - Confirm the software can be seen on the head end system
checkpoint-status | 24682c68-3d3c-4088-a47f-84d08d29ff57 |  | checkpoint | Activate functional devices and programming and confirm that the control system functions correctly eg. Manually Pressing Emergency Stop - turns off designated equipment
checkpoint-status | 422499eb-1af9-442c-89b7-20a46209d433 |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status | ad20a666-ced9-45a6-89bc-246682a671a4 |  | checkpoint | Cross check and verify that the as built drawings are complete and correct.
checkpoint-status | e184caf5-96ab-48e4-b0d3-7f21cdc789cb |  | checkpoint | Verify all inspections are complete and collate records.
checklist-sectioned | 8d89afa6-a214-413d-bf8d-1b0a956b4d32 |  | checklist | Testing & Commissioning ITP 167 |  |  |  |  | Yes | Testing & Commissioning ITP 167 | 147f3520-b794-4d74-9ce4-549dd79d8750
checkpoint-group | 7c39cdea-df9f-4e72-8375-e5c5dde52b17 |  | section | Safety
checkpoint-status | 7ca85f77-59cd-4412-b76c-e203d597915f |  | checkpoint | Project Risk identification and management register.
label | 0b3a566a-6e66-5168-98bc-364c09424c58 |  | note | Identify / acknowledge and manage risks involved with this task.
label | 3fb544c5-77fc-5401-87c3-79bec6802943 |  | note | Review the project risk register.
checkpoint-status | 6df1471d-d82a-470a-bc84-c0424e201ce5 |  | checkpoint | SWMS
label | eaf91449-013b-546a-b489-360174128893 |  | note | Ensure that all workers have reviewed appropriate SWMS and have signed onto SWMS.
label | 9898f1b8-e299-5fca-9f96-1e82aeb96c0a |  | note | Review
checkpoint-status | 46b3de25-b672-40f9-a34b-38ff7ba286a1 |  | checkpoint | Project Specific HSEQ management plan.
label | 4bde4618-20e6-5cd0-a013-aee223903306 |  | note | Review Project HSEQ management plan - these works must be fully compliant, site specific safety manual and SWMS have been submitted and accepted by the Principle Contractor.
label | 413e0c97-4526-5da9-aad5-84cd3ce251a1 |  | note | Review
checkpoint-status | dbe2d6ee-dd43-46fc-9062-6ed9be011994 |  | checkpoint | Review Fredon Procedures
label | 62fa9f92-efdd-55b2-be04-3298999cc7c3 |  | note | HSP-055 Testing an Electrical Installation
label | 4d6da747-37df-5be6-b4b8-fae908fa3aab |  | note | HSP-037 Live Work Policy Witness VOC
checkpoint-status | f8b8ee98-f216-4f23-90cc-0a666a7ecc72 |  | checkpoint | NSW Electrical Safety Regulation 2013
label | 6a6ae74a-cb6d-5724-a897-090518cf7ac5 |  | note | All Fredon Electrical personnel undertaking these works are qualified to carry out these works, and are trained, and competent in the use of all equipment and plant required to carry out these works.
label | 7cb5d77a-29d7-5f59-af30-e7aa9ab5f3c7 |  | note | Fredon Electrical Testing and Fault Finding Training & VOC in previous 12 months
checkpoint-status | d5906f7d-bef0-4a4f-81fc-9c077c5fa823 |  | checkpoint | Ensure workers whom are performing 'energised' testing hold current CPR and switchboard rescue certificate.
label | e54c4a43-b618-5f1d-9069-0c775ca6875d |  | note | These are to be renewed annually.
label | d2d47ba4-e268-5948-a3a4-560cee27cf0f |  | note | Witness
checkpoint-group | fd08a26f-6eee-4186-b5ac-682e7c6ff951 |  | section | Project Specific Scope Requirements
checkpoint-status | 5fdeef75-46ca-43eb-945d-2b173d50e27b |  | checkpoint | Insert project specific requirements here - specification ref, additional standard ref etc
label | d082fd9a-e3e8-5d91-95ff-6a5b1c0d3b05 |  | note | Review project specific documentation to ensure all relavent information is available any additional / supplementry testing requirements must be included within this ITP
label | d1fae888-e04d-5c2a-b7e6-3a94ae4e8e78 |  | note | ITCs for predecessor works complete
label | eed164e7-00ed-5e39-90ef-ef8d7c48ce01 |  | note | ITC - Switchboard pre-energisation
label | d25a9014-95d8-5f20-a64e-a2d781dc02da |  | note | ITC - Light & Power Fit off
label | b633b309-2e14-5fbd-804d-23baa89c9072 |  | note | As installed drawings complete
label | d59572f0-eed6-5d2a-b62c-a34d4002ea3c |  | note | Witness
checkpoint-group | d91b0c97-8917-4fba-aae7-59fe0c7f5c05 |  | section | Before Starting
checkpoint-status | 62af6628-a07e-499e-8ddc-beb212366d70 |  | checkpoint | Correct test equipment to complete the task
label | 15cd54c4-a611-54fc-a04a-cd18151bde6b |  | note | Insulation resistance tester - Ohmmeter;
label | edc8daf3-dba3-59d4-b829-0c90e498fcf7 |  | note | Voltage indicator (e.g. lamp, neon, LED device or meter);
label | af119dcc-5dd3-5fa4-9d1a-824e74a9742d |  | note | Suitable probes;
label | fe0edcee-6095-5817-a66a-8ed06f8e9fd6 |  | note | Trailing leads;
label | d212b52b-e128-51ef-b3f2-b65fe6bbde5c |  | note | A range of resistors of known values;
label | 4afc56a3-b7a2-55f9-af14-724488e8c2c6 |  | note | A suitable instrument for measuring fault-loop impedance; and
label | a3a48721-7a68-5fca-93f7-369c7c471db8 |  | note | A suitable instrument or device for checking the operation of a RCD.
label | c8ef5fa6-edbb-52d4-ad79-426eb98117f2 |  | note | Phase rotation confirmation instrument Witness
checkpoint-status | 2e552291-5cf1-4010-9006-4f2e3037ddc7 |  | checkpoint | Calibration
label | 4cc244c4-c6a4-50a2-9c19-a1233ae9858d |  | note | The test equipment / multimeters etc must display current calibration information. Witness
checkpoint-status | b93924db-c71a-40e8-a2fc-228f40f10e7d |  | checkpoint | Operation of test equipment
label | 1d74fea5-fb95-5db9-8ab5-238a706b5b3e |  | note | Ensure the electrician whom is to perform the works has been trained on correct operation of test equipment - multimeters. Witness VOC
checkpoint-status | ac985e34-ea55-43a5-9dc7-9ef7f1197b08 |  | checkpoint | Project specific - know the installation - be aware
label | c84a52b6-2b25-5323-90b7-462acb5bb925 |  | note | Ensure the electrician whom is perfroming the works is familiar with the installation - If required walk them through the proposed work zone. Discuss / Confirm
checkpoint-status | 886e328c-fe09-4b02-b6a2-cbe8a34aa958 |  | checkpoint | AS Standards - reference documentation
label | a9058116-c933-5130-a279-5bbb0c38a41b |  | note | Each electrician whom shall be performing these works must be given access to AS 3017-2017 Discuss / Confirm
checkpoint-status | d25d3833-8001-4199-a1da-4bef953e1812 |  | checkpoint | Red Line Markups
label | b7f15db0-2305-5165-b2e7-228975fe4a66 |  | note | Ensure the electrician performing the works has the latest redline marks up available and can easily identify circuit arrangements
checkpoint-status | 19dbfcee-c333-4efa-bc6d-675c9b556f18 |  | checkpoint | Complete ITC-167.1 / ITC-167.2
label | c6b6030e-5d76-5947-8fae-c05be4d74201 |  | note | Ensure the electrician whom is perfroming the works understands the requirement to complete the ITC [Inspection & Testing Checklist] associated with these works and that these works must be completed in accordance with Statutory requirements.
label | 6a8cf140-95cf-5f3f-a823-014945025ce2 |  | note | The electrician must enter their personal electrical licence number and acknowledge compliance via signature on ITC as works are completed.
label | a8508ae4-dedc-57b8-a43f-75a4808b0c15 |  | note | Review ITC-167.1 / ITC-167.2
checkpoint-status | 876633fa-d168-44ee-ae3e-0d296d657f84 |  | checkpoint | Electrical Certificate of Testing and Compliance
label | 662dabb9-a057-5de0-9b11-41673c6e49b2 |  | note | It is the Project managers responsibility to review complete ITC,s and compile the project testing / commissioning dossier for final review.
label | 08b79702-0202-53b6-b530-fb91a4633568 |  | note | The project manager shall then complete the certificate of electrical compliance and testing - This document must be presented to Fredon QTP [Qualified Technical Person] for project sign off.
label | 38a85860-5ad5-5e1e-aac2-1a2ce43a65ce |  | note | Certificate of Compliance
checkpoint-group | 18930e48-37de-43dc-8ae0-3935c0d3d1f1 |  | section | De-Energised Testing - Visual Inspection
checkpoint-status | 492d4017-841c-4586-98da-f7d0250eff8f |  | checkpoint | A visual inspection shall be made when work on an electrical installation has been completed in order to verify that the work complies with the requirements of AS/NZS 3000.
label | d816e841-12cd-54d7-a0ef-ee8bb34bdecd |  | note | The visual inspection shall be carried out before, or in association with testing, and should where practicable be made before the relevant part of the electrical installation is placed in service.
label | abf9493f-12f1-59f0-837f-4c8241daaa49 |  | note | Where the visual inspection of a part of the electrical installation is not practicable at the completion of the work, e.g. not accessible due to enclosure in the building structure, consideration should be given to inspecting that part during the course of the installation.
label | 72d9dd1e-bc79-5fe2-8736-c2eeb6130cae |  | note | Refer to AS 3017 section 2 for further detail.
label | b8785b79-bc1d-57e7-80ac-b8378268998f |  | note | Complete ITC-167.1 / ITC-167.2
checkpoint-group | c5b65764-5fc0-4d14-a13a-ca1ef27bc4ab |  | section | De-Energised Testing - Earth Continuity Resistance
checkpoint-status | 23c467be-dcd2-4e30-b4ac-f1040848f019 |  | checkpoint | Earth continuity and resistance tests are necessary to ensure that the earthing system has been installed in an appropriate manner and the resistance of the protective earthing conductor is low enough to permit the passage of sufficient current to cause circuit protective devices to operate if there is a fault between live parts and exposed conductive parts.
label | 79260149-6077-523a-9145-65c3bfe0ed41 |  | note | NOTE: This may include cable tray, Stainless kitchens etc
label | 85b1072e-ba87-5235-8c29-c3089e85bc76 |  | note | Refer to AS 3017 section 3.1 for further detail.
label | 649b4f4a-dc1c-5097-b56f-3eb337db260e |  | note | Complete ITC-167.3
checkpoint-status | f7ae9e55-4de1-4e54-b10c-800b6145393e |  | checkpoint | Earth continuity and resistance tests are required for Communications Cabinets with shielded and sensitive equipment requires to have a clean direct earth.
label | df2918b2-abe7-5cc9-9313-9c5d35918c9e |  | note | Refer to AS S009 Pass Less than .5Ω
label | f9759d32-88dc-5a56-960b-39b423ef8637 |  | note | Complete ITC-167.3
checkpoint-status | bce7f189-2f32-40f3-9380-5a3f3e27f652 |  | checkpoint | Note: The continuity of protective earthing conductors may also be verified by measuring the earth fault-loop impedance of the circuit.
label | 0aad2841-2394-5cd2-a111-2bc1e9869c04 |  | note | See 3.6.4.2 refer table 3.2 for values Complete ITC-167.1 / ITC-167.2
checkpoint-status | 0a992b3c-78f7-4f36-9f24-4e840715d70c |  | checkpoint | The insulation resistance tester used shall be able to maintain its terminal voltage within +20% and -10% of the nominal open-circuit terminal voltage, when measuring a resistance of 1 MΩ on the 500 V range or 10 MΩ on the1000 V range.
label | df7cb230-80ee-5697-b307-6b146a13b08b |  | note | When applying the insulation resistance test to electronic equipment or surge protection devices, care should be taken to prevent damage to the devices.
checkpoint-status | b0f82bdd-d305-4118-a764-e5c2f2e57c1b |  | checkpoint | Results The resistance of protective earthing conductors shall be
label | 4601a737-25f9-5a4c-8607-02aec1c68e57 |  | note | (a) low enough to permit the passage of current necessary to operate the overcurrent protective device; and
label | 3c1a8de7-e006-5161-99b7-0f043cd69968 |  | note | (b) consistent with the length, cross-sectional area and type of conductor material. The resistance of the main earthing conductor or any equipotential bonding conductor shall be not more than 0.5
label | 90900985-3a45-5b18-9f4f-f404f16517fc |  | note | NOTES: 1 Under the subsequent tests for earth fault-loop impedance, the maximum allowable resistance of the protective earthing conductor associated with any particular circuit depends on the type and rating of the protective device and the impedance of the live conductors that comprise the circuit.
label | 87eef55c-6f61-5c28-9b91-8860189802f7 |  | note | 2 Resistance values (Re) for earthing conductors are given in Table 8.2 as a function of the rating of the associated overcurrent protective device. These values may be used when testing for earth continuity.
checkpoint-group | e058f04a-33b1-4ecb-b730-097a59443d7a |  | section | De-Energised Testing - Insulation Resistance
checkpoint-status | c958b411-e2e6-4ef1-a2cd-5e52f1c1b9b4 |  | checkpoint | Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation. This is to prevent:
label | 9599e05f-88bb-58c2-bea6-3d35a7782735 |  | note | (a) Electric shock hazards from inadvertent contact;
label | d9384f66-dd6f-54c4-8b93-9aae711a8f79 |  | note | (b) Fire hazards from short-circuits; and
label | f8992054-8647-5fc0-ab08-9b3475229290 |  | note | (c) Equipment damage.
label | e5cdf59e-f3b0-51d7-84f6-e07258685c5c |  | note | In addition, insulation resistance tests between all conductors are necessary for consumers mains and submains to minimise potential for insulation breakdown, injury or property damage due to failure of such conductors. The integrity of the insulation is stressed by applying a direct current at 500 V, or 167 V for equipment described in 3.2.4(e) which cannot be isolated. The insulation resistance between:
label | ff0ed00e-37f4-5282-a250-7f20d9371b22 |  | note | (a) the conductors of consumers mains and submains; &
label | f72ef866-d4e2-5440-a41a-8f4087659d97 |  | note | (b) live and earthed parts of an electrical installation, or parts thereof, including consumers mains and submains shall be not less than 1 MΩ.
label | eed8620a-4f6a-5076-ad85-ffef8b8d0d4e |  | note | Refer to AS3017 section 3.2 for further detail
label | 1433e3d4-2e5b-5eee-aad2-70183389dd72 |  | note | Complete ITC-167.1 / ITC-167.2
label | 677aa97a-9da0-57f3-8030-93a57b0b53b4 |  | note | Note - If luminaires have been installed - all switching devices should be 'on' - Test only between 'live' conductors and earth.
label | bf8a2be3-ef1b-56e4-8fdf-73901737a8b8 |  | note | Note - If luminaires have not been installed - all switching devices should be 'on' - Test between all conductors and earth.
checkpoint-group | 3d737b9d-76da-4c44-bc4e-9db768b1b5f6 |  | section | De-Energised Testing - Polarity
checkpoint-status | 2c584f8b-61de-48c5-8942-6e57e0a11487 |  | checkpoint | Polarity testing is necessary to ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors. This testing is to ensure:
label | 24343b00-b249-5427-ac77-65ca34c69bb1 |  | note | (a) Active and neutral conductors of the consumers mains or submains are not transposed resulting in the electrical installation earthing system becoming energised;
label | a7e20b94-bef7-5d6b-a1b4-8ed2d95542e1 |  | note | (b) There are no combinations of incorrect active, neutral and earthing conductor connections resulting in the exposed conductive parts of the electrical installation becoming energised; and
label | 79ad8a20-4e2b-5643-9204-d203be6ec9c8 |  | note | (c) Switches do not operate in neutral conductors, resulting in parts of appliances, such as heating elements and lampholders, remaining energised when the switches are in the ‘OFF’ position.
checkpoint-status | f2cb32f6-8f77-4acd-a0df-01858273fd77 |  | checkpoint | Requirements
label | 6b7442ea-5cf4-51d3-abd1-73502ef44608 |  | note | (a) Every single-pole switch or protective device shall operate in the active conductor of the circuit in which it is connected;
label | a7cee0d1-bbf1-5211-9645-72195fa5c39e |  | note | (b) A switch or protective device of a multi-phase circuit, other than some types of motor overload protective devices, shall operate in all active conductors of the circuit in which it is connected;
label | c6504652-315e-5064-a72b-dac3ee8be1ea |  | note | (c) RCDs required to switch all live conductors shall switch the active and neutral conductors of the circuit;
label | b4f32b92-1d49-50ff-b439-bc243e50e077 |  | note | (d) Where multi-phase socket-outlets of the same type form part of an electrical installation the phase sequence of the socket-outlets shall be the same (see 3.5);
label | 5f8bfafa-1efb-5940-aeab-b9298eca178a |  | note | (e) Socket-outlets which accommodate flat-pin plugs shall be connected so that, when viewed from the front of the socket-outlet, the order of connection commencing from the slot on the radial line shall be earth, active and neutral in a clockwise direction;
label | 8ec3f6ac-795f-5843-8c8c-8c097d451043 |  | note | (f) All neutral conductors shall be connected to the neutral bar of the switchboard; and
label | 2c466e61-c3e6-5d5f-8e75-7987ef91a22f |  | note | (g) The consumers mains neutral shall be connected to the neutral bar of the main switchboard.
label | ac5ce141-17c3-5d43-9de5-24b496e1ec01 |  | note | Refer to AS3017 section 3.3 for further detail.
label | b1e0e980-0e0e-511b-ae8b-538e5f3e691d |  | note | Complete ITC-167.1 / ITC-167.2
checkpoint-group | b0ea4bb2-8653-4e47-b783-4622eaefe14b |  | section | De-Energised Testing - Correct Circuit Connections
checkpoint-status | ef20fa07-3aa1-4d98-a4e8-85c0b953a227 |  | checkpoint | Tests for correct circuit connections are necessary to ensure the following:
label | 5e03b02f-130a-5b22-b33f-fbe1a86d8d92 |  | note | (a) Protective earthing conductors do not carry current in non-fault conditions; and
label | f655e9b4-8274-5b04-a5ba-a9f261ee0abf |  | note | (b) No short-circuit exists, because a short-circuit current flowing between live conductors and through part of the earthing system can cause considerable fire damage or personal injury, particularly in high current locations.
label | 1f9fab88-cb90-52de-b96a-b2776709d1fa |  | note | Refer to AS3017 section 3.4 for further detail.
label | 37896d16-639b-586f-ae7e-55341104ad3b |  | note | Complete ITC-167.1 / ITC-167.2
checkpoint-group | 4d987e89-8365-4f4e-8656-4a8bdbd7b5a2 |  | section | De-Energised Testing - Earth Faultloop Impedance
checkpoint-status | a32c87ce-413d-4214-ab49-1920d80844b4 |  | checkpoint | 3.6.3.2 Supply not connected
label | c67b63e5-4372-5cad-9aea-71012bec60ce |  | note | When tested in accordance with 3.6.4.2, the total resistance (Rphe) of the active and protective earthing conductors of an individual circuit which forms part of the earth fault-loop shall not exceed the values shown in table 8.2.
label | aeb0499f-380e-586c-9ed6-90a509de42c1 |  | note | NOTE: The values calculated must be accumulative of submains etc.
checkpoint-status | 8b1e8fdb-5e89-44f5-9cba-b701171e9012 |  | checkpoint | The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault-loop to cause a protective device to operate within a specified disconnection time.
label | 27ec159b-102e-5c5f-8eb9-755b4b02f5d9 |  | note | Refer to AS3017 section 3.6 for further detail.
label | deee592b-fb74-5f84-a037-50fc133f6458 |  | note | Complete ITC-167.1 / ITC-167.2
checkpoint-status | a54b61a0-1dd4-41a0-88fa-c961b14bcc4b |  | checkpoint | Dead testing complete
label | 9765fecc-583b-5a0a-9b46-1ae104bebdc2 |  | note | Upon completion of 'dead' testing present all documentation to Site supervisor for approval
checkpoint-status | eb2e04d4-8a1b-49bd-8c47-e66f6859fe89 |  | checkpoint | Submit test results for review with site management
label | 510fbf8a-5732-54b8-9dec-d46282c2bad4 |  | note | Site supevisor reviews ITC for completeness.
label | e8e6f403-2abb-5ab5-bb31-5cd2d7625c8f |  | note | Note: Fredon supervisor is not responsible for test result accuracy.
label | 7c61a2ec-046a-519a-9a9f-f6dbaec21d37 |  | note | Review / issue permit energisation Permit (HSF-091)
checkpoint-group | f4a5cba0-827e-4400-b5e9-813456377917 |  | section | Energised Tests - Tests for Voltage
checkpoint-status | 73629a53-3086-43a9-8f81-199f914e8f64 |  | checkpoint | Using test lamps / voltmeter
label | d8051c2e-003b-58a4-b5ab-33ac2f7a2fae |  | note | Main switch off
label | 170f1bf6-fdd1-5dcd-87ed-e96000d53ad0 |  | note | ○ Confirm supply is present at Line side of main switch.
label | c7410f3f-ec9c-598d-a305-03ab8c5da5b4 |  | note | ○ Confirm supply is not present at Load side of main switch.
label | 04d90a52-da3c-523b-ae3a-460e8533925f |  | note | Main switch on - sub circuit (CBs) off
label | 38e8075c-df2c-5276-96c6-e379aaf2a1df |  | note | ○ Confirm supply is present at Load side of main switch.
label | 4ab7df78-c5b9-5660-8c7c-481f49d2b8de |  | note | ○ Confirm supply is present to line side of relative distribution circuit breakers. Complete ITC-167.1 / ITC-167.2
checkpoint-group | b2cae5f9-b7e7-4167-93a1-70538c2b8c3a |  | section | Energised Tests - Phase Rotation
checkpoint-status | 873f44e7-cdaa-41ec-9b41-32984e36589f |  | checkpoint | Using test phase rotation meter.
label | 0f3b12e2-f032-5ffd-9f10-6d8822673100 |  | note | Confirm phase rotation sequence.
label | ebeb5199-c903-5ff4-adab-bf5a3697c0a6 |  | note | Complete ITC-167.1 / ITC-167.2
checkpoint-group | 397637f3-9910-4b19-829c-016fb6344889 |  | section | Energised Tests - Earth Fault Loop Impedance
checkpoint-status | 6461956e-5178-4f4e-83e9-dda884f53df5 |  | checkpoint | 3.6.4.1 Supply connected
label | d4fbe468-e6fb-5100-b761-c9c6e1061152 |  | note | The earth fault-loop impedance should be measured using an instrument that has a facility for measuring and indicating low values of impedance.
label | 4baca61f-004d-583e-8ff6-d2f609ab5c69 |  | note | NOTE:
label | 09b0ed6d-9168-5d92-916a-2ef60a72e472 |  | note | (2) Earth continuity and resistance tests should be carried out on protective earthing conductors in accordance with 3.1 before measuring the earth fault-loop impedance.
label | a07e5728-b220-5701-abe5-2ac1325e09df |  | note | (3) It is preferable to measure the earth fault-loop impedance using the permanent network supply rather than a temporary supply.
label | d45c15f1-7584-53b6-8210-927e56fcd471 |  | note | (4) The measuring circuit includes the impedance of the flexible test lead, which must be as supplied with the meter. If the meter leads are fused, the fuse resistance must be taken into account. The MEN connection is to be left intact.
checkpoint-status | e6b15eb0-8f91-47be-b003-dff2793b88ed |  | checkpoint | Maximum values of earth fault-loop impedance shall not exceed the values shown in table 3.1 or the value of Ia for the protective device being used in accordance with the manufacturer’s data.
label | 83ca9ebd-21df-5f9e-826b-2312b2316441 |  | note | Refer to AS3017 section 3.6 for further detail. Complete ITC-167.1 / ITC-167.2
label | 50dc4acf-a768-50c2-8f05-e9eb68064158 |  | note | Note: If an RCD operates during the earth fault-loop impedance test, the test result is considered satisfactory.
checkpoint-group | 1cd9a98b-ddd0-47c3-8b71-45843c4e7faf |  | section | Energised Tests - Operation of Residual Current Devices
checkpoint-status | 3b0dde2c-889c-468c-aa14-e7319b781c79 |  | checkpoint | Testing of an RCD is carried out to ensure that the RCD operates and disconnects the designated circuit. The function of the RCD is verified by the operation of the integral test device, or by the use of special test equipment
checkpoint-status | db520dea-55dc-492f-98aa-5efdcbb22cd4 |  | checkpoint | Operation of the integral test device shall cause the RCD to trip and disconnect the designated circuit.
label | e40aa1d4-8a2c-5063-83b8-35413cfd1800 |  | note | NOTE:
label | 3be254d7-4f78-58ae-b099-5d415077efc6 |  | note | (1) Tripping the RCD by means of the integral test device establishes:
label | c7e168c6-7952-5084-a2c2-4d95e8da8b77 |  | note | (a) That the RCD is functioning correctly; and
label | 12f65dbf-5cd7-564c-834e-ef9716104744 |  | note | (b) The integrity of the electrical and mechanical elements of the tripping device.
label | a16bc8d8-a964-5d0b-9508-edd21805608f |  | note | (2) Operation of the integral test device does not provide a means of checking:
label | 79ce7867-7701-52fb-829c-a5bcff634853 |  | note | (a) The continuity of the main earthing conductor or the associated circuit protective earthing conductors;
label | 5a27f5a4-3866-5c84-821a-d2d2ebc54a38 |  | note | (b) Any earth electrode or other means of earthing; or
label | 4a200032-d3d4-5ce6-9177-7be317886a54 |  | note | (c) Any other part of the associated electrical installation earthing.
label | 79a05826-c123-5702-b897-094c009585f2 |  | note | (3) Tripping the RCD by means of the integral test device, or by special test equipment such as a test plug with a resistor between the active and earth pins, may be used to verify that the circuits required to be protected by the RCD are protected.
checkpoint-status | 45c8c197-23b4-4787-91d7-55cf1062c2af |  | checkpoint | RCD is to be tested using functional trip test and trip times must be recorded. Complete ITC-167.1 / ITC-167.2
checkpoint-group | cfb2ae80-0a7e-46ad-845f-34f87afa16cd |  | section | Energised Tests - Final Inspections & Safety Checks
checkpoint-status | 54a3e490-9248-44e1-b0f0-0cfb3e84954e |  | checkpoint | Final Inspections: At works completion confirm all circuit schedules are complete & correct.
checkpoint-status | 9b3a0802-2df3-409e-801a-7f324ccb1b7c |  | checkpoint | All circuit descriptions are clear & worded to be easily understood.
checkpoint-status | 9c0ed3d1-23c0-46c0-83fe-3c33ed6853c9 |  | checkpoint | Any circuits not tested remain disconnectd from circuit breaker & terminated in BP connected.
checkpoint-status | ac62130c-da51-496e-b468-afc6f54582e5 |  | checkpoint | All equipment has been labelled in accordance with project requirements, and labelling aligns with as built drawings.
checkpoint-status | 987f16ee-e101-4f3d-8f28-97e210dcb791 |  | checkpoint | Ensure that any changes made during testing which effect as built documentation are captured via RED pen mark up on drawings.
checkpoint-status | 16ea6f24-c62e-4c98-8732-907124df02a2 |  | checkpoint | Compile list of any incomplete works or defects which require rework.
checkpoint-status | 524d6fd0-660b-42c0-bafa-de35b8631a48 |  | checkpoint | Re-instate all switch board covers, doors and panels. LOCK THE SWITCH BOARD DOOR & CHECK ALL OF THE ABOVE
checkpoint-group | 249cfbb5-e002-4390-b1cb-7cf9cfff69dd |  | section | Energised Tests - Completion
checkpoint-status | 1ae631dc-8cda-4969-9a2a-d41ce0548311 |  | checkpoint | Documentation - Once complete:
label | 93b01727-db1c-5123-a53c-6972e548348a |  | note | 1. Review documentation for correctness.
label | e79f0ba6-b4ef-5b42-91b3-16110ec28ea0 |  | note | 2. Submit documentation to site supervisor immediately.
label | b75c42cd-5b2b-5676-9ee9-4bea895f85f3 |  | note | 3. ITC-167 complete & signed
label | 670bd9df-5035-57f1-bc60-44a4447a926f |  | note | 4. RED pen mark up of zone drawing for as built information.
label | de317fc5-bf11-5b1a-a6f3-a97109cb4c62 |  | note | 5. DB schedule information.
label | 96409bb9-32f9-5d43-8d97-b6233bc2867c |  | note | 6. Concise list of incomplete or defective works. (DO NOT LEAVE ON SITE)
label | 356b7d93-b1e9-5e25-b583-79c730582c8a |  | note | 7. Submit
checkpoint-status | 035265fc-2d95-458a-9b89-2319fb1b8a8b |  | checkpoint | Fredon site supervisor shall review all documentation
label | c5b6af6a-9af9-568f-ab09-f7a322020eb5 |  | note | Note Fredon supervisor is not responsible for test result accuracy
label | 4577cf44-a58a-5407-959f-80db95c635b0 |  | note | Review
checkpoint-status | d4f68046-8f6e-48ab-93bf-f3fc4a445e27 |  | checkpoint | Fredon Project Manager to provide certificate of testing and compliance Certificate of Compliance
checklist-flat | c31b197f-5fcc-4285-a670-fb2381103db2 |  | checklist | SYS - Fredon Compliance |  |  |  |  | Yes | SYS - Fredon Compliance | 1d0fe7f7-e94d-42db-96ce-c1620ef67d9d
checkpoint-status | 8b704297-2d47-435b-a0fb-3ba251abac4c |  | checkpoint | Fully compliant, site specific Safety Manual and SWMS have been submitted and accepted by the Principal Contractor.
checkpoint-status | 91d5c165-17c8-4994-b8bb-3732eb718b9c |  | checkpoint | All Fredon electrical personnel undertaking these works have been trained and inducted in the Safety Manual and the relevant SWMS for these works.
checkpoint-status | 60c4ae14-20eb-48a8-ab9b-1c6b61682845 |  | checkpoint | All Fredon electrical personnel undertaking these works are qualified to carry out these works, and are trained, and competent in the use of all equipment and plant required to carry out these works.
checklist-flat | 687f30d4-ffd8-4991-9e8c-996ccc7c341f |  | checklist | ITP 173 Fit Off Light Fittings |  |  |  |  | Yes | ITP 173 Fit Off Light Fittings | 207bef2b-c193-4b80-a8c7-8f889e3cb842
checkpoint-status | ade27e60-d244-4453-aa40-2c0c60b0e7ed |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status | f066451c-9aa3-4f23-8d53-411b08df1777 |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status | 0ea42a76-51d3-467f-8d1e-444dd313be36 |  | checkpoint | Ensure that the latest co-ordinated service drawings are being referenced
checkpoint-status | 7ac33ca8-a51d-4731-8879-ec9c47b1106b |  | checkpoint | Ensure that the latest co-ordinated drawings are being referenced Not Required
label | e66badb7-f38c-51ff-a4d7-67fd774e1c6f |  | note | Understand physical characteristics of light fitting to be installed. Recessed fitting cut out dimensions. Lineal fitting lengths v fixings. Height of fittings. Architectural requirements - light spill direction
checkpoint-status | 5ac8ff28-1e82-4237-a4ad-4c7072530b87 |  | checkpoint | Ensure the fitting is compliant with Australian Standards
checkpoint-status | 854f77fa-7594-4bb0-959d-5740cad30dce |  | checkpoint | Install fittings as per manufacturer's recommendations
checkpoint-status | fdea0450-7a2f-4ab9-99c4-6c92bc6dd16c |  | checkpoint | Ensure that the correct fitting is being installed for each location as per drawings
checkpoint-status | 54eeb41f-33ba-4b85-80b3-619d27cf5444 |  | checkpoint | Ensure that the correct mounting method is being used i.e. surface, chain suspended, recessed etc. Check all drawings prior to installation
checkpoint-status | aa750693-ec51-4d80-b4b2-0225cad8434e |  | checkpoint | Ensure fittings are installed using the correct fixing type
checkpoint-status | b2e4150d-cced-4d2a-94b6-f7baf61786c7 |  | checkpoint | Ensure that any required ceiling grid removal has been carried out by ceiling fixers only. UNDER NO CIRCUMSTANCE IS CEILING GRID / CHANNEL TO BE CUT BY FREDON ELECTRICAL PERSONNEL
checkpoint-status | d1df3a9a-3c51-4637-89cf-b95c00379a77 |  | checkpoint | Ensure that ceiling mounted fittings are adequately supported according to their weight. Additional supports added to the ceiling where necessary
checkpoint-status | 86f1ace2-ef0d-4ede-b4e2-c152810a5306 |  | checkpoint | Ensure that all terminations are correct including lighting control terminations and are as per manufacturer's requirements
checkpoint-status | 9778cd09-7ce4-45be-a3c3-df3ae722253b |  | checkpoint | All light fittings have been installed in a tradesman like manner (Straight & level etc)
checkpoint-status | 0cf52720-2bef-4b7b-b700-f551c76693f1 |  | checkpoint | Install fittings as per manufacturer's recommendations
checkpoint-status | 813cbeac-7695-445d-9286-d59e21d7a6c1 |  | checkpoint | Ensure that the correct fitting is being installed for each location as per drawings and visibility of escape lighting meets AS 2293. NOTE: Directional arrows show correct path of egress and the luminaire has the Emergency label attached
checkpoint-status | e15f41a8-c3ea-469e-b674-d72550886137 |  | checkpoint | Ensure that the correct mounting method is being used i.e. surface, chain suspended, recessed etc. Check all drawings prior to installation
checkpoint-status | 5d400545-1c88-4d44-859b-2f0e699b9728 |  | checkpoint | Ensure fittings are installed using the correct fixing type
checkpoint-status | 966baa13-9a70-4150-981c-1b0d66e92526 |  | checkpoint | Ensure that any required ceiling grid removal has been carried out by ceiling fixers only. UNDER NO CIRCUMSTANCE IS CEILING GRID / CHANNEL TO BE CUT BY FREDON ELECTRICAL PERSONNEL
checkpoint-status | d4bd8c54-9386-4f54-9f89-49e0670182ea |  | checkpoint | Ensure that all terminations are correct including monitoring terminations and are as per manufacturer's requirements
checkpoint-status | 49b458b1-2b29-4ecf-8c81-c6f5ea3b0f97 |  | checkpoint | Ensure that ceiling mounted fittings are adequately supported according to their weight. Additional supports added to the ceiling where necessary
checkpoint-status | 24cadd28-e0a1-4a46-836e-93c82e1ef339 |  | checkpoint | All light fittings have been installed in a tradesman like manner (Straight & level etc)
checkpoint-status | edb0e902-ff66-4b31-9c1b-3402449e0d86 |  | checkpoint | Ensure all emergency lighting information is kept on As Built information. Fitting number. Circuit suppling fitting. Fitting serial numbers etc.
checkpoint-status | 700633b4-945d-4bc8-80fc-a51666bb62a6 |  | checkpoint | Ensure that the lighting control philosophy is understood. Cable requirements. Cable polarity. Cable connections.
checkpoint-status | 4e5ef87f-636e-42d0-abb7-e5702fc8a00d |  | checkpoint | Ensure all fitting information is kept on as built information. Fitting number. Circuit supplying fitting. Fitting serial number etc.
checkpoint-status | 34edade0-9678-4313-8e11-4291334ce735 |  | checkpoint | Visually inspect entire circuit for completeness Ensure fittings are protected if required Remove all rubbish - empty boxes etc.
checkpoint-status | 1fac6c23-bf39-4dcf-8242-0a6a956e39c8 |  | checkpoint | Check that all ceilings, walls and floors are left neat and tidy and without any damage. IF DAMAGE OCCURS ADVISE FREDON SITE MANAGER IMMEDIATELY
checkpoint-status | 1abd2b0b-fe5b-4988-8ac8-11e0bf2de93b |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checkpoint-status | 258f5de0-0d34-43e5-aaf6-d7464f996b31 |  | checkpoint | Verify all inspections are complete and collate records
checklist-sectioned |  |  | checklist | SWMS |  |  |  |  | Yes | SWMS sectioned | 2e2db2dc-b36d-4144-bfdb-ff188ad8ed0f
checkpoint-group |  |  | section | Site Induction for all Elite Mechanical Solutions Pty Ltd Staff & subcontractors
checkpoint-status |  |  | checkpoint | Ensure inductions to site for all Elite Mechanical Solutions Pty Ltd Staff & subcontractors.
checkpoint-status |  |  | checkpoint | Elite Mechanical Solutions Pty Ltd to ensure all subcontractors have their own SWMS approved by management and staff have read and signed off on Elite Mechanical Solutions Pty Ltd SWMS.
checkpoint-status |  |  | checkpoint | agree to scope of works with Site Manager (including how other trades will be excluded/ restricted from work area)
checkpoint-group |  |  | section | Preparation and Planning for Job; Working with Services
checkpoint-status |  |  | checkpoint | Ensure employees are adequately trained to complete the job required.
checkpoint-status |  |  | checkpoint | Provide adequate and competent supervision.
checkpoint-status |  |  | checkpoint | Provide correct equipment to ensure job is completed safely.
checkpoint-status |  |  | checkpoint | All unqualified staff to be supervised at all times while on site by a suitably qualified tradesperson.
checkpoint-status |  |  | checkpoint | Check Mirvac Working with Services Document to ensure complying with requirements.
checkpoint-group |  |  | section | Assess work Area for hazards.
checkpoint-status |  |  | checkpoint | SITE WALK – IDENTIFY SERVICES.
checkpoint-status |  |  | checkpoint | Thoroughly inspect work area and access pathways for hazards; Wear appropriate PPE, adhere to all signs and site requirements. Follow Traffic Management procedures.
checkpoint-status |  |  | checkpoint | Ensure adequate lighting & ventilation.
checkpoint-status |  |  | checkpoint | Ensure adequate fall protection measures are in place if working at heights
checklist-flat | 1cef89b8-265b-446b-bf9d-bc5ec7c925c8 |  | checklist | ITP 169 Mains & Sub Mains Installation |  |  |  |  | Yes | ITP 169 Mains & Sub Mains Installation | 456cedee-b0b3-4814-b342-5e8635ea177f
checkpoint-status | 4f615875-fd8b-4300-ad9c-f327e108c978 |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
label | 9919b156-2907-5cb5-baa6-83592534c38f |  | note | For sub main installation information follow Fredon sub main installation check sheet. The check sheet will have all necessary information such as; cable size, origin and destination. This sheet is to be followed and filled out to verify correct installation. COMPLETE ITC 169.1
checkpoint-status | 34cff115-52d8-44f2-9d7f-fe6a355b0d89 |  | checkpoint | All submains dressed in the formation specified on Fredon sub main installation check sheet.
label | 8002e059-930d-5fc4-a4c9-f436467a73af |  | note | When using a winch, maximum cable pulling tensions are not to be exceeded, refer to cable manufacturer's technical data for maximum pulling tension
checkpoint-status | 99676cd8-e131-4ba3-989e-3cbd09008082 |  | checkpoint | All parallel submains dressed on cable tray/ ladder have been spaced correctly to minimise derating and satisfy all standards specs and regulations NOTE: AS3008 Table 23 & Table 24
checkpoint-status | 91b88223-f33f-40ad-bd96-f44ca2ed90ac |  | checkpoint | All fire rated submains have been dressed with steel cable ties NOTE: Essential Safety Services require their own Fire Rated Support and cable pathway
checkpoint-status | a7a9b976-1f52-43e4-83c5-a7571ff0d0e6 |  | checkpoint | Mechanical protection installed where required.
checkpoint-status | 4fd886d3-b356-4640-9e8e-42258e4f63be |  | checkpoint | No cables to be tied to or supported by sprinkler / water pipes.
checkpoint-status | 441e3950-82ff-490d-9fd7-99bc703d5cdb |  | checkpoint | All submains have been kept clear of sharp edges during installation to avoid damage to insulation.
checkpoint-status | ddccd516-f763-4160-8560-0be73afc0613 |  | checkpoint | Visual inspection of rough in carried out to ensure completion
checkpoint-status | f78b0a6b-1c0e-4f43-a0ca-692d43c04f9f |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for
checkpoint-status | 4d4b2777-9134-4256-a4c8-57d39f6e4bea |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
checkpoint-status | f1f752be-b6cf-4ea0-8f6f-dce0ba3485c2 |  | checkpoint | Cross check and verify that the as built drawings are complete and correct
checkpoint-status | 89b8d93c-690c-4c97-a362-f943e97a3037 |  | checkpoint | Verify all inspections are complete and collate records
checklist-flat | a6c85981-98a0-4101-8bff-928fa33b3ade |  | checklist | ITP-168 Switchboard Inspections |  |  |  |  | Yes | ITP-168 Switchboard Inspections | 46bb37ed-06dc-49ba-a2eb-871df877c2fd
checkpoint-status | 52d432c8-90d6-4d9d-8206-bb2f7ce42436 |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status | 9708c654-ecb2-424d-9dd9-f465e00152f5 |  | checkpoint | The updated / superseded drawing register, located next to the drawing rack in the site office, has been checked to ensure the latest revision drawings are being referenced
checkpoint-status | 87e6a1f2-b721-49e1-a166-1527ce72446a |  | checkpoint | Ensure the switchboard drawings have been reviewed and approved by the consultant
checkpoint-status | 72edb533-e8c5-4e06-aa2f-79d3924ed9fb |  | checkpoint | Ensure all new installations have been coordinated with other services, both new and existing.
checkpoint-status | 4526a30a-4224-4ff7-a150-651a44feea69 |  | checkpoint | Location & Position of Switchboard
checkpoint-status | abe75b12-1f36-4ace-9145-8cde3cc08658 |  | checkpoint | Supply Authority Access Requirements
checkpoint-status | d5afc92e-ebe7-48fd-b8b9-3c2ec971c549 |  | checkpoint | Physical Clearances in & around switchboard area
checkpoint-status | fba2dde4-9337-43fe-95b3-c6b49bbdc0d2 |  | checkpoint | Ensure proposed switchboard location is secure
label | a9416cae-2210-5c90-86d3-6552c301c0a8 |  | note | Doors on rooms / cupboards etc.
checkpoint-status | c6fc324c-c411-4058-bf81-9026dec9e427 |  | checkpoint | Signage is installed
checkpoint-status | eb30c3a9-f93c-4fba-bd84-87683580b732 |  | checkpoint | Structural supports in place
checkpoint-status | 33b6e2d8-d39c-47d7-bece-35c1645fddc5 |  | checkpoint | Carry out pre-delivery inspection at workshop
checkpoint-status | 91ad48ab-3b6c-4101-8d0e-5fcd35853b19 |  | checkpoint | Inspect workmanship and take quality control photograph. Attach or take photo of weight & lifting information
checkpoint-status | 52e24990-1455-4e6b-a2e3-2f3508d85971 |  | checkpoint | Confirm has the manufacturer supplied workshop QA & FAT documentation
label | b567f765-a23c-538e-8055-696f6cf8fbce |  | note | Fredon to issue switchboards FAT documentation for review
checkpoint-status | c70e88c4-d258-4637-bfb7-cad8b086461e |  | checkpoint | Check for obvious signs of damage DO NOT ACCEPT DELIVERY IF DAMAGED
checkpoint-status | c8a1eacc-c997-4acf-940e-8a090f385b53 |  | checkpoint | Check for delivery of quality control and quality checklist completed from factory DO NOT ACCEPT DELIVERY IF NO DOCUMENTS
checkpoint-status | a369fb8e-a2be-4191-8d58-9939a2aaceaf |  | checkpoint | Plan and resource installation task appropriately
checkpoint-status | 68f1d899-82c8-4575-849a-e18d95f2379e |  | checkpoint | Use only proprietary lifting and rolling equipment
checkpoint-status | 7f7c3e49-09fd-40eb-b79d-cc8e7de62848 |  | checkpoint | Clear route to switchboard installation location
checkpoint-status | 47542b3f-e296-43f1-b381-eb0c86348f9f |  | checkpoint | Clear installation area completely of any obstacles, rubbish, personnel etc.
checkpoint-status | 5c0fde3c-f3f1-463a-9fd2-c8ea8fa64afe |  | checkpoint | Switchboard mounted using correct fixings with additional structural support added where required
checkpoint-status | 071968fa-87bd-43c1-9239-729fb7b954d5 |  | checkpoint | Switchboard mounted in a position to allow all correct clearances around the switchboard to satisfy all standards, specs and regulations
checkpoint-status | d14cbb6c-771b-4956-9711-640cceb1d806 |  | checkpoint | Remove all covers and inspection panels from board, carry out the following checks & inspections:
label | 08343bad-c2e7-5fad-aa13-8c891fa7c368 |  | note | Visually inspect for damage
label | b739534d-de28-563a-b812-da2f2fde9920 |  | note | Visually inspect for cleanliness within boards
label | 6ef30efb-c122-5da5-9776-24c6ce9ede53 |  | note | Visually inspect for loose cables & bars
label | 1ed865b0-1ed7-53ae-9eae-86f81f7e6053 |  | note | Visually inspect for loose breakers, fuses and switches
label | ff3d27df-1ea2-59a4-a204-0560fd92a55a |  | note | Visually inspect all metering and control equipment
checkpoint-status | 2d096422-cbfa-41e5-b64d-21afdcbdeda5 |  | checkpoint | Using appropriate tension tools and equipment, physically check tension of switchboard connections (switches, circuit breakers, control compontents etc.)
label | 6283c118-70e4-5a55-abf0-c06fffc59a70 |  | note | NOTE: Switchboard connections may have come loose during transit
checkpoint-status | 11795b15-4c35-4586-9c5d-84b4db1e919e |  | checkpoint | Using a calibrated tester physically confirm functionality of ALL isolation devices
checkpoint-status | 90721352-b8a0-4b07-a382-ec180c1c8a24 |  | checkpoint | Confirm "OFF" is off (open state) by physical operation
checkpoint-status | 0bad1cff-db68-492e-bd55-71aa3400332d |  | checkpoint | Confirm "ON" is on (closed state) by physical operation
checkpoint-status | 06b1583b-5a15-426c-8706-80144408adfa |  | checkpoint | Review all protective device trip settings in accordance with engineers design, discrimination and cascade reports
checkpoint-status | 9cc84f26-c741-4b30-8b30-37bd6b2a90bc |  | checkpoint | Fredon consultant to issue the discrimination study report for review and approval
checkpoint-status | c9bece6b-c401-4af4-9d84-a5988e8cd0ce |  | checkpoint | Review all metering, fuses and control equipment wiring
checkpoint-status | 7ef51191-0270-4e9e-aa0a-31f7c602ecaa |  | checkpoint | Using as built / as constructed documentation confirm general arrangement, SLD and schematics are correct
checkpoint-status | 8be73492-30e8-4dce-ad28-387559be6435 |  | checkpoint | Confirm signage and labels on board are correct
checkpoint-status | 78f3322d-d462-4e2a-99d8-04d5221950cf |  | checkpoint | Confirm schedule is updated and inside board
checkpoint-status | 0eaf8047-ae6f-4049-ac52-e5d47afe3aa4 |  | checkpoint | Carry out insulation resistance test to confirm integrity of switchboard insulation between all active conductors and all neutrals AND earths
checkpoint-status | 8845432c-f4b6-4691-a356-a591c8ca80b0 |  | checkpoint | Reinstate ALL cover panels, close doors and lock etc.
checklist-flat | e71a73b2-2523-4820-8c5f-19a1cafb2796 |  | checklist | ITC-167.1 Consumer Mains, Sub Main or Bus Bar Test Sheet |  |  |  |  | Yes | ITC-167.1 Consumer Mains, Sub Main or Bus Bar Test Sheet | 4d00c5ba-d859-4aa5-bda8-b7cb98783925
checkpoint-status | b88f8eb5-f4c3-451c-8881-c1827347aef3 |  | checkpoint | POWER IS TO BE OFF / DB ISOLATOR TURNED OFF
label | f8dda942-b357-5d0e-8c49-46445efc7f86 |  | note | Test between phases / neutral & earth tick boxes after complete. Install danger tag if required. Should be zero volts.
text | 447d2aad-6a80-547c-afb8-5b0339cf42ee |  | textbox | R-W
text | bb5b4e1e-aa8c-57c2-b8e5-095645f54c0e |  | textbox | R-B
text | 299e461e-aec8-52dc-875d-8733499d4d1e |  | textbox | W-B
text | 1939e9f1-0b41-5026-a27a-7a79aa8d0abe |  | textbox | R-E
text | ac2f0c25-fc1c-5101-ac04-6b7b85c857f1 |  | textbox | W-E
text | 44f1d7f8-e30d-5627-902e-1ed33c745287 |  | textbox | B-E
text | 01125511-139d-500b-b2d3-054273fac135 |  | textbox | R-N
text | d1018184-20f1-5b1a-b8f7-78beb2616817 |  | textbox | W-N
text | 1ae41ba4-902f-5d9a-a056-b4da840d60e9 |  | textbox | B-N
text | fb3bbf8c-e4cb-5337-8036-5283f85be03c |  | textbox | Power Off
checkpoint-status | 969ff78e-a894-4318-b1c1-84a899d24cb9 |  | checkpoint | Disconnect M.E.N. Remove earth from neutral bar. Disconnect for all tests.
boolean | 93714fde-974a-592a-808f-5e7aae448f4d |  | tickbox | Disconnect | Yes,No
text | fea757aa-429b-5cf9-bb5c-6b604315bb93 |  | textbox | Date:
boolean | 59915ce9-bca9-5f70-934d-87cbdf8c5573 |  | tickbox | Reconnect M.E.N | Yes,No
text | 9f0feab6-e712-5c38-9748-20ab8faed8af |  | textbox | Date:
checkpoint-status | 7d6bab21-ee3b-46df-8c39-6e4d39b89e9b |  | checkpoint | Resistance of main earth. Do a resistance test on the cable from one end to the other. Make sure M.E.N is disconnected. AS3000 - 5.5.1.4 (Shall Not Exceed 0.5 Ohms)
text | 21ecd97d-6817-5b93-941e-82c8c6ac649d |  | textbox | Size of active conductor
text | fe078d2d-3b34-5bc1-b389-7cd6a3ff0327 |  | textbox | Size of Main Earth
text | 083c4f42-a79a-5f7b-9730-c9e79b864883 |  | textbox | Resistance of main earth Ω
select | ff533ffb-8f6e-55ee-bb48-3b30c363c2a7 |  | dropdown | Pass or Fail | Pass,Fail
checkpoint-status | bf02a8c0-00aa-4eef-aaaf-fb03bc79bb38 |  | checkpoint | Insulation Resistance
label | 5dcbd887-3037-550b-8281-b574692a4ce8 |  | note | Connect earth and isolate cable both ends. Test with Mega set to 500V/1000V between phases / neutral and earth.
label | 5ea0db24-abd1-5f58-8e87-ff272a9fa742 |  | note | Shall not be less than 1 MΩ
text | 3f10f18a-994d-5e57-8293-b9e480b4ed4d |  | textbox | R-W MΩ
text | b1c57e92-000a-5252-bb36-fbccb2fd4d1e |  | textbox | R-B MΩ
text | a38301d6-94e0-591b-8eb6-38bb23bdf5ec |  | textbox | B-W MΩ
text | aef23b5e-0e18-5ec7-b354-ab696d2cc9cb |  | textbox | R-E MΩ
text | a5adb732-ca1f-5ef6-88e4-2118662a3ec5 |  | textbox | W-E MΩ
text | 2b969c89-c931-51e9-8b31-b9856dbcf687 |  | textbox | B-E MΩ
text | 3a4f3ed2-5904-5729-93d4-e420859b26db |  | textbox | R-N MΩ
text | be30d9d5-7247-59f8-a9e8-2dff01376094 |  | textbox | W-N MΩ
text | 783fac1a-2ccd-5f1d-90c3-f2d5c1fc40b0 |  | textbox | B-N MΩ
checkpoint-status | 02ae566c-80cc-426e-9352-6e5daf618bb0 |  | checkpoint | Polarity Of Consumer Mains / Sub Mains
label | ef5a6c73-4fbf-5d7f-9fa3-511c02c87b50 |  | note | Using the main earth or a trailing lead as a reference conductor short a phase one end & test with meter set to ohms across other end. If you get no reading on the meter the polarity is incorrect.
text | 44a2e134-7df4-5d92-87ec-2b029c2773e0 |  | textbox | E-R Ohms
text | d1ee2667-ff73-5a38-92a5-2e81381f3902 |  | textbox | E-W Ohms
text | 84ddb0f1-c99d-5618-aedd-26efa6d70dcd |  | textbox | E-B Ohms
text | bfb8a0a6-a11a-5b0f-8d29-e89a16d9bf4f |  | textbox | E-N Ohms
select | 6da3cb9c-1508-5e78-84f6-ede1dd796d00 |  | dropdown | Pass or Fail | Pass,Fail
checkpoint-status | 61306a50-edb2-4e9f-9f2f-6d47cf599956 |  | checkpoint | HOLD POINT - Complete Energised Isolation Permit HSF-042. This service is safe to energise
checkpoint-status | 79e085ec-696b-4b32-acb9-7435eac79895 |  | checkpoint | Phase Rotation Test On satisfactory completion of above tests, and power is energised, connect phase rotation tester Red, White, Blue leads to respective phase colours and check rotation. Must be clockwise.
checkpoint-status | 64625f72-84ef-4f01-81eb-ef39831dbf4c |  | checkpoint | Fault Loop Impedence
label | 6bf30f55-dcb0-5968-a23c-0765fe580c50 |  | note | If Energised, Confirm less than AS-3000 table 8.1 (Zs)
label | 634ed4d9-c1e6-530a-9b52-e9883382a519 |  | note | If De-energised,Confirm less than AS-3000 table 8.2 (Rphe)
text | ab3ec110-0131-5a5a-ba0f-3be40b1bede4 |  | textbox | Reading (Ω)
text | 35f248f3-2ca6-5e59-8e1d-aa4ed7059673 |  | textbox | AS 3000 Table Requirement
select | bf47d23b-24cf-5be9-a814-e6f66e769bc3 |  | dropdown | Pass or Fail | Pass,Fail
checkpoint-status | 6152f378-2b22-4e31-b017-a4e9f3a9f9b9 |  | checkpoint | Pre-switchboard Energisation ITC-168 has been completed
checkpoint-status | 8638760a-e4d3-4481-b5c8-62fdc79ca7db |  | checkpoint | Check all necessary drawings available and latest issue.
checkpoint-status | d9e2e0a0-d179-4b05-a715-eee0c6c520b2 |  | checkpoint | Check cables of correct size, type & voltage rating is used for wiring.
checkpoint-status | 69142cb7-beee-416e-ba9a-f020e6410aa1 |  | checkpoint | Ensure correct main switch rating and cabling terminated
checkpoint-status | 927a46ba-0722-42ef-8789-d4736c58138d |  | checkpoint | Ensure equipment fixed at the correct height. (2000mm switch height max)
checkpoint-status | 183403ad-532f-44bc-affd-954e24881ba6 |  | checkpoint | Check cable gland is secure and tight on cable
checkpoint-status | 3fc24210-9129-4fda-a36d-446ac6e14685 |  | checkpoint | Check cable bending radius is correct
checkpoint-status | 74ead0be-b45b-4f1a-b302-f856d612aef9 |  | checkpoint | Identification & labelling
checkpoint-status | 8a432c7b-40c9-423c-959c-ad0bb1a28042 |  | checkpoint | Check for cleanliness & for visible damage
checklist-flat | 25460a31-5230-462e-b365-f11603a2db57 |  | checklist | ITP 172 Light & Power Rough-In |  |  |  |  | Yes | ITP 172 Light & Power Rough-In | 58fd809e-d4a6-4f5b-9d85-2a785441a7a2
checkpoint-status | 46ba36d5-bd67-4e57-9600-b68399a26df0 |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to.
checkpoint-status | 34b513d5-3dc9-414c-8e52-81509234ae54 |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status | 5da35605-b432-4cd1-8a41-01663e54ba5b |  | checkpoint | Ensure that the latest service drawings are being referenced
checkpoint-status | 44710e88-63d0-45a5-b5e3-8a03fc744904 |  | checkpoint | Ensure that the latest co-ordinated drawings are being referenced
checkpoint-status | 1e79f5a6-1a91-4bcb-931b-eba9916008f8 |  | checkpoint | Cable locations marked on floors and walls, if required
checkpoint-status | 92a750b6-d84e-435c-81a4-17c80e72ba91 |  | checkpoint | Cable locations marked on drawings for ease of locating where required
checkpoint-status | 4c215130-cf16-42de-b7f1-7713b75511d7 |  | checkpoint | Surface conduit correct size to house required number and size of cables
checkpoint-status | 785c76f1-ec46-4c9c-aa35-12b851e481fd |  | checkpoint | Surface conduit fixed correctly and all required draw boxes installed
checkpoint-status | bc14bfa0-76bf-40d0-9126-427c431e45b6 |  | checkpoint | Ensure that no PVC Conduit has been installed passing through fire rated walls, breaking the integrity of the fire rating.
checkpoint-status | b0c4b5ba-e399-4b6e-b4a7-9195c5b3041d |  | checkpoint | Ensure that steel conduit has been installed in areas where mechanical protection is required or where called for by the project documentation.
checkpoint-status | d756af4d-90f0-46c9-b497-7794cb7f20d4 |  | checkpoint | All surface conduit installed in a tradesman like manner.
checkpoint-status | 0dcf6334-733f-40ec-9c40-8b894e24ba49 |  | checkpoint | All penetrations are sized correctly
checkpoint-status | de383bf6-54fb-4200-8596-73f5b2d350b9 |  | checkpoint | All penetrations are sprayed or painted with galvanising paint
checkpoint-status | 0aa10326-93f3-493e-a577-bb2c5af9a047 |  | checkpoint | All penetrations are bushed to prevent damage to cables passing through them
checkpoint-status | 644c6073-a2f2-40c5-b02c-735ea30d9dfc |  | checkpoint | All penetrations are sealed to prevent the ingress of insects or vermin
checkpoint-status | 47e13bda-0f4a-42a2-a371-61c2b8c5b703 |  | checkpoint | All cable sizes selected correctly to suit the size of the supply required and to satisfy all standards, specs and regulations.
checkpoint-status | d947bc5f-ffd4-4434-b043-8f2b3266a860 |  | checkpoint | All cable sizes selected correctly to allow for Voltage Drop due to excessive cable run lengths to satisfy all standards, specs and regulations.
checkpoint-status | eb834bc2-f1ce-4c37-b821-7a6734c95b6c |  | checkpoint | All cables fixed or supported correctly to satisfy all standards, specs and regulations.
checkpoint-status | 1dcc96d4-a2a9-4e60-95ed-abef19e512f3 |  | checkpoint | Mechanical protection installed where required and minimum segregation from other services maintained
checkpoint-status | a5a9a83f-8269-4266-9610-48fd83d47a0c |  | checkpoint | No cables to be tied to or supported by sprinkler / water pipes.
checkpoint-status | 68f78b31-efb3-4b62-8bc5-c2b7b54232ef |  | checkpoint | All feeds are marked and checked from the drawings to ensure that none have been missed.
checkpoint-status | 577a7a5b-16da-4519-bb2e-3a139907a933 |  | checkpoint | All cables are marked with their circuit identification numbers at each point.
checkpoint-status | 7df94d34-6980-4799-8fad-180e98ab3f31 |  | checkpoint | All cables installed on cable ladder/tray are dressed and spaced correctly to minimise derating and satisfy all standards, specifications and regulations.
label | dc1e6997-9612-5d26-90ec-672a9a57eddf |  | note | Do not leave any cable ends exposed / bare. Fredon Policy TWIST-PREPARE-TAPE
checkpoint-status | 82b3da9c-1d6f-435c-b3d7-2c27390d535c |  | checkpoint | Visual inspection of rough in carried out to ensure completion.
checkpoint-status | f346ad75-9213-4fa8-a7f3-3c96b8774b74 |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for.
checkpoint-status | db45de5e-39c8-4e5d-85b3-5d349476064a |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status | 920ffb5f-b963-4a35-a29b-fbb18aacf917 |  | checkpoint | Cross check and verify that the as built drawings are complete and correct.
checkpoint-status | 5d975062-99a8-4ae1-bd1f-2181e0367796 |  | checkpoint | Verify all inspections are complete and collate records.
checklist-flat | 539e4dad-1e78-4143-952d-912092be7c95 |  | checklist | ITP 177 Horizontal Cabling |  |  |  |  | Yes | ITP 177 Horizontal Cabling | 643e0ec3-5955-4d93-9636-beb7e9dfd8cb
checkpoint-status | 2e39061a-c908-4e7d-8882-c71f9e39ba0e |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status | ee68f6c9-19ff-4eba-98a7-cd63056de8d5 |  | checkpoint | The Updated / Superseded drawing register, located next to the drawing rack in the site office, has been checked to ensure the latest revision drawings are being referenced
checkpoint-status | d0b48181-1787-4ddc-8966-a7d1d3cf9311 |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status | 0d591ccc-5df8-4d32-82a4-8f8888fdfa84 |  | checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
label | 5fd6119c-fd36-524a-8da3-5076aa3c679c |  | note | Prior to installation submit numbered Communications shop drawings for review to the satisfaction of services engineer
checkpoint-status | 0177650e-58cc-4352-b128-e8051b245026 |  | checkpoint | Ensure that the latest services and co-ordinated drawings are being referenced
checkpoint-status | aacd344e-5a2d-4d9a-bc66-1dbf4f52cb12 |  | checkpoint | Ensure that the latest co-ordinated drawings are being referenced
checkpoint-status | b8d7abe5-247e-4fd3-a466-d257e77de71a |  | checkpoint | Ensure the cable does need exceed manufacturer's bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status | 13f7f3cf-f2f3-451f-af0b-09593113509b |  | checkpoint | Ensure the cable has adequate support and the pathway is less than 90 m including service loops & goose necks before drops
checkpoint-status | 05882822-e1ee-4c89-a18f-23d5f16ae6a1 |  | checkpoint | Visual inspection of rough in carried out to ensure completion.
checkpoint-status | 3d83993b-fca1-4409-b481-6c0621465bc2 |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for.
checkpoint-status | bf0034b1-0aba-4f81-904b-653386578cf5 |  | checkpoint | Ensure Cabinet Layouts are installed to the latest drawing layouts with door swing and clearances considered
checkpoint-status | a1184d78-5306-4963-9662-fbe833482ae4 |  | checkpoint | Ensure cabinet is secured and and all accessories, panels and management installed correctly to latest RU Layout Drawings
checkpoint-status | 9e628ab6-acfd-48a5-af27-8301ce4ed1a1 |  | checkpoint | Ensure all shielded equipment is earthed and the electrical contractor has supplied an earth with a maximum resistance of 0.5Ω
checkpoint-status | a46976bd-4630-4308-b39e-7240f20a2573 |  | checkpoint | Ensure that all Field End Cabling has been labelled, terminated and is level to other services
checkpoint-status | b9be355d-660a-4f75-867c-4a0323c5bf38 |  | checkpoint | Ensure that cables are bunched into their final looms and dressed throughout the communications room to individual patch panels
checkpoint-status | 78fd58b3-e1fe-4a99-a507-da87abed041a |  | checkpoint | Ensure that all cabling is terminated according to communications rack lay out drawings
checkpoint-status | 97614a61-a228-4930-a7ab-bd21918274b9 |  | checkpoint | Ensure that all cabling is terminated has been labelled
checkpoint-status | 99d35590-9160-4c20-b7b6-61abe2491504 |  | checkpoint | Ensure that Fluke DSX Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their correct label on cabinet and latest revision drawings
checkpoint-status | 21decd5e-3ad4-4fe4-9dde-f80dfc9d11fb |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status | 90da26d1-5276-4618-8296-b04787c160b1 |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checkpoint-status | 2e2f556a-1850-4ae8-a9ab-38ae69fad0d8 |  | checkpoint | Verify all testing are complete and collate records
checklist-flat | 5b5f8cda-1599-4db1-bb15-cb4768e52237 |  | checklist | ITP 175 In Ground Works |  |  |  |  | Yes | ITP 175 In Ground Works | 75c4236d-92ca-4db3-996d-2e3944bfe5a4
checkpoint-status | cb40078d-0fe3-4f1e-8e64-d2e0e6bae022 |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status | f7f33e2c-3bc6-42da-b7a7-dd6efcf1b9a7 |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
label | 7cb9f505-ab1e-5315-9615-861cfe58b701 |  | note | Prior to installation submit conduit shop drawing for review to the satisfaction of structural engineer
checkpoint-status | 1079b17c-fe19-40a4-8017-c138844b288e |  | checkpoint | Ensure that the latest service & co-ordinated drawings are being referenced
checkpoint-status | db918d33-7600-4098-9d87-bfc1abb91c61 |  | checkpoint | Ensure correct datum points are identified confirm datum points with building works supervisor. Use correct set out measurement tools and equipment
checkpoint-status | 90399a29-c147-4f99-b1f6-c8c767867cd6 |  | checkpoint | Engage certified surveyor for critical set out works
checkpoint-status | 8a7fa076-262c-478e-9075-fca7cf015942 |  | checkpoint | Identify circuit to be installed, confirm circuit cabling requirement. Select conduit size accordingly
checkpoint-status | 5268aaef-4c22-4bf9-968a-8d6bd53b2311 |  | checkpoint | Conduit to be measured and cut using correct tools
label | 24828341-9eea-546b-8487-c72792ff7d11 |  | note | All conduit bends to be sweeping using bending spring. Or large sweeping proprietary bends
label | c7ab69e8-b254-5540-8e56-bdcb07d6e981 |  | note | All joins to be glued using PVC jointing cement
label | 2b60f04e-20d2-58ad-9ccc-832bfcc6a9fe |  | note | All conduit boxes to be correct type with correct number of entry points i.e. 2way, 3way T, 4way
label | add6368e-44b5-5546-bcaa-1791492677e0 |  | note | Do not use corrugated conduit in decks
checkpoint-status | 1ffb4319-08ef-4ee0-9149-06895884b9ff |  | checkpoint | Ensure entire conduit installation is fixed to steel work using tie wire
label | f2742dbb-6d89-551b-a7ae-cbd5a1853e34 |  | note | Conduit should be tied to bottom mat of steel
checkpoint-status | 9edbba28-b90b-4a02-a5b5-46ad31aa9033 |  | checkpoint | Ensure conduit installation is supported from deck over entire length
label | a801afee-275f-57d0-8aab-6aa89253712e |  | note | Where deck is post tension and steel support is minimal, use deck chairs and spare steel
checkpoint-status | 6f449c82-bc25-4874-aef7-30d06f19f455 |  | checkpoint | Ensure that the void/materials are fixed securely at its final location with the correct dimensions to allow the final equipment to be installed at FFL and Adjacent to walls Floor Boxes & Cast in Light's etc
checkpoint-status | 9627d2fc-6395-4f8e-b0cf-0c4a6027b61f |  | checkpoint | Ensure sufficient concrete cover can be achieved
checkpoint-status | e2a9a7f9-27e2-4b56-8a3c-f5e3eab7508e |  | checkpoint | Complete as installed conduit drawing showing all conduits. Photograph area of works.
checkpoint-status | c5a52ad5-a63c-46bb-bfa6-df75c0d85dc5 |  | checkpoint | Ensure that if the slab may be used as a floor for showers and bathrooms have an equipotential bond to the steel reinforcement.
checkpoint-status | 1bce793b-9d24-4c6a-a0ca-fda859d55c9d |  | checkpoint | Observe concrete pour with particular attention to critical area
checkpoint-status | dfd88d43-2f50-4fdd-81c1-2a1314d15c07 |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built drawings.
checkpoint-status | 611fb298-8c86-4beb-9d25-8a137e8abe56 |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checklist-sectioned | 9f42502e-eee4-408b-98e1-d5e21168bae8 |  | checklist | ITC-168.1 Switchboard Delivery & Pre Energisation Inspections |  |  |  |  | Yes | ITC-168.1 Switchboard Delivery & Pre Energisation Inspections | 77d8c5b0-ed94-47e7-a9c6-8f6d385be7c2
checkpoint-group | 18a2ae94-e9c4-488f-b51d-82da25b6b775 |  | section | Workshop pre delivery inspection
checkpoint-status | ee6cf967-ef04-437a-81d1-402ba67e6530 |  | checkpoint | Approved Drawing (#)
checkpoint-status | de43cbb7-4826-48c9-8cb5-6c0fa987e78c |  | checkpoint | Workshop Inspection FAT Complete
text | 18900667-89ef-5694-9089-51497f2a1771 |  | textbox | Approx weight
checkpoint-group | 5657958d-8f97-4f82-8787-b057f3aed4f7 |  | section | Site installation
checkpoint-status | 30d80897-7403-4f60-b82c-c32d49479aea |  | checkpoint | Fixed Correcly into Position ¦ Fixing Type
text | 7cb437db-7b48-5166-ab7d-38820467289e |  | textbox | Seismic Restrained
text | 1696d88c-d907-5d9d-9b64-b19e71a53362 |  | textbox | Type
checkpoint-status | c4976412-35cf-4076-936f-090caf111d73 |  | checkpoint | Clearances
checkpoint-group | f8bfedcc-9dfc-4701-8ddd-d5753cd67a89 |  | section | Visual Checks
checkpoint-status | ecfd4be7-ef0e-4a15-9c4b-07e3aad2ff21 |  | checkpoint | Obvious Damage, Paint etc.
checkpoint-status | df22e726-fd33-4e5a-96b0-3bcdf9dc7706 |  | checkpoint | Internal Clean
checkpoint-status | ac1e4a52-80ba-482b-92ef-0179576d32c1 |  | checkpoint | Internal Fixtures, Meter's, CB's etc. Secure
checkpoint-group | d67ae223-ffe1-49a7-9010-435ef6c9ec9c |  | section | Tension Checks
checkpoint-status | 6803e739-a866-484c-84d5-09f8082c21c3 |  | checkpoint | Main Switches
checkpoint-status | 9b25197a-7412-4a81-b930-ebfacea7803c |  | checkpoint | Circuit Breakers
checkpoint-status | eb973979-9e97-45e9-8f3f-0d19dd63b51a |  | checkpoint | Controls
checkpoint-group | 8ffde4a3-0e16-4381-915c-88c984dafe8a |  | section | Isolation Checks Completed
checkpoint-status | bfe47b05-d5e5-4ba0-9dae-a1529d477e9e |  | checkpoint | Main Switches
checkpoint-status | 271f148c-8c2d-41e7-aa66-f98291c504c2 |  | checkpoint | Circuit Breakers
checkpoint-group | 1e873b1c-57f1-4845-bcbb-322b1f5a8b08 |  | section | Check Trip Settings & Procective Device Ratings
checkpoint-status | 604875f3-25c9-4e67-a306-8ad2f7f31616 |  | checkpoint | Fredon to issue Discrimination study report for review and approval
checkpoint-group | 2090daf1-8ea5-41f2-b8ac-ec6748b2a5ae |  | section | Correct Labelling has been fixed
checkpoint-status | 40fd9ab1-7d7c-4eab-ba51-647078c23630 |  | checkpoint | Review switchboard as built general arrangement and engineers reports
checkpoint-group | 44f392b3-ff04-48b8-9efc-9f461fa92671 |  | section | Signage
checkpoint-status | 23c124b6-47b5-42c3-abda-190f08b04d7b |  | checkpoint | External Doors, Trench Covers & Schedules
checkpoint-group | 762f2dac-0606-44d4-be33-4f6de0109acb |  | section | Insulation & Continuity Test
checkpoint-status | 078cc8d6-a460-4371-9192-b9fe48f0123d |  | checkpoint | Insulation & Continuity Test Completed
checkpoint-group | 5076c45f-4d78-45b2-af71-07cc2f5bd2b6 |  | section | Reinstate All Cover / Panels
checkpoint-status | 510988e0-ffa9-47bd-aa14-c68d0885ab9a |  | checkpoint | Switchboard Covers Secured
checklist-flat | 9cccf8bc-0247-4696-8785-8dd52782df8a |  | checklist | ITP 183 Lighting Protection |  |  |  |  | Yes | ITP 183 Lighting Protection | 78189768-f160-4d18-af4e-8d108a427d71
checkpoint-status | 7f8a8f3e-26ed-4b88-9cc4-b349582bc1ed |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status | 476ffd97-08e5-41a5-bf32-a3bcd883188a |  | checkpoint | Ensure that all installations have been coordinated with other services, both new and existing underground
checkpoint-status | a03d4c2d-d35d-4cd5-bdaa-a4be5a2a7177 |  | checkpoint | Ensure the distance of 20m between Lightning electrodes is not exceeded and that all external corners of buildings are protected
checkpoint-status | abd2a372-22f6-4312-b11f-095e7626af25 |  | checkpoint | Ensure down conductor is installed in the most direct path practicably possible
checkpoint-status | e5577b05-13d1-46ff-9c65-fd6a532557b0 |  | checkpoint | Ensure all conductor sizes meets the minimum requirements as per AS 1768 Table 4.6
checkpoint-status | f5705eda-3e13-41b6-bf16-c5a375a6bd06 |  | checkpoint | Ensure each Down Conductor is fastened securely to the engineered attachment point
checkpoint-status | d3864ef7-6608-4ba5-b318-244726ad3a96 |  | checkpoint | Ensure pit is installed to correct RL's and not above other underground services
checkpoint-status | 89830556-ba03-4f94-8661-6d50beb74971 |  | checkpoint | Ensure Buried earthing conductors meet the requirements of AS 1768 Table .6
checkpoint-status | e2558021-ed06-4309-804b-710e8b94a9da |  | checkpoint | Ensure the correct length earth stake is used
checkpoint-status | 68b900b3-3918-43ef-a5a0-4e268f61ebef |  | checkpoint | Ensure all earth conductors are correctly lugged and Identified
checkpoint-status | 98d3b34c-de0f-4894-bc16-3ec739afebec |  | checkpoint | Ensure all earth conductors and fastened/clamped to the down conductor securely
checkpoint-status | 3f69b71a-b347-4a8f-80df-f7a8186ed014 |  | checkpoint | Down Conductor Testing - Project Specific Testing Requirement
checkpoint-status | ca0b8920-f0de-401c-96ef-513028f2e5a5 |  | checkpoint | Ground Resistivity Testing - Project Specific Testing Requirement
checkpoint-status | f3c64230-1697-40c2-ab45-271df18bb4f7 |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as built drawings.
checkpoint-status | ec335ab3-37c0-4f20-a214-4c245e8b8a2b |  | checkpoint | Cross check and verify that the as built drawings are complete and correct.
checkpoint-status | fdf50805-9c22-4cd8-b2a2-f1d8256ba7d7 |  | checkpoint | Verify all inspections are complete and collate records.
checklist-flat | 4981da4c-9012-450e-9c4d-4c5b793298c7 |  | checklist | ITP 181 Fibre Optical Cabling |  |  |  |  | Yes | ITP 181 Fibre Optical Cabling | 87849b0a-4964-4545-9aeb-aac377647d1a
checkpoint-status | 366d7e73-fd70-4c59-a54d-54b6efe657fa |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status | 13e6982c-e511-4792-b849-1da2eee19b38 |  | checkpoint | Ensure all test equipment including leads have been calibrated within the previous 12 months.
checkpoint-status | fd6fca14-8b5d-4314-9a93-10c0238e3fbb |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status | a6f525bb-ab66-4d7d-9d94-ee43f679e97f |  | checkpoint | Ensure pit and underground piping are clear of obstructions and have the appropriate access and barricading
checkpoint-status | 1693f631-6d84-4514-80b9-3675e3191c37 |  | checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
checkpoint-status | 82c5a78f-e1c0-4905-b76f-3b6c8497a5f1 |  | checkpoint | Prior to installation submit numbered Communications shop drawings for review to the satisfaction of services engineer
checkpoint-status | 324a4f4f-83e7-4d13-85b2-a333225e5c98 |  | checkpoint | Ensure that the latest services and co-ordinated drawings are being referenced
checkpoint-status | 03d5fd4a-bea5-4bee-8a5d-97420502e9c0 |  | checkpoint | Ensure the cable does need exceed manufacturer's bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status | 9d446b02-324c-4239-ad20-8fc5f1b49b01 |  | checkpoint | Ensure the cable pulling strength is not exceeded as per manufacturer's recomendations
checkpoint-status | 210c16b5-ead4-4352-ab82-165cf50fe473 |  | checkpoint | Ensure the cable been loomed in neatly along cable pathway and has adequate service loop's at both origin and destination
checkpoint-status | 5454e257-d37f-4c3f-b84c-79e932274ac7 |  | checkpoint | Ensure the area for splicing has the appropriate workstation and is in a dust free environment
label | 9a330634-7abc-565e-91d8-27e169ed6899 |  | note | Cut the last 2 meters of the fibre and remove it to avoid any dirt, or damage from the hauling that may have taken place.
checkpoint-status | 1f7d374c-2605-4ef7-9402-03361ffb309b |  | checkpoint | Ensure the cable is stripped using the specialised tools and remove all Gel using telstra wipes if applicable and secure kevlar rope
checkpoint-status | 2b7d50ca-07b7-45e8-8ba1-1f1cf5ca5031 |  | checkpoint | Ensure all equipment (cleaver and splicer) has been visually inspected, self checked, cleaned and regular servicing has been maintained
checkpoint-status | 52c1a5a6-abd4-44dd-afcf-5b510c74cd23 |  | checkpoint | Ensure all splicing follows the correct sequence and any cut off shards are accounted for and disposed of correctly
checkpoint-status | 82734673-6e76-4f5a-9bfc-dfbb8196790d |  | checkpoint | Ensure fobot is securely placed inside enclosure and dust caps installed
checkpoint-status | 30dcabd7-dbd9-4b6b-a0fa-454a18c91712 |  | checkpoint | Ensure that OTDR Testing is taken from both directions and at multiple wavelengths and all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
checkpoint-status | 2246262c-f30d-4099-abde-cd4994189d96 |  | checkpoint | Ensure that Light Source Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
checkpoint-status | 598fcbf7-ce9a-4d20-bc15-2b84eace4b84 |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status | 6d204683-c316-44ff-a4f1-b9f0c82fce26 |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checkpoint-status | a83bdcc9-1d67-4428-a85d-dddd826e7b12 |  | checkpoint | Verify all testing are complete and collate records
checklist-flat | 296dd308-70ac-4910-b62e-fa17d934470a |  | checklist | SYS - Drawings |  |  |  |  | Yes | SYS - Drawings | 882c088c-90bd-4781-b09d-458f0539a3b5
checkpoint-status | c916caf9-4320-44bb-973d-f24408604d02 |  | checkpoint | Attach Drawings
checklist-flat | 2cb9e0b9-ef8f-4c52-81e0-9ef983289882 |  | checklist | ITP 171 In Slab - Works |  |  |  |  | Yes | ITP 171 In Slab - Works | 8abd0c7b-4308-4ca7-a177-bcf6b8583fde
checkpoint-status | 32507242-5828-4573-ba28-5da20fb7e3dc |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status | 652a8861-29ee-4d9a-8de2-1a14d053b081 |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
label | 487b1d83-419d-5117-b381-5de296d75c77 |  | note | Prior to installation submit conduit shop drawing for review to the satisfaction of structural engineer
checkpoint-status | e17f8c29-e94b-4ab9-9c5a-59f4adb72e33 |  | checkpoint | Ensure that the latest service & co-ordinated drawings are being referenced
checkpoint-status | 2640487a-11f1-4c82-932e-f2dcbe6202f7 |  | checkpoint | Ensure correct datum points are identified confirm datum points with building works supervisor. Use correct set out measurement tools and equipment
checkpoint-status | b2a49552-5925-4a8f-9b8d-7ab3e3696014 |  | checkpoint | Engage certified surveyor for critical set out works
checkpoint-status | 8684bd13-1dda-4031-a868-f43bc009b4aa |  | checkpoint | Identify circuit to be installed, confirm circuit cabling requirement. Select conduit size accordingly
checkpoint-status | 989cd199-582e-4357-a284-9e0c96dc3db2 |  | checkpoint | Conduit to be measured and cut using correct tools
label | be7f5afb-0c1e-5685-af55-dfebb0d475a6 |  | note | All conduit bends to be sweeping using bending spring. Or large sweeping proprietary bends
label | cccf38cc-5628-5a83-90a7-a4ed62857e53 |  | note | All joins to be glued using PVC jointing cement
label | 0d65c222-a4fa-5690-98d5-66421ec4a559 |  | note | All conduit boxes to be correct type with correct number of entry points i.e. 2way, 3way T, 4way
label | d1a71981-d002-53aa-816c-0b7914432652 |  | note | Do not use corrugated conduit in decks
checkpoint-status | 53c17039-43dd-441a-876c-56e37b33bb3c |  | checkpoint | Ensure entire conduit installation is fixed to steel work using tie wire
label | 9bba34c3-945f-5e1b-a27b-3003b5ae2c43 |  | note | Conduit should be tied to bottom mat of steel
checkpoint-status | e1ec545c-0501-4937-967f-92caf3b20ffb |  | checkpoint | Ensure conduit installation is supported from deck over entire length
label | d23e9fc4-7fc5-569a-8b24-84100aeeda15 |  | note | Where deck is post tension and steel support is minimal, use deck chairs and spare steel
checkpoint-status | 70b52ebb-fa2e-474b-a79f-78c79f0d5aaf |  | checkpoint | Ensure that the void/materials are fixed securely at its final location with the correct dimensions to allow the final equipment to be installed at FFL and Adjacent to walls Floor Boxes & Cast in Light's etc
checkpoint-status | 5562785d-a677-4b7e-a484-22780dc8d2cd |  | checkpoint | Ensure sufficient concrete cover can be achieved
checkpoint-status | 9b18a6f4-d982-4545-b14d-285180494ce1 |  | checkpoint | Complete as installed conduit drawing showing all conduits. Photograph area of works.
checkpoint-status | c4cd4c20-2884-4471-82bc-d1bb16bb404c |  | checkpoint | Ensure that if the slab may be used as a floor for showers and bathrooms have an equipotential bond to the steel reinforcement.
checkpoint-status | 1ccb4434-f897-4c69-9f38-81b58fa49688 |  | checkpoint | Observe concrete pour with particular attention to critical area
checkpoint-status | d165bc7f-fcbb-4cfb-b9c0-ab72280bd765 |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built drawings.
checkpoint-status | 7b4582cb-2d41-4c89-ae04-7278d3c861f4 |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checklist-flat | 2eddc9a4-eaef-4afb-9e2c-d3cae5283a42 |  | checklist | ITP 178 Lighting Control |  |  |  |  | Yes | ITP 178 Lighting Control | 8c80a08a-c8fb-443c-a696-480bc8cf65da
checkpoint-status | 8d8e88c8-542e-44b9-9b0c-6ae0585c2e0d |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
checkpoint-status | 2b2be054-9003-4e9b-b826-e4e5a2a18040 |  | checkpoint | Ensure that all installations have been coordinated with other services, both new and existing
checkpoint-status | cca3369e-e5d6-48b2-9334-d5eb50305705 |  | checkpoint | Ensure segregation is maintained pending cable insulation and shielding ratings
checkpoint-status | 79f2bd36-dedc-489e-af03-7d7ee4266ca5 |  | checkpoint | Ensure cables can communicate the specific protocols over the distances installed
checkpoint-status | 035f438f-863e-4989-8a29-192db50c474e |  | checkpoint | Ensure not exceed the maximuim number of devices per group
checkpoint-status | 620d5327-bb8b-4212-86e6-b725eb59455a |  | checkpoint | Terminations have been performed according to the manufacturer's requirements
checkpoint-status | 0ef6ed02-7f72-43cf-8d91-47b2fad8e5b6 |  | checkpoint | Test for voltage on the dali line
checkpoint-status | 0cca8709-1bea-4134-8007-5050164c3259 |  | checkpoint | Test for Short Circuit on the dali line
checkpoint-status | 9d14e667-3dcb-4c06-9f5e-c0fc62bf9ef1 |  | checkpoint | DALI flash each individual line to confirm all lights are communicating correctly
checkpoint-status | 9e2d6c22-57bc-44c3-9b86-c2d8f4c8c1be |  | checkpoint | Test for voltage on the communication cabling
checkpoint-status | 0251147e-46db-4495-97ca-cc43d8b9a3eb |  | checkpoint | Test for Short Circuit on the dali line
checkpoint-status | bd1c94ed-07a4-4b24-aec3-dd9c94690bce |  | checkpoint | Scan communication line and confirm all devices can be programmed
checkpoint-status | b732e17c-cfa7-46e3-9407-171b9e8c3062 |  | checkpoint | Address all DALI drivers/light fittings with their fitting ID number and update drawings
checkpoint-status | e9ece87f-e76d-4a6e-b008-8f40c7df9e4b |  | checkpoint | Address all devices/inputs with their device ID number and update drawings
checkpoint-status | a2c0a3d5-44c5-4cb4-b375-8c8dc79a2231 |  | checkpoint | Setup the the relationship between devices/ inputsand light drivers.
checkpoint-status | 898267ca-dc80-45d8-a797-ddb93d2d0e67 |  | checkpoint | Program all Touchscreens using the approved graphical interface as per the clients requirements
checkpoint-status | 59cf870b-4747-49ee-92c1-bca1b3417e5d |  | checkpoint | Confirm all lighting and switches functions as per the latest specification, technical submissions and drawings. This may include Dimming, Motion, Lux, timing parameters etc
checkpoint-status | cfbe1499-473e-4c9a-81b5-645e4215199c |  | checkpoint | Program Head End PC/ Control system and backup all information for future maintenance and rectification
checkpoint-status | 5bbf0a35-3a1d-45c4-b36e-b93e5e095df2 |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status | 8663192c-2d52-4012-b871-79c0a6a9d8a3 |  | checkpoint | Cross check and verify that the as built drawings are complete and correct.
checkpoint-status | 899178be-5902-4aeb-8781-024e23f97000 |  | checkpoint | Verify all inspections are complete and collate records.
checklist-flat | ccfb5e51-0dd8-4f32-9092-d8efc07cd88e |  | checklist | ITP 170 Cable Tray & Ladder |  |  |  |  | Yes | ITP 170 Cable Tray & Ladder | 8e860642-0b67-4b2e-a03f-1d0e0e594f85
checkpoint-status | 1aeff4f7-1dd3-45da-8779-3480ae34deb7 |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to.
checkpoint-status | 119454ed-3068-4842-af3c-4c1b792fbc21 |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status | ae4cbc99-982a-4c49-b8f1-dc1890d0158b |  | checkpoint | Ensure that the latest service & co-ordinated drawings are being referenced
checkpoint-status | 7391ad02-9b9a-4ec6-94b7-e378121848b6 |  | checkpoint | Correct fixings have been used for the installation of support rods e.g. HKDs, Drop In Anchors. Fixings have been knocked in correctly with appropriate punch tool.
checkpoint-status | 93c7410e-1cd3-4403-be2c-be01cf90f8a3 |  | checkpoint | Load bearing capacity has been calculated and confirmed - PM to have cable support technical submission to confirm.
checkpoint-status | e026a9ba-4040-49a2-862d-d9f7f0da9dd7 |  | checkpoint | For any trays with a high expected load a pull test could be requested and witnessed by customer (if required)
checkpoint-status | 0daa7bff-bdf4-49af-81d9-8574235a608a |  | checkpoint | Cable tray / ladder has been supported at intervals not exceeding manufacturer's specifications.
checkpoint-status | 5f644317-613d-44b2-94d9-e48550aeb0e1 |  | checkpoint | Seismic restraints have been installed in accordance with engineered approvals.
label | b3538510-196f-54df-b8fc-4bbb4e165dfd |  | note | Has the Seismic consultant been engaged to inspect install and signoff against their design? Inspections to be complete inline with customer ceiling signoff and construction program.
checkpoint-status | f0db038d-49b5-48fa-ab89-c97cfd8f6669 |  | checkpoint | Cable tray / ladder has been installed at the correct height in order to coordinate with other services and ceiling heights.
checkpoint-status | 2a2a7400-dba8-48c8-98ee-a3fe4b53f7a1 |  | checkpoint | Cable tray / ladder, which will be carrying fire rated submains, has had fire rated ladder and supports installed to manufacturer's specifications
checkpoint-status | 07658b8b-9983-48c6-9e75-7c38e8553aa0 |  | checkpoint | All threaded rods have been cut to a maximum of 30 mm below the fixing nut on completion of installation
checkpoint-status | 9353aa30-7b36-4ccf-bd91-df1648015b72 |  | checkpoint | All cuts to cable/tray ladder and supports have been galvanised to prevent corrosion
checkpoint-status | e62297b6-f9a6-49d4-b0a7-81b6b65d0c54 |  | checkpoint | Ensure the Cable tray has been bonded to earth securely
checkpoint-status | fc5f2f05-8413-4e06-b97a-fef4314e9104 |  | checkpoint | Visually inspect the cable tray/ladder run to ensure all above requirements have been fulfilled
checkpoint-status | 6776fcb2-b07c-4b73-9d71-b41687554e20 |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawings located in the site office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-status | a4376eaa-eebf-4286-a182-fe33093d8345 |  | checkpoint | Cross check and verify that the As Built Drawings are complete and correct
checkpoint-status | 8af4ec66-263e-4fb2-962f-d6dfe1206443 |  | checkpoint | Verify all inspections are complete and collate records
checklist-flat | 69d235c9-290c-4902-a902-ca1218a4e224 |  | checklist | SYS - Documents |  |  |  |  | Yes | SYS - Documents | 9f43875b-600a-4401-b8df-2fe15db8d226
checkpoint-status | 6f5ea8ec-77ac-4b54-b52c-aa95f4abcf01 |  | checkpoint | Attach ITP / ITC
checklist-sectioned |  |  | checklist | SWMS |  |  |  |  | Yes | SWMS combined | a089119c-7a26-468a-b500-3e75938cb3de
checkpoint-group |  |  | section | ACTIVITY
checkpoint-status |  |  | checkpoint | Site Induction for all Elite Mechanical Solutions Pty Ltd Staff & subcontractors
label | 62e7a2b5-a751-55d6-8f79-806a2387b28e |  | note | ○ Ensure inductions to site for all Elite Mechanical Solutions Pty Ltd Staff & subcontractors.
label | 088a6831-2ffc-577f-a076-509d86477b29 |  | note | ○ Elite Mechanical Solutions Pty Ltd to ensure all subcontractors have their own SWMS approved by management and staff have read and signed off on Elite Mechanical Solutions Pty Ltd SWMS.
label | 4c85d906-f627-5150-9203-1ba80e77d4ce |  | note | ○ agree to scope of works with Site Manager (including how other trades will be excluded/ restricted from work area)
checkpoint-status |  |  | checkpoint | Preparation and Planning for Job; Working with Services
label | 8de5b46e-521f-5100-ae28-9d9fe9dd12f2 |  | note | ○ Ensure employees are adequately trained to complete the job required.
label | 554ff869-14d6-57c8-bc68-9e0c3f5e8a08 |  | note | ○ Provide adequate and competent supervision.
label | 14f65b8f-ab97-5bd3-85d1-a460f420dd6b |  | note | ○ Provide correct equipment to ensure job is completed safely.
label | 3f667782-8b3d-5669-81f5-c0e2cfc78bea |  | note | ○ All unqualified staff to be supervised at all times while on site by a suitably qualified tradesperson.
label | 1e5439d3-de09-5a2d-b2b9-08c163ff2c01 |  | note | ○ Check Mirvac Working with Services Document to ensure complying with requirements.
checkpoint-status |  |  | checkpoint | Assess work Area for hazards.
label | 592b2b9a-8668-5278-9eb0-a1279b642131 |  | note | ○ SITE WALK – IDENTIFY SERVICES.
label | cb806b08-32c0-5299-b5a6-079f308bde8b |  | note | ○ Thoroughly inspect work area and access pathways for hazards; Wear appropriate PPE, adhere to all signs and site requirements. Follow Traffic Management procedures.
label | 769ddbcc-0e7f-5722-89a3-ecbf19b83e2d |  | note | ○ Ensure adequate lighting & ventilation.
label | c3f3e454-1c6c-551c-953a-3c1ba628fc03 |  | note | ○ Ensure adequate fall protection measures are in place if working at heights
checklist-flat | c7f9b0ac-79b0-4218-a15b-a97381acf18a |  | checklist | ITC-167.3 Earthing |  |  |  |  | Yes | ITC-167.3 Earthing | ae100a26-1430-40ac-af2f-8a010daa3bbf
checkpoint-status | ab7d09d6-6dab-474d-96e7-749f46bc94f1 |  | checkpoint | Attach any photos or documents
text | 70305f45-c830-5298-b06b-c33695f4b956 |  | textbox | Earth Point Origin
text | 715805cd-cc6b-523c-812b-5bce24ecb0b4 |  | textbox | Destination
text | 141e0b69-f287-5e58-8899-1f081fde6486 |  | textbox | Correct Location to Drawing
text | 6ec6cef8-419f-53e1-9eed-44f4f347994e |  | textbox | Protective Earth Size
text | e7c7513f-2379-53dd-9049-b83370cdc93c |  | textbox | Earth Joint Secured
text | e0556443-e1e6-5865-8fc8-c5f34cc12ce3 |  | textbox | Continuity |  |  | Equipotential = <.5Ω, General Earthing = <1Ω
checklist-sectioned |  |  | checklist | Main Switchboard & Termination of Cables ITP002 |  |  |  |  | Yes | Main Switchboard & Termination of Cables ITP002 | d0899caa-76b7-45cb-818a-7fed5ca56ea4
checkpoint-group |  |  | section | Preparation
checkpoint-status |  |  | checkpoint | Locate & fix switchboard into position - check for clearances fix correctly
checkpoint-status |  |  | checkpoint | Determine cable sizes for cable glands & mark out gland plate (check cable O.D's for cable size glands)
button | ee31b335-cbc1-591c-9b25-279f2db62b8c |  | button | Install cable glands & cables | Yes, No, N/A
button | c866d1d8-443e-572d-ab8b-a9d9678abb68 |  | button | Install lugs & terminate | Yes, No, N/A
checkpoint-status |  |  | checkpoint | Clean & vacuum out board - please take a photo
checkpoint-status |  |  | checkpoint | Check all circuits are terminated & safe at the other end or disconnect
checkpoint-status |  |  | checkpoint | Final visual inspection of board - please take a photo
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Confirm that all cabling has been installed and terminated so that it is configured as per Section 6 of the ELF EMF Assessment
checkpoint-status |  |  | checkpoint | Test earth continuity & resistance
button | 2e7f960e-6231-5bb9-ac23-d5aefce4b0a5 |  | button | Test insulation resistance | Yes, No, N/A
button | 6425e2ce-e409-5f7f-b586-2804cd32d447 |  | button | Test polarity | Yes, No, N/A
button | 40d65002-05be-5d78-b6c7-c69fd1d0f018 |  | button | Test phase rotation | Yes, No, N/A
checkpoint-status |  |  | checkpoint | Attach prescribed certificate of electrical safety. Organise inspection by inspector (Add photo or attached certification
checkpoint-status |  |  | checkpoint | Isolate / lock off/ dange tag all outgoing circuits - please take a photo
button | eb8ceca1-b906-58c1-a7bb-fbb38d34890b |  | button | Ensure labelling is complete & accurate | Yes, No, N/A
checkpoint-status |  |  | checkpoint | Energise system
button | 49fdcb9b-9520-5bef-a9ba-b0b71fb13aaf |  | button | Check phase rotation | Yes, No, N/A
button | 14b2cfd5-4dc6-5bb7-b569-241f0e8b66d2 |  | button | Check switchboard as installed as per drawings | Yes, No, N/A
text | 5f8b7e18-669f-5458-b08e-bd2b061a81a2 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Ensure any modifications to shop drawings are matched to existing & returned to office / attach drawings
checkpoint-status |  |  | checkpoint | Ensure switch room is left clean - please take a photo
checkpoint-status |  |  | checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checklist-flat | 830f07e4-b6e1-438e-82b1-cb5c568c975e |  | checklist | ITC 183.1 Pit Install |  |  |  |  | Yes | ITC 183.1 Pit Install | d620d999-d9ae-4c11-86c4-37d75c1177f5
checkpoint-status | 303efb75-8877-45ea-92dc-7e86dfa8ed1e |  | checkpoint | Installed to IFC Drawing
text | fed40605-ffa8-5151-9f38-96fe730b1a55 |  | textbox | Lighting Pit Reference Number ID
checkpoint-status | 5ab5f5c0-ab64-459d-a5af-4439688ce7f2 |  | checkpoint | Pit Installed Correct RL
checkpoint-status | bba3ed5c-cf99-4163-9aff-09d924364f90 |  | checkpoint | Down Conductor Identified
checkpoint-status | 0ea30b46-a0c1-4703-8b20-2bc50e8326eb |  | checkpoint | Earth Stake Correct Length
checkpoint-status | 3b7bc9dc-268c-49d8-b589-acf793ffa745 |  | checkpoint | Test Link Installed
checkpoint-status | 8ee60c7b-55f4-45d3-8b88-27b46790fd52 |  | checkpoint | All Earth Cables Clamped / Terminated
checkpoint-status | ea8527b8-90ac-43a2-9830-d4613abd1734 |  | checkpoint | Earth Pit Labelled
checklist-flat | 6e8013d6-0fde-421f-ade7-09194c13fe2c |  | checklist | ITP 184 Lux Measurements |  |  |  |  | Yes | ITP 184 Lux Measurements | d6d42bcc-3d14-4e70-97d1-4befeb7a3520
checkpoint-status | 4e5f70de-20d6-42f3-99a0-c3e9ef282962 |  | checkpoint | Ensure that the lighting exceeds the minimum requirements and meets the design criteria
checkpoint-status | e2ad7d2e-f657-4d6d-9bd9-fdce0bb4ff42 |  | checkpoint | Appropriately set out the area in a grid
checkpoint-status | abd57b1f-0c03-4dd5-bcf6-0f4d367d6078 |  | checkpoint | Visually inspect the light meter and confirm the the calibration has not expired.
checkpoint-status | 11849362-dfbe-47ef-ae8e-b8ce4df6f949 |  | checkpoint | Architectural requirements - light spill direction
checkpoint-status | 58cd55ca-5093-4037-b3f9-8b93e70988c1 |  | checkpoint | Ensure the Light meter is pointed directly at either the light source or the viewpoint/camera in which the light levels need to be recorded
checkpoint-status | 2639c5d9-42ec-4583-87ff-0b58d1085c29 |  | checkpoint | Ensure all readings are taken at a consistent height and at the relative intervals to the grid setout
checkpoint-status | 386ae841-fe72-429c-bd56-f5159f1b88e2 |  | checkpoint | Ensure the Light meter is perfectly horizontal and no shadows from the technician are covering the meter
checkpoint-status | bc7a1f20-98d6-4a46-9d3e-d658c47edb49 |  | checkpoint | Ensure all readings are taken at a consistent height (Normally 1500mm) and at the relative intervals to the grid setout
checkpoint-status | 0bee8779-0e10-4239-a25e-458f886dcf8c |  | checkpoint | Record all information & verify the Minimum and uniformity requirements
checkpoint-status | 0b7e25e3-e650-4a3a-98df-dd1443f3175e |  | checkpoint | Verify all inspections are complete and collate records
checklist-sectioned | 413ea245-c71d-4e4c-af09-97f79d804266 |  | checklist | ITC-167.2 Single & Three Phase Sub-Circuit Test Sheet |  |  |  |  | Yes | ITC-167.2 Single & Three Phase Sub-Circuit Test Sheet | e0006273-54e4-49cd-bb29-ffbc8d960dea
checkpoint-group | d9803676-1417-432e-9fcc-13acbb0e5a31 |  | section | De-Energised Test
checkpoint-status | c4dd04bf-ba24-44b1-a361-118f0de74c91 |  | checkpoint | Attach any photos or documents
text | 9f9f36e5-2360-53ce-aefd-79d7ecf00f2f |  | textbox | CB No.
text | 8990abb5-8db4-5b65-9746-1e477abaff9d |  | textbox | Neutral No.
text | 385e3bb9-1d16-57f2-b4aa-58af17e91580 |  | textbox | Circuit No.
text | d398b264-732b-544b-95b4-952e05306fcc |  | textbox | Cable Size
text | 8ee5750d-0c33-5504-ba72-c23d9e9496c5 |  | textbox | Destination
text | 83f99a57-e9d6-54e9-b382-fa00ccfe58e1 |  | textbox | No. Pts
text | 1252f9d1-187f-5ab1-b73e-4f8f4d8849c6 |  | textbox | Visual Check (tick)
text | 7cf2bdc6-d046-5b9a-8caf-cbb914b47ce8 |  | textbox | CB Size (Amps) & Type (A, B, C, D)
text | 3f1bd9ec-f5dd-52b7-bce3-050ad35d0f17 |  | textbox | Earth Continuity (Ω)
label | 37ca0098-8fd0-537a-b438-ee1bc00478bd |  | note | Insulation Resistance (MΩ)
text | cf22abe3-14da-5c5c-99a1-b33fcaacab8a |  | textbox | Red to White
text | fad61a92-0add-559e-bf7a-a5d102ea6a2a |  | textbox | White to Blue
text | 3bb2d0ec-6150-5538-91ca-4cc6e116cf22 |  | textbox | Blue to Red
text | fe571895-a153-561e-92cc-8770be8f22ea |  | textbox | A Phase to Neutral
text | 6ecb56bc-7769-587b-84b7-b44ac0b1a91d |  | textbox | B Phase to Neutral
text | 54e6007f-ed42-5502-a209-9db3e0bbff5b |  | textbox | C Phase to Neutral
text | 6ea09b75-d939-509d-9957-b9be8e75a1be |  | textbox | Phases to Earth
text | 76fb78a0-099c-59a9-9fb6-ed8782fd0a95 |  | textbox | Neutral to Earth
checkpoint-status | 8450ea03-7313-4823-be90-c47ccda57227 |  | checkpoint | Polarity Pass (tick)
checkpoint-status | 9578d60c-1111-4c94-aa7b-4bfe834621fb |  | checkpoint | Correct Circuit Connections
checkpoint-group | c9348e44-b57a-48eb-833b-44b3e8ff164f |  | section | Holdpoint
checkpoint-status | ba80a7ea-8b57-4bcd-bf07-3b612f65bbf7 |  | checkpoint | Safe to Energise? (Initial)
checkpoint-group | db22dad5-0c96-4812-9958-3ebc1bc8afc4 |  | section | Energised Tests
checkpoint-status | 0538f401-8750-4f0c-8248-e449b37ec016 |  | checkpoint | Attach any photos or documents
text | d0468ed7-a3dc-59e7-ac7b-7775db355edf |  | textbox | Voltage (v)
text | 87280173-b97b-51ee-a087-648c887ce899 |  | textbox | Phase Sequence
text | 95e6d834-17b4-5687-b68a-667e92d1c6d1 |  | textbox | Fault Loop Impedance
text | dfea5fa8-a88d-5a22-8803-8972efeb0666 |  | textbox | RCD Timed Test (mS) 30mA / 10mA - 0
text | 9fb45569-967d-5a11-9965-63d05b48295d |  | textbox | RCD Timed Test (mS) 30mA / 10mA - 180
checkpoint-status | 1d8c1726-d805-48e1-b2d6-96a1c768652b |  | checkpoint | Label Installed
checkpoint-status | 31be6332-03b5-4318-8287-3457b699ffe8 |  | checkpoint | Signed Off
checklist-flat | bdf268c4-1d7a-49b9-94f6-927283eb6b72 |  | checklist | ITC 175.1 In Ground Works |  |  |  |  | Yes | ITC 175.1 In Ground Works | e962f39e-a24a-4bdb-ac91-9f29136a2a2b
checkpoint-status | 99a144de-4e80-42a7-9880-093753ece3a3 |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
text | abd6d3e5-ae04-5cb5-92b5-e167d17834ed |  | textbox | Reference and Revision:
text | d1addea9-88a2-53b8-a10f-afaccb4291b1 |  | textbox | CCT Ref:
text | 89d0bdbe-f338-59b4-a311-7a73dc245c97 |  | textbox | Pour Location (e.g. Document Gridlines):
checkpoint-status | 102c8c43-1301-4c0d-8ebd-32d113c7cbb5 |  | checkpoint | No Structural Implications
checkpoint-status | 3c362982-140f-4dc0-bac0-18e347b8adc2 |  | checkpoint | Marked Out Correctly
checkpoint-status | 656d8394-1459-451b-a24a-12a6f0c168dc |  | checkpoint | Glued & Tied Securely
text | f8bf5f0d-5f5e-5097-864d-ec2cc2c5b700 |  | textbox | Conduit Size
text | 2056980a-2f65-5bee-b27a-e7b7ff7ad352 |  | textbox | Approx Lengths of Conduit
checkpoint-status | 0f6e526f-75e0-4ccc-be1c-968bdc6e7804 |  | checkpoint | As Installed Drawing Attached
checkpoint-status | fe18d372-9b1e-48fa-a0a6-e475551972fc |  | checkpoint | Conduit Ends Capped
checkpoint-status | 585f361e-9c54-469c-bbec-59ddc9987bc6 |  | checkpoint | Signed off by Installing Tradesman
checklist-flat | 289fb117-46f9-472a-b07d-e7d5ce5d832b |  | checklist | ITC 171.1 In Slab - Works |  |  |  |  | Yes | ITC 171.1 In Slab - Works | f468d52e-21e3-4bf8-b3a6-4067474e5036
checkpoint-status | cbe80638-0dfc-4432-946b-4afe77ee5f48 |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to
text | 9ee5fdff-7f3a-56af-a937-9a15aa750fdb |  | textbox | Reference and Revision:
text | af37a30c-4285-55dd-9fd1-2417458c6f97 |  | textbox | CCT Ref:
text | 2ec69ea9-2635-509d-9002-8d7bb1fefefc |  | textbox | Pour Location (e.g. Document Gridlines):
checkpoint-status | 02c2ebda-af66-4882-9f38-f856660b048f |  | checkpoint | No Structural Implications
checkpoint-status | 08876d29-cb79-48d0-bc2f-6dde50cbbf3b |  | checkpoint | Marked Out Correctly
checkpoint-status | 5fc09cc1-491f-4ceb-98d5-6f849688d8c8 |  | checkpoint | Glued & Tied Securely
text | e78a93cc-3672-519d-8cc7-b9f0df0dc325 |  | textbox | Conduit Size
text | c086a5b2-0fc0-5c2e-b38f-abae4f655644 |  | textbox | Approx Lengths of Conduit
checkpoint-status | 3a0eb9d8-7aa2-43e2-99e6-d68e2d3ba4ba |  | checkpoint | As Installed Drawing Attached
checkpoint-status | d799ed04-f749-4583-9689-d5d76b6b0082 |  | checkpoint | Conduit Ends Capped
checkpoint-status | 939a4c1e-c3e0-47b9-a250-cfa4dd8b0971 |  | checkpoint | Signed off by Installing Tradesman
checkpoint-status |  |  | checkpoint | SDC Foreman Sign Off
holdpoint |  |  | signoff | Complete Sign Off
checkpoint-status |  |  | checkpoint | Passive Fire Sealing
checklist-flat | 3758dc77-e4f3-42d1-a79e-5d1b089032f2 |  | checklist | ITP 174 Fit Off-Power, Switches & Accessories |  |  |  |  | Yes | ITP 174 Fit Off-Power, Switches & Accessories | fd49124f-050a-478f-8077-c39077f7ca55
checkpoint-status | fd9f944f-9a4c-4405-8817-481f2bed33f9 |  | checkpoint | Ensure that the latest revision drawings and specifications are being referred to.
checkpoint-status | 632cd9b3-e1e7-4c7b-8731-f44af0bc23da |  | checkpoint | The Updated / Superseded drawing register, located next to the drawing rack in the site office, has been checked to ensure the latest revision drawings are being referenced.
checkpoint-status | 687c65aa-edd5-49b6-a845-c1a184ebadc6 |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status | 21bd8fd3-915d-48c2-b85f-4738aa1283b9 |  | checkpoint | Ensure that the latest service drawings are being referenced
checkpoint-status | 25123b85-99d7-4925-8f4c-c6b6e34cb2f7 |  | checkpoint | Ensure that the latest co-ordinated drawings are being referenced
checkpoint-status | d9becd7b-a090-4103-8255-011a6b49d114 |  | checkpoint | Ensure all required distances are kept from other services as per AS3000, e.g. in damp situations
checkpoint-status | 602d42e1-c1c2-4e43-9bbd-5429fc113ee1 |  | checkpoint | Ensure the fitting is compliant with Australian standards
checkpoint-status | b3c89fa9-ad3b-43e3-bd95-9f4e289dc9ba |  | checkpoint | Install GPOs / Switches as per manufacturer's recommendations
checkpoint-status | 5338f43a-5b45-4f2d-9593-05ae204c1e01 |  | checkpoint | Ensure GPOS are installed using the correct fixings and brackets
checkpoint-status | de36bce6-ad79-417e-8260-8df91f3941f2 |  | checkpoint | Ensure the correct item is being installed at each location prior to fit off (Current rating and Phases required)
checkpoint-status | 39e50f56-ef9a-49b1-ba65-7985173e6267 |  | checkpoint | Use fire boxes, acoustic boxes etc. where required - if in doubt check with the site manager
checkpoint-status | 68375d9b-c2bc-4013-8805-d8dff4843df7 |  | checkpoint | Ensure correct weather proof fittings are used where required
checkpoint-status | 6547a834-e4d0-43c2-922c-c323217e1e78 |  | checkpoint | All switches and GPOs are installed in a tradesman like manner, e.g. level
checkpoint-status | aac09d09-f4da-4e8f-90ff-e8c65a152ad4 |  | checkpoint | Ensure all Sensors and PE-Cells are terminated correctly and switch the approved lights. They should also be installed in a position that will not obstruct it's ability to function correctly.
checkpoint-status | 4ea77fc9-57f7-4941-a70c-5b5ea7a5df55 |  | checkpoint | Ensure all ELV smart/programmable switches have been terminated with correct polarity and to manufacturer's recommendations
checkpoint-status | 991529ad-8fe3-4d45-8ff2-114681369ec8 |  | checkpoint | Ensure that all penetrations through the steel structure have been properly bushed before fitting off item
checkpoint-status | ae37a3ea-8290-4def-a724-7ef726bf92e0 |  | checkpoint | Bushing installed is not able to fall off over time
checkpoint-status | 4fc826cf-8f61-4e38-af61-c541204285dd |  | checkpoint | Penetration is sealed to prevent ingress of vermin before fit off where required.
checkpoint-status | f8c1ddc7-0352-476f-99af-bbc016c5ade5 |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built Drawings.
checkpoint-status | 84fe1a56-f778-4d67-a1b9-00346ab5fafe |  | checkpoint | Visually inspect entire circuit for completeness.
checkpoint-status | 8e4ecde3-deb8-417c-91a8-35b8ffd922b5 |  | checkpoint | Ensure fittings are protected if required
checkpoint-status | 39cf408f-a37b-450e-bc11-fcb2c916ba8a |  | checkpoint | Remove all rubbish - empty boxes etc.
checkpoint-status | 0080f8d5-ca02-453e-90ad-a25c08e61c0c |  | checkpoint | Check that all ceilings, walls and floors are left neat and tidy and without any damage. IF DAMAGE OCCURS ADVISE FREDON SITE MANAGER IMMEDIATELY
checkpoint-status | 5dec80a2-36eb-4e07-ac56-de6d68ecdff4 |  | checkpoint | Cross check and verify that the As built Drawings are Complete and Correct.
checkpoint-status | fa4ca507-5cfd-4abd-894a-e1af5c59792f |  | checkpoint | Verify all inspections are complete and collate records