## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | FH-ZU2-QU-ITP027 - AGL Cabling - Rev 0 | itp |  |  |  |  | FH-ZU2-QU-ITP027 - AGL Cabling - Rev 0
section | 1.0 - Preliminary Works
checkpoint | 1.1 - Check for correct documentation
label | Frequency - Prior to commencing any activity
label | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
label | Reference Documents - IFC Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to commencing any activities
label | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Verify
label | Record of conformity - Site and office inspection
label | HP*
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 1.3 - Existing service location
label | Frequency - Prior to Start
label | Acceptance Criteria - Prior to installing any fittings, location of all existing services to be identified and marked onsite.
label | ○ Services located in the works area to be proven.
label | Reference Documents - SWMS
label | Inspection/Test Method - Verify
label | Record of conformity - APAM Excavation Permit
label | HP*
label | Responsibility - Project Engineer/ Site Supervisor
date | Date Completed:
checkpoint | 1.4 - Cable route
label | Frequency - Each Lot
label | Acceptance Criteria - HOLD POINT
label | ○ Primary cabling route installed as per path shown in construction drawings (and/or approved markup).
label | ○ See relevant lot from ITP 025 – AGL Conduit Installation for cable route.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.1, ITP025 – AGL Conduit Installation
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, Aconex reference
label | HP
label | Responsibility - Project Engineer / Beca
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 - Material / Equipment Approvals
checkpoint | 2.1 - Primary cable
label | Frequency - Prior to Start
label | Acceptance Criteria - Primary cables shall be:
label | ○ 6mm2 cable with black polyethylene jacket and copper tape screen
label | ○ Rated for 5000V
label | ○ 7 Strands
label | – or approved alternative.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.2.1
label | Inspection/Test Method - Aconex
label | Record of conformity - Datasheet
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 2.2 - Secondary cable
label | Frequency - Prior to Start
label | Acceptance Criteria - Secondary cables shall be:
label | ○ Min 4mm2 cable with black nylon jacket.
label | ○ Rated for 600V
label | ○ 56 strands
label | – or approved alternative.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.2.2
label | Inspection/Test Method - Aconex
label | Record of conformity - Datasheet
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 2.3 - Cable connectors
label | Frequency - Prior to Start
label | Acceptance Criteria - Plug and sockets shall be further sealed by the application of double lapped layer of self-amalgamating tape protected with a double layer of PVC insulation tape.
label | ○ Field attached plug and socket connections shall be constructed in accordance with the manufacturer’s instructions.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.3.3
label | Inspection/Test Method - Aconex
label | Record of conformity - Datasheet
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 2.4 - Series isolation transformers
label | Frequency - Prior to Start
label | Acceptance Criteria - New SITS shall be:
label | ○ Fully encapsulated synthetic rubber watertight (IP68)
label | ○ 6.6 Amps rating
label | ○ Minimum 600 mm long primary tail/1200mm long secondary tail
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.3
label | Inspection/Test Method - Aconex
label | Record of conformity - Datasheet
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
section | 3.0 - Cable Installation
checkpoint | 3.1 - Primary cabling connections
label | Frequency - Each Lot
label | Acceptance Criteria - Underground primary cable joints are only to be made where the cable length exceeds the maximum cable drum length or jointed to existing cabling. These joints shall only be made in pits. The joint shall be waterproof and shall allow the jointed cable to be installed within the pits without causing damage or undue strain on the joint.
label | ○ Use only approved plug and sockets for joints in primary cables. Primary cable must be jointed to the primary cable tails of SITs using approved cable jointing kits.
label | ○ Plug and socket connections shall be constructed in accordance with the manufacturer’s instructions paying particular attention to the screen continuity joint and ensuring the rubber housing and insulating silicone remains free from moisture, dirt and debris.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.1
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 3.2 - Secondary cabling connections
label | Frequency - Each Lot
label | Acceptance Criteria - Individual secondary cables shall be provided for each lamp contained within individual lights. The secondary cable shall be installed in a single, unjointed length from the SIT to the AGL light.
label | ○ A secondary cable that shares a common slot shall not be installed under any light base. Any joints within the slot shall be made utilising crimped links “staggered” and be installed external to the light base.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.3
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer/ Site Supervisor
date | Date Completed:
checkpoint | 3.3 - Secondary slotting
label | Frequency - Each Lot
label | Acceptance Criteria - Pavement shall be saw-cut to specified depth and thickness and slots cleaned/free from debris.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.5
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, Avionics Secondary Slotting and Sealing checklist
label | IP
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 3.4 - Max conduit capacity
label | Frequency - Each Lot
label | Acceptance Criteria - If APAM approve three or more cables enclosed in conduits and/or ducts, the total cross sectional area of the conductors must not exceed 40% of the internal area of the respective conduit and/or wiring duct as recommended in AS/NZS 3000 for short distances without bends.
label | ○ No more than 10 primary cables shall be installed in a conduit
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.2.3
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 3.5 - Secondary sealing
label | Frequency - Each Lot
label | Acceptance Criteria - Backing rod shall be installed on top of the secondary cable, followed by flexible sealant:
label | ○ Dowsil 888 to be used in concrete expansion joints.
label | ○ Dowsil 890SL to be used in asphalt slots.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.5
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, Avionics Secondary Slotting and Sealing checklist
label | IP
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
section | 4.0 - General Works
checkpoint | 4.1 - Protection of existing cabling
label | Frequency - Each Lot
label | Acceptance Criteria - Where the crossing of existing secondary cables cannot be avoided, the existing secondary cables shall be reinstated and made good.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.3
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 4.2 - Slack
label | Frequency - Each Lot
label | Acceptance Criteria - Primary Cabling – a single minimum 500mm diameter loop shall be made in each primary cable where they pass through a pit other than a SIT pit.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, ADBSG Installation of Primary Cable checklist
label | IP
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 4.3 - SIT pit earthing rod
label | Frequency - Each Lot
label | Acceptance Criteria - Earthing inspection pits shall be provided with earth electrodes of sufficient length to achieve the required resistivity of less than 6 ohms. Earthing electrodes shall be copped clad stainless-steel rods of minimum size 13mm diameter.
label | ○ The earth wire size shall be 16 mm2 PVC insulated copper, other than where equipment is wired in PVC/PVC cable in which case the earth continuity conductor may be enclosed within the PVC/PVC sheath.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 6
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 4.5 - Identification of configuration
label | Frequency - Each Lot
label | Acceptance Criteria - Label all cables for new and existing circuits remaining in service at every access location such as pits, duct crossings, and ALER. Position the labels such that they can be read without displacement of the cables.
label | ○ In transformer pits serving multiple taxiway lights, the Contractor shall label each secondary cable at the transformer connection to indicate the designation of the associated light connected.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 7.2
label | Inspection/Test Method - Visual
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
section | 5.0 - Post Construction
checkpoint | 5.1 - As-built Documentation
label | Frequency - Prior to practical Completion
label | Acceptance Criteria - Submission of as built report showing cabling route submitted to the Principal’s Representative prior to practical completion.
label | Reference Documents - FH QMP
label | Inspection/Test Method - Verify
label | Record of conformity - As-built survey report
label | SCP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: