## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
3b5c4f98-bc84-4ccf-b425-dbbe5d043aa2 | checklist | EFPQF09 - MASDS Install |  | EFPQF09 - MASDS Install
93e9f64d-d421-4cb4-b19d-318e64d8c12b | section | Documentation
c2ee6dab-eef5-41ca-b631-38212e882a30 | checkpoint | Confirm construction drawings approved for use.
eb308516-ac52-4112-9f2f-a6d968a4b2c9 | section | Incoming Inspection
21332ff0-4445-44d2-b73c-8147fdb746f1 | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
42afaae7-5186-5460-9fe6-6e0d69af039b | tickbox | Fire rated cable
760d1bf0-76b7-5dd5-ba59-bba1deb9f1e8 | tickbox | TPS cable
1162abbd-8036-508c-baa3-9020272f4222 | tickbox | MASDS units
cadea230-3b8d-58bd-9215-d9f4df4ce99d | tickbox | MASDS pipework
0ef11119-3705-5aca-b04e-eac4ddd7e3eb | tickbox | MASDS Power supplies
6691e8a7-2991-4494-9311-82dd6f7efd6d | section | Installation Rough In / Fit Off
c32b0045-e756-4bd7-bbb1-144a8b943346 | checkpoint | Confirm correct cable type run
660a9d49-f04e-4f78-bbb2-d96ddbea2967 | checkpoint | Confirm cable support/conduit fixings and spacings
372ca9a4-e4af-4869-a681-d5c9a6b39394 | checkpoint | Confirm segregation from other electrical services
5ac8219e-7d18-44e4-8508-0d4d1f9ad7f9 | checkpoint | Confirm MASDS pipework installed as per drawing
1fbe2635-5509-4757-8860-9e30a8e66f38 | checkpoint | Confirm MASDS sampling points size & spacing
9a57a1de-9255-4e70-946d-d466bd747659 | checkpoint | Confirm MASDS unit fit off locations
a2efacc3-8f3f-4d2d-acfc-19aab1789299 | checkpoint | Confirm MASDS power supply fit off locations
82c62a12-f827-402f-9274-42ee3a531a05 | section | Sign-Off
cb32d2a3-b4f1-41cb-a6db-665d5afc24a6 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
5489fe70-8bd6-463b-9910-90dfb842e76f | checklist | EFPQF11 - Fire Hydrant & Hosereel Install |  | EFPQF11 - Fire Hydrant & Hosereel Install
93c689f6-4e0d-4773-9862-0f2da19b4002 | section | Documentation
dd82195a-a2f8-4ee6-b5eb-579a33839975 | checkpoint | Confirm construction drawings approved for use.
e57f274b-5383-409c-8753-6e8ee7e4ef93 | section | Incoming Inspection
26b00dec-56e6-491a-8fda-ef8f283a6037 | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
6818e1c3-bab1-5ec9-b91b-5d789d68c7ed | tickbox | Pipework.
5638ea13-a4c6-5579-9c45-42eabfc6d928 | tickbox | Fittings.
dca5f531-3b21-562a-b197-478cdebca5ef | tickbox | Hangers.
71932036-c7fe-5e2a-9d5b-2a7241a16b58 | tickbox | Isolation valves.
2f67df12-6db9-57e5-8718-50bf5835c81b | tickbox | Hydrant valves.
afc5b309-14c1-5988-a2f0-7e6b00d01f2f | tickbox | Hosereels
c82e5909-2dda-4047-8f19-e76c54bba038 | section | Installation Rough In / Fit Off
c66e6dac-74b7-4005-9f70-76f198d481b0 | checkpoint | Confirm hanger spacing.
8d7bd39c-b406-51ac-98f8-46045885f3bb | note | 100mm - max 5m spacing.
4e1052d0-f15f-50c6-a63a-422dee82d851 | note | ≥ 150mm - max 6m spacing.
4929f50c-bbed-412f-b4aa-140d02c5e563 | checkpoint | Confirm support at change of direction at 1m max.
003d462c-eb0c-4f02-9d67-b265eea79dba | checkpoint | Confirm support of pipework no more than 1m from end.
d5599a0b-cac7-4aac-9713-218796d54962 | checkpoint | Confirm support of horizontal branch from vertical riser no more than 300mm from riser
e222a024-83c2-4a76-a724-10f44e44eb17 | checkpoint | Confirm pipework installed as per drawing.
a0e98c70-8ba6-4b6f-8d46-be3b3aacb2f6 | checkpoint | Confirm hydrant height at handle between 750mm and 1200mm
f03b79ca-7878-40ff-a9c1-3621e5d8d1bb | checkpoint | Confirm minimum clearance around hydrant handle 100mm
4646ce54-fd18-490a-986d-1db8f903d5db | checkpoint | Confirm hydrant valve outlet not inclined more than 35° from horizontal
40fdaf84-a415-4fb8-9a0b-424f7aa272d4 | checkpoint | Confirm outlet has 300mm clearance for a minimum 225 degrees
3c515543-cc16-4c62-95cd-d2cea7a58527 | checkpoint | Confirm hosereel mounting height 1400- 2400mm to centre of barrel
e93958f0-b1f0-43c4-bb19-8ef48594c6ad | checkpoint | Isolation valve height is 900 – 1100mm
03bbbbad-10b1-4aa9-a377-30032e1d6092 | checkpoint | Maintain 100mm clearance around barrel
dbc11a10-bf61-47bd-836d-4d45945cbcc1 | checkpoint | Confirm hydrant cap and chain installed
a010fc8b-6586-42a0-a660-1f16e0fa4c71 | checkpoint | Confirm installation pressure gauge installed at top of most remote hydrant
11ec8cf6-6e83-4ce8-8c31-455c832e3a1c | checkpoint | Confirm pipe identification labels installed
0335bae9-b488-4ef4-94a4-6f6207500d4c | section | Sign-Off
02a28e02-7df3-498d-96fa-e52200a9f995 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
09f340b8-2276-4a8c-a56a-03b4751f4c9e | checklist | EFPQF12 - Fire Tank Install |  | EFPQF12 - Fire Tank Install
3f97e9aa-bf65-4877-afa5-14f8f269b585 | section | Documentation
76ee7cab-8de9-423b-9773-c2f9630862c1 | checkpoint | Confirm construction drawings approved for use.
3930905b-9410-47ba-8fa4-8a54866311dc | section | Incoming Inspection
2a5f9597-ea74-4fcd-8ead-88a4a0f016bb | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
7e213972-dbde-5e02-8ee2-7069825316be | tickbox | Tank Panels.
971ff072-eb46-5d6b-bcff-665931acb33e | tickbox | Roof Purlins.
2722e81f-ea82-56c9-b65c-ac6781b01907 | tickbox | Roof Sheet.
9f56a0ec-fc95-53d8-908c-d0a202041d85 | tickbox | Access ladder.
9610f5d6-ac21-5123-a4d4-3757115e5dd2 | tickbox | Vortex.
67d69e3f-8ddb-5149-9925-126c92c247e8 | tickbox | Pipe nozzles.
c524c022-037a-4280-a0ab-9b45b6da04da | section | Installation
d24c2770-5c61-4d9c-ae5e-af5704d43e7d | checkpoint | Confirm tank slab tolerance within +/- 3mm
73687511-552c-476c-b995-8cd65fd9de41 | checkpoint | Build first panel ring
1ccf2667-c565-4b28-b49b-58c57d3191a4 | checkpoint | Build roof including access hatch
d5819f92-ccaf-4948-961f-5f633e825f57 | checkpoint | Hang tank liner
060561d9-1c36-4e30-a946-6812bbebfac6 | checkpoint | Fix tank jacks and lift for next panel install
eb268997-c8e9-4d31-94dc-f063031d2395 | checkpoint | Install ladder sections at each lift
67e4d975-37f3-47ac-bdd3-3bb8fc936d15 | checkpoint | Fix base ring and remove jacks
0351cdb3-5e72-4589-a8ca-0db782be3963 | checkpoint | Ensure internal tank base free of debris
705f4a8a-68c1-470a-829f-7166f89ce842 | checkpoint | Install geo fabric to base
a379b63d-9292-4f17-be38-6a551babb9ef | checkpoint | Stretch tank liner to tank base
142e4173-99fe-483b-8659-93bc480b7518 | checkpoint | Connect pipe nozzles and vortex
f60addc0-e3f3-473d-80ae-4fd887f94b06 | checkpoint | Confirm tank level indicator installed
0be70db1-eca4-43ed-8292-50fdcda0cb0f | checkpoint | Confirm tank capacity labels installed
395d184d-a0fc-4dca-b2f6-20862a9ae879 | checkpoint | Confirm warning labels installed
977fb647-fe6e-4b0c-b931-e20a517d7ea1 | checkpoint | Confirm ladder guards and inspection hatches installed
2a4ebe97-8be5-4301-bf8c-c637bcbb39ba | checkpoint | Confirm no leaks when tank full
e34bf9f3-538e-43d8-ab33-1b5c27cfe392 | checkpoint | Copy of Installers statement attached
fa0fef44-e12c-4c2f-8de9-3e96c9a1bdaf | section | Sign-Off
70a78c48-f2cc-40b9-9e94-9a954d073225 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
a9cdf8c0-efbd-4d1a-8b29-bde80fb31491 | checklist | EFPQF13 - Fire Booster Assembly Install |  | EFPQF13 - Fire Booster Assembly Install
51e75907-66c9-46ad-ae59-0c011c659fec | section | Documentation
84e7d696-c49c-4818-9f15-7209ff444532 | checkpoint | Confirm construction drawings approved for use.
79967718-1945-44bb-a2cb-efd9133dc9a9 | section | Incoming Inspection
321d3b1a-1a52-4ab6-853b-1864a3ab469e | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
1974494a-6d91-5609-a54b-143b1448b0c1 | tickbox | Fire Boosters
15f69ad4-4498-56c8-9623-f8a15719780b | tickbox | Suction Connections
292d3364-5a1f-522a-8ab9-b637fca612ce | tickbox | Feed Hydrants
83670f2c-1453-5446-b963-24cb3d9969c3 | tickbox | Isolation valves
11e30c10-69ba-4888-89a3-8f1ffaae35fb | section | Installation
f37920a6-0bdb-4c38-9a19-6b0c05494bb8 | checkpoint | Confirm height of booster outlets between 750mm and 1200mm above standing surface in front of booster
aa327c0a-32d3-471c-ade2-f643e1d5728f | checkpoint | Confirm height of feed hydrant outlets between 750mm and 1200mm above standing surface in front of booster
282045c2-e979-4141-9a5a-f4e03f0df457 | checkpoint | Confirm height of large bore suction connection between 450mm and 600mm above standing surface in front of booster
71637a45-a66b-44a2-9620-72b11818e56f | checkpoint | Confirm height of small bore suction connection minimum of 400mm above large bore suction connection
48ff3e1e-bd7d-4e60-b101-f58356b7d2ca | checkpoint | Maintain minimum 450mm centre to centre clearance between outlets
d80dfe67-24c8-4692-adb2-cb1a19820d50 | checkpoint | Confirm front face of all connections within 150mm of the front of cabinet
4eb74fe7-5131-490f-af52-d6b8d3b307ac | checkpoint | Confirm caps and chains installed
f021b871-76fc-420e-a2a2-3a356f9ed309 | checkpoint | Confirm isolation valves chained and locked
b23b433d-9871-4199-8f7b-8b76fb00c9cc | section | Sign-Off
21fb9362-596e-4130-91fc-c39c4740f943 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
6fa439de-f544-4ac7-bac4-ad10d5d205fe | checklist | EFPQF14 - Gas Suppression Install |  | EFPQF14 - Gas Suppression Install
986bbd74-d957-4928-b666-68b54b8a8312 | section | Documentation
6c1e039f-82e9-43e2-abef-b4d303d75d54 | checkpoint | Confirm construction drawings approved for use.
2157f73b-e471-4d26-9adf-1e752aea6ba0 | section | Incoming Inspection
ccf2191d-86f2-46d9-8aaa-23c5d868a25f | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
a4e895ee-0daf-58ae-b24a-32cda3b85a49 | tickbox | Fabricated pipework.
ee17e9cc-2c2c-5561-9dad-e788fae698c4 | tickbox | Fittings.
ee008fa1-9860-5422-9e5e-43cd490a7870 | tickbox | Hangers.
c611aff2-d98b-553e-badd-75c743e380fd | tickbox | Nozzles
6cfbce27-3da2-554b-88b2-e166a6ddb134 | tickbox | Cylinders
6e4b6717-4653-558a-b652-eff069629630 | tickbox | Actuators
23dbf763-99e0-56f6-a8ce-fa3777bea216 | tickbox | Hoses
c6896bb5-c5a7-5221-a58d-28303707c004 | tickbox | Gauges
75b41022-a2ad-4972-ad62-222f0ff551a1 | section | Installation Rough In / Fit Off
f4fbff26-1e89-4d61-a62e-7e6767c73df6 | checkpoint | Confirm maximum hanger spacing.
dadc388b-1fc8-52d2-be97-80790e514ba2 | note | 25mm - max 4m spacing.
29201d3a-6fb4-5a7b-a902-bbc2cb534877 | note | 32 – 100mm - max 5m spacing.
f6e3da1a-3573-56e6-8f11-9947836ad5ac | note | ≥ 150mm - max 6m spacing.
f7710abd-198c-5984-9696-b0772d8ffc34 | note | Acceptance Criteria - AS:2414
f3af2566-dcd0-4d3a-bfbb-804783e48f49 | checkpoint | Confirm support at change of direction at 1m max.
1d464dd6-ecb7-52ca-860d-ae5deaa954f3 | note | Acceptance Criteria - AS:2414
951caf3e-a593-4e2f-994d-fa8d59317455 | checkpoint | Confirm support of pipework no more than 1m from end.
2e3a1912-ec76-5139-b7d1-b518f99c938d | note | Acceptance Criteria - AS:2414
431fb993-f1da-4679-b410-080d2ec72da1 | checkpoint | Confirm support of armpiece exceeding 500mm.
40c91390-8b61-5f0e-ac64-001c24717a37 | note | Acceptance Criteria - AS:2414
cf5a5ab9-6489-4cb5-9b2a-4d904c59d951 | checkpoint | Confirm first support of range pipe within 2m of mains.
a5d6c55a-ca4d-5e6c-b1ab-8d9f14c911d3 | note | Acceptance Criteria - AS:2414
1261fe7e-f112-46fa-8026-709b64457380 | checkpoint | Confirm pipework installed as per drawing.
3f5b5586-4bab-4a91-be57-353f93543e54 | checkpoint | Cap installation and perform pressure test
81a2b2ad-d121-562a-81fa-e74333980939 | note | Acceptance Criteria - AS:2414
f5087423-d48a-4334-be01-a07004698cf6 | checkpoint | Confirm discharge nozzles installed.
e2a4be2f-aff3-4c85-868a-6dc20701b421 | checkpoint | Confirm gas cylinder mounting as per manufacturer instruction
f8f7671a-ce01-4666-802f-1cc90e28cdd1 | checkpoint | Confirm cylinder hoses fitted to discharge manifolds
7e6cbe69-36f8-42e1-9c39-29e1b370115f | checkpoint | Confirm cylinder pressure gauges fitted and indicating correctly
3d9cbcce-790e-493e-a5b2-a3870a525c24 | checkpoint | Confirm discharge actuators fitted
ed2bb849-d252-4201-a737-db905cb95570 | section | Sign-Off
003ce40c-4fe8-42ef-9e9d-1efcfcf18d0e | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
d21cadb1-fcad-43bd-8a06-735673bbd9da | section | Pressure Test Report Sheet
ca3b51f6-d3a5-40bf-9e69-35bf4d0633eb | checkpoint | Test Details & Results
4faf1b05-05d2-5406-bb88-9654c537a191 | textbox | Test number
9796709d-6899-5c7d-8931-bea469191c39 | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa), PNEUMATIC TEST – 300kpa 10 MINS - PERMITTED LOSS 20% (60kpa)
6b37a1b2-08a0-528f-8361-935a20d4d377 | textbox | Start Date
78945998-fcce-5956-a0b9-fb9e203a8878 | textbox | Start Time
9cf10380-868e-5e01-82ca-1dc52f8c0add | textbox | Start Pressure
ed7bd0f4-ea02-5596-8b09-210d8bf18f18 | textbox | Finish Time
19737aef-b87b-516f-b550-4735d13005be | textbox | Finish Pressure
2d2d7368-f660-5f9d-8051-53fedd8e0089 | textbox | Gauge Reference
b9204bad-13b6-4c37-afa7-69fd1e5bb002 | checkpoint | Test completed to specification/drawings & Area left clean/tidy
0fa9ef1c-27f5-5029-b1fe-754b34af888b | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
4248c414-3728-4082-9f39-283f57ee544a | checkpoint | Entire Fire Sign-Off (attach signature)
647ac0bc-157d-4fd6-8e04-a810fbd724df | checklist | EFPQF15 - Water Mist Install |  | EFPQF15 - Water Mist Install
8af041ff-0677-489b-801b-cb809f872472 | section | Documentation
fb233c3b-7bac-4058-b194-ab373dde0961 | checkpoint | Confirm construction drawings approved for use.
226d22e6-1222-4598-92a4-9eda0ac06b06 | section | Incoming Inspection
6d7d5f3e-e2da-4eb1-9bac-47e0e581e845 | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
f99270bc-2dee-5ce9-ba97-789356e3ed7e | tickbox | Pipe.
6b206b76-7a7d-5c57-9ad1-feb23f10e89a | tickbox | Fittings.
f90d1927-8f8e-59c2-a388-e8f22f126191 | tickbox | Hangers.
4f0608a4-c092-540b-bb0e-be60dbe09530 | tickbox | Nozzles
c895f19a-fa75-54d8-8589-d90f1a1aab4f | tickbox | Valves
0950268b-2c89-4fe2-8a6f-52e10f11aae9 | section | Installation Rough In / Fit Off
ae86670b-fafb-49f5-92a0-199bc954e84f | checkpoint | Confirm maximum hanger spacing.
77caee2d-0e29-5044-8805-d910d015cf61 | note | ≤25mm - max 4m spacing.
e78cd5a3-7227-5072-aa12-910a56d4302d | note | 32 – 100mm - max 5m spacing.
cb9a41aa-e1c4-562d-86b4-9cb99b9ed893 | note | Acceptance Criteria - AS:4587
89913e29-2979-4783-8cb9-2e6e140c6bf0 | checkpoint | Confirm support at change of direction at 1m max.
a8a45d9b-cdd9-580b-b4f4-29d1951ffa85 | note | Acceptance Criteria - AS:4587
8b7380bb-b9c2-47f7-8837-7bca811ff2e6 | checkpoint | Confirm support of pipework no more than 1m from end.
4d5b52e7-5743-5a42-b94f-144e75d9fcf3 | note | Acceptance Criteria - AS:4587
042d6097-b624-47cd-8996-b8cf06e2e1f6 | checkpoint | Confirm support of armpiece exceeding 500mm.
c8b2b30b-f3c1-5b49-a741-a637a94fe986 | note | Acceptance Criteria - AS:4587
d7e03d62-99cc-4829-9892-d98f2ed24ece | checkpoint | Confirm pipework installed as per drawing.
45ca6fa9-bf7d-4450-8fe6-88d73b08337b | checkpoint | Confirm isolation and test valves installed
7f2bf7d0-7cfe-4156-9313-0ad6d8f12bc7 | checkpoint | Cap installation and perform pressure test
90887c33-d606-5822-bda5-81aebb76c0d1 | note | Acceptance Criteria - AS:4587
adf06e96-874d-4adc-80ab-27e867ad0c35 | checkpoint | Confirm discharge nozzles installed.
8402d717-f7cc-4a11-9afa-a6a0075abe34 | section | Sign-Off
680cf148-3d86-467f-af7e-17d849b888d3 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
cb679f8f-2acb-4ea1-ac44-4d2ec0e36a4f | section | Pressure Test Report Sheet
073ab0d8-85e8-49a9-ba84-31542345c06f | checkpoint | Test Details & Results
cd626ee3-64dc-5419-a746-a61ccb3352cd | textbox | Test number
d4257a2a-c880-5d48-b685-27b201c17bf9 | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa), HYDRAULIC TEST - 3300kpa 2 HOURS - NO LOSS
9f64331b-2616-5137-aca6-c59dd7b32d67 | textbox | Start Date
5ee7146a-05a1-51c7-9917-84768731d9e0 | textbox | Start Time
565ad3bd-6bdf-5981-946d-0a14c6dc1363 | textbox | Start Pressure
965a2bae-1b5f-50cf-ac5b-0a9182d97961 | textbox | Finish Time
893e90aa-dc65-5e21-ac71-f058085afc8d | textbox | Finish Pressure
8b721c64-9b6e-5b8a-8e49-b6b2a262d895 | textbox | Gauge Reference
7bae6f16-5caa-4248-b796-d751afc54464 | checkpoint | Test completed to specification/drawings & Area left clean/tidy
9ba604fb-1914-5e9e-8975-bdfc26603872 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
7ffdf506-72d6-4ca3-8ce7-110b286fc52b | checkpoint | Entire Fire Sign-Off (attach signature)
4956b25c-e2fc-477c-9bf6-a5b1ea05a280 | checklist | EFPQF16 - Fire Extinguisher & Blanket Install |  | EFPQF16 - Fire Extinguisher & Blanket Install
94a6a5e2-f74c-4faa-9245-40adf640f90d | section | Documentation
9893665e-04ee-4232-9c75-09e099ea0d0e | checkpoint | Confirm construction drawings approved for use.
ade9e2ca-08a4-4f1e-8dbf-e293014ea1f9 | section | Incoming Inspection
c4131cb6-ad9c-49d8-8ca5-e19fa8070b95 | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
19d2cc4e-3aca-5176-9458-62e0e6d6d2aa | tickbox | Fire Extinguisher.
5afb76c4-7264-5dc1-95d9-ad857806df1b | tickbox | Fire Blanket.
31497df2-4920-50a3-a8fc-669aac1ab9e1 | tickbox | Signage.
d30d5f15-3c26-4884-9e45-407f11939b07 | section | Installation
41cbf6ac-8788-4e20-8b43-2350efa4745e | checkpoint | Confirm top of extinguisher handle ≤1200mm above floor level
a5bbb604-e734-53b4-a308-351e42561a99 | note | Acceptance Criteria - AS:2444
2d4659f5-6418-4ef1-a911-d7d7deaaf81e | checkpoint | Confirm extinguisher type signage located just above handle
53921f17-28bc-5c25-90ea-d9ce76b50f92 | note | Acceptance Criteria - AS:4587
f8f69d33-8aae-4dac-a66a-41f4aea801eb | checkpoint | Confirm extinguisher location signage located at ≥2000mm above floor level
7cd954f3-127a-504a-8c92-199001f1e4ae | note | Acceptance Criteria - AS:4587
cdc3a15b-4065-49e7-885f-db81621c8f14 | checkpoint | Confirm fire blanket located in a readily accessible location
4b653cb5-4568-5076-9e54-f49fef16fdf8 | note | Acceptance Criteria - AS:4587
65510244-ac0b-46f1-842e-b434da0b150f | checkpoint | Confirm fire blanket signage provided adjacent to the fire blanket
ef993f8d-b848-574e-9370-65ecff496aa3 | note | Acceptance Criteria - AS:4587
64252675-48f0-45ed-8bcf-023c44ea1ad5 | checkpoint | Confirm fire blanket location signage located at ≥2000mm above floor level
4ad6fe9d-c81a-58e1-8927-5de436984206 | note | Acceptance Criteria - AS:4587
044dbf7e-7712-4327-a87f-8b3ec7cd188e | section | Sign-Off
df6c49be-eebd-49f9-bc24-eae9866d659a | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
8b7f6fae-e1ae-4de5-a44a-865eb5d74013 | checklist | EFPQF17 - Fire Electrical Commissioning Test Report |  | EFPQF17 - Fire Electrical Commissioning Test Report
f73f7e0b-32f3-4e31-8a0a-a3a46d44a449 | section | Pre-Start
a46dce8c-e4d6-4bcb-9724-ec01170f4956 | checkpoint-no-value | Pre-Start:
0a9a8ccf-6d5d-57cf-8a0b-0975891a18b8 | textbox | drawing reference
7f174a8e-aee1-50ca-8e47-12006832e0d9 | textbox | level and area
c47e62ee-3e25-48b9-bb9f-9847708cccc3 | section | Installation
eeef5065-95c8-4824-8aa4-f362dc63d43d | checkpoint | Secure cabinet
e111c804-0087-5345-95e2-b3243bd9c76b | note | Specification Ref: drawing
54ec5be5-c46a-47bd-a33d-ea1becc8b7c3 | checkpoint | Extinguishers installed
32805cbb-88c3-5ceb-9190-f5313ca9a816 | note | Specification Ref: drawing & AS:2444
3a8d14d8-f247-45d0-92ae-f9585b35bdc6 | checkpoint | Signage to meet code compliance
a6528d2e-cb3d-5503-99e1-5d3d2be28054 | note | Specification Ref: drawing & AS:2941
5a38d940-1e56-40b1-8e4b-29db13341fa0 | checkpoint | Hangers location and spacing
e292fb4b-7d40-5ea5-bdab-e5db73839fbc | note | Specification Ref: drawing & AS:2941
5fbb1eba-c4e3-4096-8fe5-dd74adc0e5ff | checkpoint | Fire blankets
55a0c6fd-35d2-591c-9887-e873b72f9867 | note | Specification Ref: AS:2444
10799360-6ac8-4eee-8541-808949d42caf | section | Sign-Off
d8c29708-dbec-47b8-a6b1-1dd3cc159f14 | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
e1b409c5-487c-5e27-8a4d-a784fd4ec605 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
48f0e366-49a3-54b3-8c6b-7f63c0e3f918 | button | Entire Fire Signature Sign-Off added below | Yes, No
ef17fccd-7af6-4495-af15-97ba85f035e1 | checklist | EFPQF18 - Fire Penetrations (x 10) |  | EFPQF18 - Fire Penetrations (x 10)
438ef0d9-aa2e-4305-bef7-c5ad51dee81c | section | Details
642dd49b-eabb-4aff-8ceb-8b981f25cbf4 | checkpoint | Fire Penetration details
ea7c5c03-d83f-515d-b25b-74ac1f47e895 | textbox | Location
c57016d1-df45-5317-a444-81d5db0c03d4 | textbox | Diameter
021dd667-26c7-5b1d-8639-7bb34fbaf823 | textbox | Wall/Slab Thickness
e08857f4-df4d-4391-8e7b-282b196efebf | checkpoint | Sleeve installed satisfactorily
2b00d975-b3e1-56a0-a3a8-fb41d60c3642 | textbox | Date
fb72085a-ca41-42cb-ae0e-535a6b7f5dec | checkpoint | Fire Penetration details
33e32e06-e3b7-52bd-adfe-a837e5bc2d8c | textbox | Location
954acd1b-3093-5c0f-8ea0-9c8a7ac5d29e | textbox | Diameter
80af62fb-08e3-5a8c-b2fb-f2ed14f16ba6 | textbox | Wall/Slab Thickness
4711e8ca-f14e-4098-9b07-b5bbd22fc8de | checkpoint | Sleeve installed satisfactorily
dd97e279-6fc3-56a1-a335-745ac1ccaf93 | textbox | Date
3934f5ab-abed-4657-af63-acc1c336f9c3 | checkpoint | Fire Penetration details
2d2c2442-4320-5ea9-b8ec-eea91d8c6c46 | textbox | Location
7503a99d-f8fb-5084-bcbb-afeb7eccdbe7 | textbox | Diameter
c1fd62dd-96cd-542c-adcf-39090ae30607 | textbox | Wall/Slab Thickness
bec9bbe7-3996-462d-b90a-4bf814e50cf0 | checkpoint | Sleeve installed satisfactorily
9d330b24-9560-5e39-b0f2-1715ab497b8d | textbox | Date
9ac10d00-3a24-452c-b9da-d983ddd84ef3 | checkpoint | Fire Penetration details
2623c5dc-c0cc-5579-b8ae-2dec93c02763 | textbox | Location
fd5a7350-0842-50e0-a615-df7be962d61b | textbox | Diameter
050a780a-9013-54b3-b6e5-bbe5c3f235c3 | textbox | Wall/Slab Thickness
bae39ad9-c3a0-4a6a-aad4-aa20baa7ebba | checkpoint | Sleeve installed satisfactorily
68e54a8b-6992-5f69-b3f2-4c4e5dd38a6d | textbox | Date
b7b98ff8-bc1b-4045-9412-a05d5ebabfc2 | checkpoint | Fire Penetration details
ab3e6116-df04-5c2a-8a49-52341b917c00 | textbox | Location
a19a5102-3846-5188-897e-aebca4a8d40f | textbox | Diameter
86795459-b68d-535d-aa76-5d681cb3d957 | textbox | Wall/Slab Thickness
01016735-9d16-4e54-8d56-b13a80bff45e | checkpoint | Sleeve installed satisfactorily
e9573ef4-2a87-55c3-a5e1-fc5df257485c | textbox | Date
3aea5f57-232e-4e2a-a5ba-9eeb3e64d029 | checkpoint | Fire Penetration details
74b192ce-bb76-5658-b489-f38e5e651c02 | textbox | Location
6c8ace9c-5b20-527f-a9ef-5ef6f91ecea5 | textbox | Diameter
3d4d9d43-98a9-57f9-a8ca-f6384c64a6c4 | textbox | Wall/Slab Thickness
06825929-40d1-4fc6-931b-4f4068c5283e | checkpoint | Sleeve installed satisfactorily
1b7e1dba-465b-5825-a5bc-5703db41f8dc | textbox | Date
c8d62334-7c62-4952-9cd8-575544d7c71e | checkpoint | Fire Penetration details
220c2bc2-ebde-5c4e-a568-2a1de5ab2336 | textbox | Location
5628418e-fd5b-5592-accc-9e9d0c6dc3ac | textbox | Diameter
edf6678e-fb44-5330-9c00-80d69f596d25 | textbox | Wall/Slab Thickness
094404a9-160b-4708-886a-c9721bb59d90 | checkpoint | Sleeve installed satisfactorily
6e4a0a0a-0d02-59b7-a5c7-a01cc6b243cd | textbox | Date
02adcd1a-ceac-4eaa-8c53-8eb76fa1772e | checkpoint | Fire Penetration details
44ead85b-4715-5833-8515-6fcb365af6a4 | textbox | Location
5356b62c-da88-5213-ad32-a3e6978de422 | textbox | Diameter
4bf4f765-fe68-5e26-8aa0-355a92f771c4 | textbox | Wall/Slab Thickness
eb2c57b2-a32d-470a-ab3b-4b7335978956 | checkpoint | Sleeve installed satisfactorily
8fa8a58c-e3a6-50e5-b17c-33fa67810de4 | textbox | Date
a07d42de-6aac-4cbc-a954-ec83abf114bf | checkpoint | Fire Penetration details
751ab4d7-ce23-577a-acda-4a7ff1ed1781 | textbox | Location
cc31bde6-69cb-5487-9aa0-1e08cba718e8 | textbox | Diameter
bd4964a9-03dc-5780-ab97-38aa54e2329c | textbox | Wall/Slab Thickness
a1107546-7fbe-4d22-a0ae-2d58be28e11f | checkpoint | Sleeve installed satisfactorily
f17d2746-33cb-5b50-b412-b48eca839b01 | textbox | Date
f1f6cdbb-498e-4f61-a90f-9cea7cb0c6fc | checkpoint | Fire Penetration details
c6a22091-51eb-545c-a393-1d90de04c7d1 | textbox | Location
ebad3d9a-c620-5b3e-bb45-0f350819d52a | textbox | Diameter
156aa093-aaf1-5b1d-a0b4-8f9779bab110 | textbox | Wall/Slab Thickness
69db78d1-9c33-4d72-a923-84a1db039426 | checkpoint | Sleeve installed satisfactorily
5cd5bd4c-ffe5-5919-85fe-6b4663a0879d | textbox | Date
e5473481-6231-44e2-98a1-aab1ce5293e0 | checklist | EFPQF20 - Calibration Record (x5) |  | EFPQF20 - Calibration Record (x5)
ff3391de-58a1-4eac-9e1a-e58a5852ee62 | section | Details
506da9eb-31ba-41c1-bf32-7b89349a4db0 | checkpoint | 1.Calibration Details - Pass once entered
8e7bdbd9-e770-5f54-87d9-1cee596417c2 | textbox | Equipment
0e41dbf8-79a8-5fe7-a54b-4cbdbe299943 | textbox | ID Number
83416da9-46cf-5a1b-bade-2fdfea72bacc | textbox | Expiry (If applicable)
64b87110-3437-5e54-a36f-8833095a9204 | textbox | Record Number
e80865f1-4998-5e3b-be7b-54c7f2796d97 | textbox | Date Calibrated
34d9b119-0f4e-48ea-919f-b4db42fc64f1 | checkpoint | 1.Calibration Details - Pass once entered
2af769ad-8dca-556f-82be-e2ab2f074733 | textbox | Equipment
d74375e3-7024-5016-901f-8e3b893ca45f | textbox | ID Number
68881979-17e9-5384-bbc1-4b0c13049fd9 | textbox | Expiry (If applicable)
fb5fa211-8743-5492-bf44-b7f2f6f3095b | textbox | Record Number
9bd931e0-020f-5c18-b093-4febf26c5f26 | textbox | Date Calibrated
c3a28e28-8ead-45ce-b591-d707ead60072 | checkpoint | 1.Calibration Details - Pass once entered
2e4359d2-d6de-5370-b367-8047a78431c1 | textbox | Equipment
36443c9c-ae1e-54f4-9cf7-1fa55cb6c30f | textbox | ID Number
6c0a36a9-1ac1-54d3-a564-b3ad2c898eb2 | textbox | Expiry (If applicable)
644175bd-099d-5d1b-88ce-54da3394680a | textbox | Record Number
bfae0574-d627-5355-b130-c755ac705f3c | textbox | Date Calibrated
a7bf746c-a523-4756-93d3-2c4dfcdffb5d | checkpoint | 1.Calibration Details - Pass once entered
f4e86714-1781-550e-880b-4e0842624d62 | textbox | Equipment
92b87664-34fb-5d85-8de0-4d03be7c5511 | textbox | ID Number
df69a3ed-298e-5f73-a771-bafd9326eb1d | textbox | Expiry (If applicable)
51930264-7dc5-5563-b8c9-1fa8bbdada65 | textbox | Record Number
5459ea8a-0639-5610-b139-ec0f4c3adc60 | textbox | Date Calibrated
a9c44ce5-5671-4e94-aded-be3e4bf866c7 | checkpoint | 1.Calibration Details - Pass once entered
09313e47-229c-5e91-b4ad-7cfad9393121 | textbox | Equipment
106e4f9f-0be0-5c40-a8b5-b8297986c408 | textbox | ID Number
b3229b00-9cc6-5089-b84d-b14697a09653 | textbox | Expiry (If applicable)
b448f19e-e5c3-571f-9c9e-7864b91ebe3c | textbox | Record Number
7210e865-711b-578a-afca-aace8556fb92 | textbox | Date Calibrated
18db940f-c130-4183-b872-548008835090 | checkpoint | Sign-Off Records completed
5afe8df0-0298-5f8c-a3bf-f75f28eb1004 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
494f45a7-d7da-5f17-98f4-4452a56f07a5 | button | Entire Fire Signature Sign-Off added below | Yes, No
cecd2aca-223e-4eae-a90f-c9301eece4da | checklist | EFPQF21 - Action Request |  | EFPQF21 - Action Request
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
e790564c-b82d-4d2e-96e9-834ca60b027c | checkpoint | Action Request Details - Pass once entered
8eca7afa-4cc4-5bb0-b061-a4321939e55f | textbox | Action Request Number
e78adc4f-abd1-51df-ac02-892e1b1da63e | note | This action request is a result of (Tick below)
61cb6dec-e102-52a2-80fd-836890323ff8 | tickbox | Audit
c9b3491d-af76-5d38-a001-d3ffd0b9fbac | tickbox | Failure
88829f4f-93c7-5e1c-8f2d-a19436ef1ffc | tickbox | Non-Conformance
baf877cb-ca89-5cb5-92cb-056bc75991ff | tickbox | Process Improvement Idea
0e2817d0-4b92-5858-bc24-a317c31e2e8a | tickbox | Customer Complaint
ee02cb65-aeea-53e8-ad74-9fee01d079fc | tickbox | Corrective/Preventative Action
5e6b86e3-04dd-4de5-bd78-d2ba75ee463d | checkpoint | Description of failure/Non Conformance/Improvement Idea/Customer Complaint
31d43346-0ed4-5bfa-aa10-644ee834d7ad | note | Send to Quality Manager for allocation of number and passing to appropriate person for action
d9a17ec9-3033-5f20-8825-a82aca7a3797 | textbox | Details
5a4440f9-b0bd-5f26-9a33-adc1d3d4bcb4 | textbox | Reported By
e0ea39ee-b4bc-53ae-840b-55fc565e6f04 | textbox | Date
ffa1d803-523c-455a-a98e-4b1ce81254fa | checkpoint | Investigate cause and list details
126ad9fe-8ccf-5058-bc38-2a52da3f451d | note | State action when and if there is a deeper underlying issue or problem
870e83d8-572f-5712-9d73-fa00d16d23cc | textbox | Details
c743afa8-6f03-5edc-9446-b7c253501fba | textbox | Assigned To
38c763d2-4d1d-54d5-bfcb-4b14828857db | textbox | Date of Completion
3f6d64db-bb98-57c9-91fd-25ce22123542 | note | Signature Sign-Off attached below
3386771b-cd73-4f66-8862-1940ce32b136 | checkpoint | List details of deeper underlying issue and corrective action
6dedd1f9-3453-50e5-93fc-4c8514b0fecf | note | This section only applicable if above indicates the need
c14a074d-e03b-5866-889b-fb0fd0296b1e | textbox | Details
59a008f3-8604-5a0e-981c-e40844c8d2a0 | textbox | Assigned To
c750d4f3-940e-5d06-bd7f-371ef70366a7 | textbox | Date of Completion
6db13648-c436-5021-a154-b93809e0def4 | note | Signature Sign-Off attached below
72ea7f6a-2048-4623-8f81-86af92357ab3 | checkpoint | Verification/Follow-up
145e38bf-95c5-5c36-915b-7603449b1d6f | textbox | Details
a672c256-d451-50cb-8783-cf6b4fe15c27 | textbox | Assigned To
3c32d149-d154-5bd5-8fe4-be4df6666296 | textbox | Date of Completion
c18788a7-5b89-5ec0-85ed-3e0c389969ee | note | Signature Sign-Off attached below
e0a8bdef-611e-4322-8ae0-d8f9c7ced8de | checkpoint | Sign-Off Records completed
b8a48069-b520-5fad-9d60-35a5cda8fb8b | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
9db3ac0a-a6fe-5f6c-8cca-1e784af0c08c | button | Entire Fire Quality Manager Signature Sign-Off added below | Yes, No
a18c5aab-cd56-4520-8845-e1f56d0e5a59 | checklist | EFPQF22 - Register of Non-Conformance Reports x10 |  | EFPQF22 - Register of Non-Conformance Reports x10
bb3f7f98-6afa-45d4-a9db-35e95a42a00e | section | Details
16081060-d22f-4a8a-9940-605a536b8752 | checkpoint | Item 1. Pass once entered
d03371db-3ac7-5e2c-b787-bdf6f5af1394 | textbox | Report Number
34c39c61-d7f1-58b0-8b39-654b6f4aeeef | textbox | Description
d7da86c8-09a4-5fea-9650-1a8a71dbdaff | button | Non-Conformance rectified (Input date below) | Yes, No
45ad7317-f37c-566b-83ee-98efef2bb3a8 | textbox | Date rectified
863e366f-996d-5b28-819e-fc883175f2c9 | button | Non-Conformance approved (Input date below) | Yes, No
0f38f75b-8255-4e66-822c-9dff57d4cfbe | checkpoint | Item 2. Pass once entered
02184978-9c96-5e51-9d1a-33948a2ca968 | textbox | Report Number
9c863d60-5713-5157-9e90-8fe9c776657c | textbox | Description
299b065e-df59-5638-98c3-497822dd9c1d | button | Non-Conformance rectified (Input date below) | Yes, No
d9b1aba5-bd55-5810-acde-d70677e983ec | textbox | Date rectified
7ca0b50c-6006-574a-b0e9-40789b7a1067 | button | Non-Conformance approved (Input date below) | Yes, No
a1e5a8e1-b460-47f3-ba5c-2b38089b709f | checkpoint | Item 3. Pass once entered
68af7adc-ea62-5117-9583-a39e06a9f6f8 | textbox | Report Number
d84a2509-6f3b-5fc4-a7c3-89185b417fb2 | textbox | Description
e99c1121-8f82-54cb-9044-912174ea2bbb | button | Non-Conformance rectified (Input date below) | Yes, No
4425e5ed-d63b-57b6-9639-e799388634f0 | textbox | Date rectified
538cbb22-2923-544b-8101-10d5cb83fae7 | button | Non-Conformance approved (Input date below) | Yes, No
cb38a6ab-01ab-40fd-9c54-81efa4d7c0dc | checkpoint | Item 4. Pass once entered
2d47e05f-77e6-5466-abcf-e9c65561b1cf | textbox | Report Number
e2ab3c4a-4d58-5e1a-a2a7-03b6a34bf5ae | textbox | Description
a915196e-3f4d-5496-b90a-09c3cd2c32fa | button | Non-Conformance rectified (Input date below) | Yes, No
a5d1ddfb-0a52-5700-a625-ea60b5adaaae | textbox | Date rectified
017015ad-a4c3-52fc-8be3-700da3b51131 | button | Non-Conformance approved (Input date below) | Yes, No
95bf2983-21d8-42a3-a4a1-3f22f6e0d143 | checkpoint | Item 5. Pass once entered
e8602794-43e8-52c9-a791-dfc8c15a2be5 | textbox | Report Number
5e63edca-7066-5f55-9b31-c0e23fbd8227 | textbox | Description
d0d9a85d-f865-5e42-bb94-1f67915335fd | button | Non-Conformance rectified (Input date below) | Yes, No
68a0c55d-92ad-53ec-adc9-5be8c2de793f | textbox | Date rectified
1e6d58e4-20b7-5ae1-8b45-5dd0ba345501 | button | Non-Conformance approved (Input date below) | Yes, No
da4e1461-67bf-4e03-9993-74f0b04ee6f9 | checkpoint | Item 6. Pass once entered
16bc52fc-3e63-583f-8ed5-c03085e9b221 | textbox | Report Number
e1b80da7-c1f3-55c6-a16b-398e9d6dae63 | textbox | Description
68d41c43-e197-59bc-a8f7-ad2ea7c8dc00 | button | Non-Conformance rectified (Input date below) | Yes, No
4f52b75d-cbbc-5380-b645-8079d1c33ea0 | textbox | Date rectified
1c5821e4-0962-5267-8ec7-176138065f30 | button | Non-Conformance approved (Input date below) | Yes, No
1b2e38dc-b219-4e49-94d8-4320a55d12ef | checkpoint | Item 7. Pass once entered
8fb13537-c66f-5349-a567-8cf13170e4f8 | textbox | Report Number
f7c072ba-0274-5b3f-a04e-b53c99daf2c5 | textbox | Description
c3b1ca08-ecd3-5ca8-b76e-4776772bafbc | button | Non-Conformance rectified (Input date below) | Yes, No
60df4db3-290f-5c6e-ad06-a438df43ce0d | textbox | Date rectified
64eeaff1-4ff4-5635-bd1e-e2ecf449d9d5 | button | Non-Conformance approved (Input date below) | Yes, No
7f81e6c6-bf14-4a12-a673-7a5d2c409f2c | checkpoint | Item 8. Pass once entered
152ea86d-8864-545c-b7f7-bf3fd23cb16a | textbox | Report Number
ad7b4ed3-8286-5c4a-b6c3-00a95bbf535b | textbox | Description
4523e02e-0fdb-5be6-a730-f7343b83822f | button | Non-Conformance rectified (Input date below) | Yes, No
b47d5753-6f7a-5479-913e-12c78f522517 | textbox | Date rectified
efd2a84b-8821-52de-b9ea-b6c40a15b6c1 | button | Non-Conformance approved (Input date below) | Yes, No
59834f79-61f5-449d-99dd-1477cc33ae56 | checkpoint | Item 9. Pass once entered
143793ca-287b-53a2-9b69-3aaf7ff7cd17 | textbox | Report Number
087ed80e-c973-58e0-bf97-21d0d999b042 | textbox | Description
ec789d18-a97f-51dd-86ae-020c7bd6b775 | button | Non-Conformance rectified (Input date below) | Yes, No
1955a168-b7ed-5873-b6af-353af0fd8df3 | textbox | Date rectified
107d1f25-3f3d-51ce-b963-44a9f5921c5f | button | Non-Conformance approved (Input date below) | Yes, No
b4ffb715-cea3-42a7-a684-8ed8b94cb0d9 | checkpoint | Item 10. Pass once entered
c46726e6-db24-5d6c-a91b-1dd62de427be | textbox | Report Number
9c5d1e0b-4ec4-5503-a02e-6a524c9cce83 | textbox | Description
cf2e0354-cb01-5f37-a2d2-0633e28822d7 | button | Non-Conformance rectified (Input date below) | Yes, No
d228672e-f30b-5aa0-a810-8a9fb71e140d | textbox | Date rectified
f51c88a1-2e0c-550a-975d-7b265eb399b6 | button | Non-Conformance approved (Input date below) | Yes, No
b3f7da19-33e8-4682-91ea-c525fa77c717 | checkpoint | Sign-Off Records completed
870ae145-d0fb-5a06-85ae-1d826dadbc75 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
7274c668-1d62-5fca-9756-16756f38fee7 | button | Entire Fire Signature Sign-Off added below | Yes, No
1ea0b3ef-6c46-4c82-80ae-9f6fe389d1e8 | checklist | EFPQF27 - EWIS Commissioning |  | EFPQF27 - EWIS Commissioning
27d530c4-f511-4e9d-8ed1-3da93921a045 | section | Details
8d56001c-0052-4277-8a1b-a1f85b708157 | checkpoint | Download, fill in and upload completed EWIS Commissioning sheet
478cef79-6bda-49ba-97d4-53e753a00684 | checklist | EFPQF28 - Fire Matrix |  | EFPQF28 - Fire Matrix
d0b623a3-c5c4-4a69-b781-a64ea96709ef | section | Details
a3c71a80-9782-41fc-a19e-aa876346e2b3 | checkpoint | Download, fill in and upload completed EWIS Commissioning sheet
b0d8e586-d6ac-48b2-b0ac-908babfd1436 | checklist | Ω (DEPRECATED) EFPQF08 - Fire Alarms Install |  | EFPQF08 - Fire Alarms Install
0fbcb6f4-a662-4f3e-b855-4366c3edea79 | section | Documentation
b32993ec-eb0a-462b-a170-d0bc874e216b | checkpoint | Confirm construction drawings approved for use.
a4b69e1b-ed7e-48c6-807b-890c9451b72f | section | Incoming Inspection
701a8129-1362-4588-86bc-c23bf3a5aebc | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
3da4a757-602a-5a25-bf7d-1a742acfeaa5 | tickbox | Fire rated cable
7030282d-ffbf-579c-9f53-e0cc28c74195 | tickbox | TPS cable
b79984f1-dddb-5f97-ac06-e728fdc7496d | tickbox | Detectors
6d8fc1a9-faeb-5175-bd14-1e88b116a9a4 | tickbox | Strobes
66edc632-ceb4-5305-b354-01e290bcfd8f | tickbox | Speakers
d628f3ce-97cb-4159-b097-c49ac708236a | section | Installation Rough In / Fit Off
f253b6be-66f6-47df-ab79-6a6e68235774 | checkpoint | Confirm correct cable type run
d954aa8b-a3e6-482b-94ac-acb786efd7af | checkpoint | Confirm cable support/conduit fixings and spacings
55937f0c-d2dc-4781-b78b-c9aaa436a5cb | checkpoint | Confirm segregation from other electrical services
a9f20cdc-6081-43bc-9d86-d4764a7aa1b3 | checkpoint | Confirm detector fit off locations
d0659338-d73a-4ede-b82e-607a769a2abf | checkpoint | Confirm speaker fit off locations
ca8a7ec2-bcaa-438b-ab44-fa29f7235f23 | checkpoint | Confirm strobe fit off locations
839f5cf8-4c5b-42ea-9b0a-4be6ac3589ef | checkpoint | Confirm fire interfaces connected to sprinkler installation
fd6f84fb-a2b4-4c31-b49b-210540055515 | checkpoint | Confirm fire interfaces connected to security
b0e9d7cd-d60f-4140-b927-d926b1ac3a9e | checkpoint | Confirm fire interfaces connected to mechanical
39983372-6851-4f36-ae99-1c3e70f15991 | checkpoint | Confirm fire interfaces connected to BMS
73f9f35e-6b32-4686-a39c-67dcc76bd6dd | section | Sign-Off
3b8fa25d-978a-433e-821c-baebf6550b44 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
a7b71ec9-fb38-456f-92b2-e34b9c011904 | checklist | Ω (DEPRECATED) EFPQF10 - FDCIE Install |  | EFPQF10 - FDCIE Install
852e2488-c3ae-438e-bcfc-a233e8afb95a | section | Documentation
ff6ef055-e80d-4f6e-9d7c-9cdc55430b9d | checkpoint | Confirm construction drawings approved for use.
5ecc9a43-3970-4c8b-a9ca-ee6ad1bcf5e4 | section | Incoming Inspection
91eed048-773d-4a70-9c94-fda79b64d9a4 | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
c7674618-79fb-56c4-9685-89d7eb73d518 | tickbox | Fire rated cable
dd662592-f724-5f93-9095-74cd8b529d3d | tickbox | TPS cable
dc19e916-ff6a-5b1b-8f3f-9f709047bc4b | tickbox | FDCIE Panel
2b59acec-eb82-427c-96e1-8b21999c9f43 | section | Installation Rough In / Fit Off
fb306922-0168-4cfb-a899-fbd82a759d22 | checkpoint | Confirm correct cable type run
14ed266b-87f0-4224-824a-4f7aaa75fa5a | checkpoint | Confirm cable support/conduit fixings and spacings
c1be3744-2642-4d35-b64c-353ee6691ff0 | checkpoint | Confirm segregation from other electrical services
4a220956-25a0-4c8b-9f4f-3032b73a9e57 | checkpoint | Confirm FDCIE mounted in correct location
67a58526-de18-4fab-8f19-e4e692a5431e | checkpoint | Loop cables terminated to correct output
97629c14-51b0-40e9-b38d-bda191ba0a0e | checkpoint | Confirm OWS cables terminated to correct output.
16646843-b057-425c-9e14-196e4ff94a57 | section | Sign-Off
99762377-ba7b-40b5-897d-d2f8552d7fd7 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
5f343f2e-8ef4-4351-b54a-5cca275e3931 | checklist | Ω (DEPRECATED) EFPQF19 - Occupant Warning System Install |  | EFPQF19 - Occupant Warning System Install
d6a00970-34e1-47e7-b1ff-e25a809b29ad | section | Documentation
ca7a8762-46c0-46d2-87c1-7eab0baa49f3 | checkpoint | Confirm construction drawings approved for use.
e5b607e9-294a-40cf-a9e5-c36e99fbc2e0 | section | Incoming Inspection
9f6c8134-7c1a-4428-ba27-3f4fa441d28c | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
3d0cb9d5-9739-5c08-8f18-188c2302998e | tickbox | Fire rated cable
acae3654-5128-5b37-bd5b-1a48e7974c78 | tickbox | TPS cable
2a0d0952-2446-539b-9759-c5320d185ddd | tickbox | OWS Panel
752c3e53-b762-5783-99e5-95309eb1d0ad | tickbox | Speakers
9c9763bd-aa62-5b7b-a4c9-d347185df0fe | tickbox | Strobes
af8c8301-3650-583a-9f72-ac22f54a5f9a | tickbox | VAD
6209da7b-843e-40e6-8815-72e22c3b2875 | section | Installation Rough In / Fit Off
e70d2a3f-e88c-4c3c-a965-464c010a59df | checkpoint | Confirm correct cable type run
433723b7-cf61-56e4-ae86-8bf34b2e72ef | note | Acceptance Criteria - AS:1670
182926c5-8230-4e34-84a1-e7db70b6d9a1 | checkpoint | Confirm cable support/conduit fixings and spacings
7dbe0946-9335-5013-9b9f-2f5570552c90 | note | Acceptance Criteria - AS:3000
5014a035-6e27-4eee-b866-cfc01bf498f0 | checkpoint | Confirm segregation from other electrical services
f2e0044e-ff47-56d3-808d-b89d63f4505a | note | Acceptance Criteria - AS:1670
b10f08fc-1c5c-4654-a2e0-e6a8d1d507f2 | checkpoint | Confirm OWS mounted in correct location
ce5d4fe0-7804-440d-a258-ae581649e970 | checkpoint | Loop cables terminated to correct output
39235b56-b3ee-4ceb-bfde-89f09f5d2db4 | checkpoint | Confirm FDCIE cables terminated to correct output.
37f78fc4-7fbc-48cc-a071-2234a5487841 | section | Sign-Off
8d1f7da9-815c-4da6-a3da-5695eb745649 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable