## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-050 - NPD - Structural Steel Installation | itp |  |  |  |  | ITP-050 - NPD - Structural Steel Installation Rev1
section | 1 - Design and Submissions
checkpoint | 1.1 Check for correct documentation
note | FREQUENCY: Prior to commencing any activity
note | ACCEPTANCE CRITERIA: Ensure that all employees and subcontractors are:
note | – using the correct and complete set of drawings
note | – all drawings are the latest revision
note | REFERENCE DOCUMENTS: Drawings and drawing registers
note | INSPECTION/TEST METHOD: Visual inspection
note | RECORD OF CONFORMITY: This ITP signed
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 1.2 Implementation of all measures and controls
note | FREQUENCY: Prior to commencing any activity
note | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
note | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
note | INSPECTION/TEST METHOD: Visual Inspection
note | RECORD OF CONFORMITY: This ITP signed
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer JSME
textbox | DATE:
checkpoint | 1.3 Base Plate Grout or Mortar
note | FREQUENCY: Once, for each product, prior to placement of product
note | ACCEPTANCE CRITERIA: Product to be selected based on the following criteria:
note | i. either a single component, self consolidating and dual shrinkage compensating cementitious grout
note | ii. have the required strength at 28 days as noted on the IFC drawings, but 40MPa minimum
note | iii. have a flowable consistency
note | iv. the surface preparation matches the concrete surface underneath the post base-plate as per the IFC drawings (see 5.1 also)
note | v. have the characteristics capable of being applied to the minimum and maximum thickness as noted on the IFC drawings
note | REFERENCE DOCUMENTS: IFC Drawings
note | INSPECTION/TEST METHOD: Document Review
note | RECORD OF CONFORMITY: This ITP Signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
section | 2 - Installation Activities
checkpoint | 2.1 Material Inspection
note | FREQUENCY: Each Component
note | ACCEPTANCE CRITERIA: General inspection of structural steel elements for defects including cracks, handling and storage damage & distortion.
note | • Bolts, nuts and washers shall be the size, material, strength grade and coating as noted on the IFC Drawings.
note | • Where bolted faces are sloping at 1:20 or greater, tapered washers must be used.
note | • Galvanised coating - no loss of adhesion, damage, blisters, roughness, sharp points and flux residues.
note | • Paint or powder coating - uniform in appearance, colour & texture with no loss of adhesion, damage, blisters, holidays, chalking or any other visible defects.
note | REFERENCE DOCUMENTS: IFC Drawings
note | • AS4860 Clause 7
note | • AS2312 Clause 9.6.4 (i)
note | • AS4506 Clause 2.3
note | INSPECTION/TEST METHOD: Measure, Visual
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.2 Structural Steel Handling
note | FREQUENCY: Each component
note | ACCEPTANCE CRITERIA: The method of handling and erection of the steelwork shall ensure that the members are not stressed or deformed beyond the design limit and that there is no damage to the protective coating during these operations.
note | • Where damage exists, it shall be repaired using an approved repair procedure for both steelwork and coatings.
note | REFERENCE DOCUMENTS: Contract Drawings
note | • AS4100 Clause 15.2.2 & 3
note | • AS5131 Clause 11.5.6
note | INSPECTION/TEST METHOD: Visual
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.3 Structural Steel Erection
note | FREQUENCY: Each component
note | ACCEPTANCE CRITERIA: Place steel component into position, ensuring that it is plumb, level, square and within tolerances shown in 5.6.
note | ○ Where mounting to supports or foundations, adjust RL accordingly using suitably sized shims, levelling or jacking nuts (where applicable).
note | ○ Where steel to steel connections exist, holes shall be aligned so that a drift pin equal in diamter of the bolts can pass through freely.
note | ○ Where a misalignment is found, heating of bolts, hand flame-cutting of holes or (heat) drifting of holes shall not be permitted, only rheaming, milling, drilling or machine flame or plasma cut. Internal surface of the hole to remain smooth and free from burrs.
note | ○ Holes shall not exceed the greater of:
note | • 1.25 x bolt dia. OR bolt dia. + 8mm
note | ○ Slots shall not exceed the greater of:
note | • 1.33 x (bolt dia. + 10mm) OR 2.5 x bolt dia
note | REFERENCE DOCUMENTS: AS4100 Clause 15.2.3 AS5131 Clause 11.5.7
note | INSPECTION/TEST METHOD: Measure, Visual
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.4 Fastener Tightening - Snug Tight Condition (4.6/S & 8.8/S)
note | FREQUENCY: Where applicable, each bolted connection
note | ACCEPTANCE CRITERIA: Place bolts, washers and nuts as detailed on the IFC Drawings.
note | • Washers shall cover the hole or slotted hole completely by 0.5 x bolt diameter.
note | • Tapered washers shall be positioned if the surfaces are on a slope of 1:20 or greater.
note | • Tighten from the stiffest section working towards the free edges with a few impacts of an impact wrench or the full effort of a person using a podger spanner.
note | • Protrusion to be at least 1 clear thread shows beyond the nut but no greater than 12mm.
note | REFERENCE DOCUMENTS: AS4100 Clause 14.3.5.2
note | • AS5131 Clause 6.7.4
note | • AS4100 Clause 15.2.5.2 (a)
note | • AS5131 Clause 8.3
note | INSPECTION/TEST METHOD: Measure, Visual
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.5 Survey Conformance
note | FREQUENCY: Each element
note | ACCEPTANCE CRITERIA: Grouting of base plates shall not commence until verification that the Works meet level and location requirements within the tolerances below:
note | • Departure from RL = ±10mm
note | • Departure from plan position = ±6mm
note | • Departure from alignment = ±6mm
note | • Irregularities in alignment = 25mm in 30m
note | • Projection of bolt = +25mm, -5mm
note | REFERENCE DOCUMENTS: IFC Drawings AS4100 Clause 15.3.1 - 7 AS5131 Appendix F, Table F3
note | INSPECTION/TEST METHOD: Measure, Visual
note | RECORD OF CONFORMITY: This ITP signed
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.6 Base Plate Formwork Construction & Placement
note | FREQUENCY: Each Column Location
note | ACCEPTANCE CRITERIA: Dimensions as per drawings to achieve the profile.
note | • Formwork rigid, sufficiently braced to support the pressure of the grout/mortar product and sealed to prevent leaks.
note | REFERENCE DOCUMENTS: IFC Drawings
note | INSPECTION/TEST METHOD: Measure, Visual
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.7 Pre-soaking Concrete Surface
note | FREQUENCY: Each Column Location
note | ACCEPTANCE CRITERIA: Pre-soak the concrete surface with potable water for the recommended time frame indicated on the Product's TDS.
note | • Prior to mixing the product, remove excess water that has not leaked out of the forms or been soaked into the substrate by appropriate means such as a leaf blower.
note | REFERENCE DOCUMENTS: Product TDS
note | INSPECTION/TEST METHOD: Visual
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.8 Mixing Product
note | FREQUENCY: Each batch
note | ACCEPTANCE CRITERIA: Size of mixer should match the application.
note | • Only whole bags to be mixed with potable water.
note | • Volume of water matches the required amount for flowable consistency and accurately measured.
note | • Product poured into the mixer slowly.
note | • Mixing time as per TDS so that a smooth, even consistency is obtained.
textbox | Enter: Required information on the Grout Pour Record.
note | REFERENCE DOCUMENTS: Product TDS
note | INSPECTION/TEST METHOD: Measure, Visual
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.9 Placement & Compaction
note | FREQUENCY: Each Column Location
note | ACCEPTANCE CRITERIA: All batches are traceable.
note | • Product poured from one side of the formwork to eliminate the entrapment of air or surplus pre-soaking water.
note | • Product should flow to all areas and self consolidate.
note | • Product that stiffens or is showing signs of stiffening shall not be used.
textbox | Enter: Required information on the Grout Pour Record
note | REFERENCE DOCUMENTS: Product TDS
note | INSPECTION/TEST METHOD: Visual
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.10 Surface Finishes & Protection of Works
note | FREQUENCY: Where applicable
note | ACCEPTANCE CRITERIA: If shaping of the unformed surface is required, shape prior to the product fully hardening.
note | • All freshly finished surfaces shall be protected where required from the sun, wind or rain. If applicable, implement curing measures as per product TDS
note | REFERENCE DOCUMENTS: IFC Drawings Product TD
note | INSPECTION/TEST METHOD: Visual
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
section | 3 - Post-Installation Activities
checkpoint | 3.1 Inspection of Coating
note | FREQUENCY: Each component
note | ACCEPTANCE CRITERIA: After installation Works are complete, inspect the steel element for damage to the coatings.
note | • Where damage exists, it shall be repaired using an approved repair procedure.
note | REFERENCE DOCUMENTS: IFC Drawings
note | • AS4680 Clause 8.3 & 8.4
note | • AS4506 Appendix E
note | INSPECTION/TEST METHOD: Visual
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 3.2 As-built Survey
note | FREQUENCY: Each component
note | ACCEPTANCE CRITERIA: Provide record of dimensional measurements to demonstrate that all Works meet level and location requirements within the tolerances below:
note | • Departure from RL = ±10mm
note | • Departure from plan position = ±6mm
note | • Departure from alignment = ±6mm
note | • Irregularities in alignment = 25mm in 30m
note | • Projection of bolt = +25mm, 5mm
note | • Attach: Survey As-builts / Survey Report
note | REFERENCE DOCUMENTS: IFC Drawings AS5131 Appendix F, Table F3
note | INSPECTION/TEST METHOD: Visual
note | RECORD OF CONFORMITY: As-Built Drawing
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | Print Name:
text | Position:
text | Date: