## Master List Templates
Id | Type | Name | Values | Prompting Name
72644a6c-34e1-530c-a7e8-5351e29f25a3 | checklist | Backflow Test Report Water Authority Approved |  | Backflow Test Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
585974c6-02cb-514b-9e87-5b7ac108700e | checkpoint | Description of property or vehicle
91e79822-8dde-5aaa-81f9-ad08e78269e1 | note | The description must identify all land or vehicles covered in the application
d284e6b4-f929-58b8-94d5-0b328a9cf63d | textbox | Street address (number, street, suburb and postcode)
4a848919-0a0e-541f-a59c-c2625acc7dab | textbox | Water authority property service / installation number
9dc5fb52-17c2-530c-a000-50835cf81245 | textbox | Water meter number
eb7d2055-3881-5790-b5ce-e9490cc3e55d | checkpoint | Type of test
38a9d5f6-b05a-5498-98c5-4bce9616c23c | tickbox | Commissioning of new device
8815a749-aa74-5e87-ab81-c49f5d75a947 | tickbox | Replacement
1abf7be1-a725-53fe-86df-cd47f8d1769d | tickbox | Annual
8d5f7a6e-e223-5aec-9068-1f6429463172 | tickbox | Repairs
eabc2bab-5633-5361-806d-02a5912b0381 | tickbox | Decommission
b0097003-182e-5bee-9086-d9aecfce067d | checkpoint | Backflow prevention device location
dabf55fa-a50b-5e34-aa0f-f1178dd403b7 | textbox | Location of device (eg: Northwest side of building @ FHR external)
0f7e2599-45b6-5ae7-aeff-a9e32a79ea55 | textbox | Mains pressure (kPa)
167cc3d1-a150-5625-91b7-98a2ff866f98 | textbox | Time and date of test
195a525d-2640-51ef-86c4-48fc1bd7b51f | checkpoint | Main device
3f607054-57b2-56fd-b5a3-bdd681f9125b | tickbox | RPZD (E)
4451b81e-49c5-5893-a754-f1aabfbea05a | tickbox | DCV (F)
62c14501-fdb5-5157-8ba8-a68b3c58c61c | tickbox | SCVT (I)
4184f236-50c4-5177-9856-70f36e54b629 | tickbox | Containment
279b225c-e44e-5aa9-a574-3ca1b344a48e | tickbox | Zone
8eed17e7-55b9-5e08-bab3-9e3a37d050e4 | tickbox | Individual
c9db3a6a-76e1-5823-bf3f-a52d6a8e51d2 | textbox | Make
9457a020-8737-57ff-858b-75daf7e11cfe | textbox | Size mm
7b3015ab-e9e0-5035-9c59-7fb0cbf10929 | textbox | Model
09e8e5b3-85e2-53c5-885b-451cc7ba6d26 | textbox | Serial number
a2a6c3c8-2301-5317-91a1-aae5b5896c45 | button | Cleaned strainer | Yes,No,N/A
58b40ab6-c938-530b-bc7b-d08afedd0d60 | button | Upstream IV | Leaked,Tight
e1b28486-56bd-59ee-aa85-4ce4c68719a8 | button | Downstream IV | Leaked,Tight
037c66ea-b7d8-5f7f-9602-7acb9d67cae9 | textbox | Check valve #1 (kPa)
5ebdaeaf-8ef3-52ef-ba56-5233fb655e6f | textbox | Check valve #2 (kPa)
afc60cf1-7e69-554c-a659-1b74fa1489e5 | textbox | Relief valve opened
0cba4129-b150-5f77-a2f5-6454677b69d6 | checkpoint | Device installation notes
fdd1c243-3089-52b3-af5c-90b48c74adfa | button | Isolating padlocks installed | Yes,No
0344672a-becd-5883-9173-5ac4205d9314 | button | Installation complies with AS/NZS 3500.1 | Yes,No
4c6f0025-e719-525b-81ac-ef265d68a9e7 | checkpoint | Test kit
ae15db3e-6952-5cef-95d1-8ada9b262ca1 | textbox | Test kit serial number
aadc8d9f-7ee3-56a0-9656-caa41158d9ca | date | Date last calibrated
b65a095e-ac93-52c6-b0db-1e184e5966f0 | checkpoint | Authorised testers details
10c31868-8c42-5421-8cd4-4a74de251d0d | textbox | Testers name
d5dcd8c6-8dcd-5d91-996f-dfc18faf8517 | textbox | Registration licence number
a93227d5-1a19-5a17-88a6-a5daeab6485d | textbox | Phone number
3d9483e0-efb8-5e50-ad56-69f06fa15b7b | checkpoint-no-value | Licence person
bdc0c5c3-19f3-57aa-8610-ec2e6d576a0a | note | Full company name - Geschke plumbing
10d62ae7-66af-5714-bd04-14174f6d98d4 | note | Licensed tester name – David Geschke
01ba6182-b263-5b04-ba70-d2c8917ea205 | note | Licence number -50043
53a86f34-72bb-5c37-a036-58be8b5e2241 | checkpoint | I hereby state that the information provided in this form is a true and accurate record. I have tested the above device/s in accordance with AS/NZS 2845.3:2020
fffa76eb-8043-5d23-b241-64d19d311e66 | note | Note: Failed devices must be repaired and retested within 20 business days as per the Water (Estimation, Supply and Sewerage) Regulation 2014.
293ff535-4f83-5dac-b044-caeb4ce197e8 | textbox | Signature licenced plumber
7419f545-15ef-5d6c-b003-dab505d3db76 | date | Date
e73241f0-0943-57bb-8c1c-35dd4ee1589d | textbox | Signature tester
b8763db2-dd2a-5dee-bc73-25179502e2df | date | Date

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Prefix | Postfix
47bbc3c2-c416-47c0-a677-264c4e3f3ed2 | checklist | Add Fire Penetration Checklist |  | Fire Penetration:
3ceb5017-f665-4a7b-ad4d-bfc7b19b195f | checkpoint | Treatment Type
79b1a475-a9f3-576f-8479-28beda087851 | dropdown | Treatment Type: | A1,A2,B,C,D,E,F,G,H1,H2,H3,J,K,M,N1,N2,O,P,Q,R,S,T,V
22d3ae07-2155-4a62-9d46-44bbe6bcc986 | checkpoint | Photo of penetration and sticker must be taken
1053f95e-28eb-5176-9568-0b74aeec1e72 | textbox | Installed by:
4d560f5c-5d42-5ad1-8354-e5d79725cae9 | textbox | Comments / Reasons why cannot complete:
255cc89c-95d3-4852-a80c-e86bd590611e | checklist | Add Project Photos |  | Project Photos
a3a0ad49-43f8-4aaf-9c05-ceb526906524 | checkpoint | Attach Photos and Comments
dc780dec-221d-42ab-9a60-ca83b88eba54 | checklist | Backflow Test Report |  | Backflow Test Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
72ce784b-a72e-4c5e-9bb3-e43f30a09502 | checkpoint | Description of property or vehicle
f5c6a856-f844-59f6-97a0-720e09fd1a2c | note | The description must identify all land or vehicles covered in the application
917b91fb-efe7-59cf-84ca-c158a0d85d42 | textbox | Street address (number, street, suburb and postcode)
59f0b3f5-d4d9-5105-a188-d9e3efff7c4b | textbox | Water authority property service / installation number
52c3379f-4af8-5b41-957c-d11299e28715 | textbox | Water meter number
60e8f9e0-d586-41ac-8e93-db7c9a5bd4a0 | checkpoint | Type of test
8c52b20b-90ef-579a-af12-b447e50a1977 | tickbox | Commissioning of new device
2a886bef-76f1-5638-8fff-5a35ea760759 | tickbox | Replacement
71143247-bf7d-560b-9456-ecb495fa5d44 | tickbox | Annual
e9760a4b-a377-5f16-845c-0bda0ceb2cc7 | tickbox | Repairs
b8d0cd52-4146-5502-be10-7d720d251cce | tickbox | Decommission
c3d75610-ad20-42a1-8fc0-ce7cc736731a | checkpoint | Backflow prevention device location
37eb3f4d-a2e2-51a9-bbe2-7c39ed1d9923 | textbox | Location of device (eg: Northwest side of building @ FHR external)
becca536-b89b-5315-9206-023d84a59e64 | textbox | Mains pressure (kPa)
3d9d44e2-f5df-56ed-b20f-c62d7fd7ceba | textbox | Time and date of test
50270579-661c-475a-af67-d7fabbfaa486 | checkpoint | Main device
d7258235-40d2-5ae8-85c8-a047189645ab | tickbox | RPZD (E)
44c228a9-2e53-5ac5-982d-3baf21d286c3 | tickbox | DCV (F)
f9d8ecca-2b8f-54ea-86c5-1d9073aef899 | tickbox | SCVT (I)
4b4c6023-8271-5cba-b5bb-f126febb8ac4 | tickbox | Containment
9b10c19f-fdc6-5dbc-b7fc-2f058e30c185 | tickbox | Zone
ef2ed69d-f7e4-58da-a795-5fc9f2571106 | tickbox | Individual
33607420-d6b5-5fae-846f-efdd7209c502 | textbox | Make
8ddd54ca-cebe-5bbb-bd1d-1e6b2465afa2 | textbox | Size mm
e6cdb67e-0a16-5c01-b5cf-4bfbbfa8f787 | textbox | Model
f3c15890-4084-55e3-af31-8f383b186ec7 | textbox | Serial number
9deba725-df68-5006-9c75-d25aeccd6bc9 | button | Cleaned strainer | Yes,No,N/A
962b53d0-4f42-5950-9c28-a23cbbf39052 | button | Upstream IV | Leaked,Tight
b6d2a666-b70b-5c14-8c56-5b5451333a26 | button | Downstream IV | Leaked,Tight
f911a729-426a-5e2b-a2dd-576696a3ddb8 | textbox | Check valve #1 (kPa)
3af2721f-667d-5538-9597-cfb861fb5740 | textbox | Check valve #2 (kPa)
0f96f684-c525-5ef1-ad18-40ee9b2d687b | textbox | Relief valve opened
b3e4f25e-9445-4e9b-9a94-1299c279fe31 | checkpoint | Device installation notes
02288da3-4c8c-5e46-89f8-ad7cbdcc3669 | button | Isolating padlocks installed | Yes,No
4f74ba74-9876-5e11-bd6a-83add62d1462 | button | Installation complies with AS/NZS 3500.1 | Yes,No
f1941052-a7e9-4906-88cc-1f25f0ac5a4e | checkpoint | Test kit
d1395bee-67de-55de-b65c-5e8a15c05a4b | textbox | Test kit serial number
c33b3606-c315-5845-97e0-adf92e4fa687 | date | Date last calibrated
d23d159f-499c-456e-b85d-5bd846e2e7d9 | checkpoint | Authorised testers details
a72531a7-091b-5bd7-b74c-f646638bc4df | textbox | Testers name
48c711fd-c5c8-5cf8-9042-5113fb8db062 | textbox | Registration licence number
494ef4af-5316-5259-a8de-26e54dab12c9 | textbox | Phone number
57466cc8-1d2f-43cb-94a3-4d1857c2a940 | checkpoint-no-value | Licence person
97ddc5e4-63b4-5e97-a6d4-1c91d346314d | note | Full company name - Geschke plumbing
08315b01-c63d-58bc-a8de-fe868eb0be86 | note | Licensed tester name – David Geschke
a833e5dd-1674-53f5-89c3-a6a7de983a54 | note | Licence number -50043
8142ce24-cacf-4225-8c39-75be077df6d7 | checkpoint | I hereby state that the information provided in this form is a true and accurate record. I have tested the above device/s in accordance with AS/NZS 2845.3:2020
3ce47e01-5c70-548a-9cf7-8b2da13d3bbd | note | Note: Failed devices must be repaired and retested within 20 business days as per the Water (Estimation, Supply and Sewerage) Regulation 2014.
b6ba8f6b-da91-5e66-80ce-587f599c12be | textbox | Signature licenced plumber
18c84e08-44c0-59e4-bbb0-4c57d2fab358 | date | Date
49bb3de3-760c-5471-beec-5de0521f239b | textbox | Signature tester
91e41a9c-7806-5ec3-b63b-e0b874c27c9a | date | Date
667a600d-b4fc-434b-b083-657fdf8df72f | checklist | Calorifier Periodic Test Record |  | Calorifier Periodic Test Record
417251b7-0cb3-4e8e-af26-5f3bdf3f30fd | section | Details
3b4f2be4-6d2c-4159-a9e6-12093ce196fc | checkpoint | Details:
4d261301-279f-5a1b-a15e-d0537ddfff4c | textbox | Date:
dba1c1fc-6d93-5043-a9d9-9a12062e21a9 | textbox | Inspector:
cde7680e-612a-54c8-bc92-c714902e5cda | textbox | Location:
3e3966d0-ceab-58d6-af96-ca4e44beaab2 | textbox | Serial Number:
fa42814e-2a58-5250-bd7b-f83c714de0e0 | textbox | Barcode:
13950ba2-779b-5de9-afec-b96c073dff89 | textbox | Year of Manufacturer:
c9018761-d028-4dca-b972-385dfdbc6e1d | checkpoint | Inspect Tank Connections for signs of wear, rust, corrosion - Inlet, Outlet, PTR, Drain, test/gauge point
506eb8f1-d709-57f6-89ba-7b0be67601f0 | textbox | Observations:
d1b949ca-e98e-5951-8a2e-70fa0f1dc1b6 | button | Are cassette/coil supplies fitted with test/drain points? | Yes,No
fdf27224-2f97-5fe5-a1f6-f61daf3880bf | button | Are inlet/outlet valves in good order, can the unit be isolated? | Yes,No
1ae4f71c-32f8-51de-9eb9-3da43543239d | textbox | Confirm operating pressure through cassette (if possible) |  |  |  | kPa
dcaec7d2-6049-5955-9043-d1404b59bff2 | radio | Confirm presence of back pressure through cassette (if possible) | Yes,No,Unable to check
f3b78c01-342b-59d5-a6cb-b64f2cb31fcd | button | Is the lagging in good condition? | Yes,No
570aa150-011a-45ec-860f-730892bc467a | checkpoint-no-value | Observations
fbc91134-60ee-56b8-b7a9-dfd10b03580e | textbox | Observations:
038ce57b-101f-5869-b805-0d1438c56502 | textbox | Other Comments:
5e4547f1-12a8-4850-9f90-92fb18a0b85b | checklist | Day Labour Docket |  | Day Labour Docket
abb0d95a-feed-412a-8607-180a16a32fa6 | checkpoint | Day Docket Details
585164c1-9d78-560e-bb0a-2ce7c50aff2d | textbox | Project Name
2609e487-bfe6-5d82-a401-823a534892e3 | textbox | Job Number
6fb4a55e-e331-56ec-8c4c-9ab3dd38f0f1 | textbox | Site Instruction
b8fb231e-0772-5b7d-ba16-db5ee6ee8ad8 | textbox | Geschke Reference / Subject
d22d6944-777e-54f4-95f5-1353b75c3477 | textbox | Requested by name
2f83be0b-17ac-5735-a3f2-1f6c240e3e2e | textbox | Requested by company
2957b183-d2ca-5da1-8b3d-671059a61f87 | textbox | Brief description - scope, location, other contractor involvement
4b63188f-c786-4304-8ec2-8b811ffbcbc1 | checkpoint | Attached - requester signature
51a7c664-7ba6-4588-a686-503235f3daf0 | checkpoint | Attached - photos before
2258cbe3-caa8-47f4-9988-d9fb9d52dac0 | checkpoint | Attached - photos after
e5d4a5bd-1e33-4e87-982b-b19fe67644f2 | checklist | ITP - Fire Sample Excl. Backfill ACOR Review |  | ITP - Fire Sample Excl. Backfill ACOR Review
4fc9eff0-55a1-4bb0-9e6a-120640c6a73f | checkpoint | 1. Approve specialist subcontractor
7de1495f-ce74-58e2-81e4-db0191283c84 | note | STAGE / FREQUENCY: Prior to awarding subcontract
160b3946-d6fb-534f-9c91-0a890af7ba4f | note | RECORDS: Refer to Overall Project ITP – for Written approval Geschke Quality Management Plans
39eab42b-ad6d-5029-ba19-3e09d55e61bd | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
27cef69f-15d8-5485-ae82-6ce751d7624d | note | INSPECTION / TEST PROC: Document
b1a5cf61-eaea-5033-8eb2-c90e201b5086 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
81d891e8-3ad9-5ea3-92b4-852a5c7897f5 | note | HOLD OR WITNESS POINT: Hold Point
c8dff88e-4ee4-4305-a87f-d51fc942d355 | signoff | hold point
b3e5ccb5-81c0-4dbd-9eb8-33ea96b5244d | checkpoint | 2. Approve Samples
0836f6b7-0c8a-5b45-8d24-c958108af8aa | note | STAGE / FREQUENCY: Prior to ordering materials
14dcc98f-431f-552c-afe6-b272b9f8baa8 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
d1bd734a-3dc6-547c-b9a6-aa899229cca9 | note | ACCEPTANCE CRITERIA: Samples is marked with ‘Approved For Construction’
98a536d0-963a-5c65-9648-abca34a9da42 | note | INSPECTION / TEST PROC: Document and Review
2af43ac8-d246-5da4-af3e-166a00806322 | note | INSPECTOR / APPROVER: Engineer. Geschke
42607788-a5fe-5410-aa52-d7deb3264a9c | note | HOLD OR WITNESS POINT: Witness Point
71aa3b7d-7ffb-4581-8001-d5c71ef05583 | checkpoint | 3. Approve technical details
d885e702-f45b-5e7b-9325-c4be16b12b62 | note | STAGE / FREQUENCY: Prior to ordering equipment
b65a00d8-5178-541a-bc4c-7fb5a33d6306 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
877f00f8-6fa5-5ae2-b594-e85a84b95d2d | note | ACCEPTANCE CRITERIA: Technical Data is marked with ‘Approved For Construction’
bfd58530-e96f-53d2-b79f-19fc7edc0473 | note | INSPECTION / TEST PROC: Document and Review
5784d9fe-c9f1-52f1-96ed-3184e26d5c5e | note | INSPECTOR / APPROVER: Engineer. Geschke
f53bceb2-ca31-5b83-a409-215f1a502369 | note | HOLD OR WITNESS POINT: Witness Point
5179512f-d7ea-4e18-8581-28a32def4270 | checkpoint | 4. Approve shop drawings
a413d5a8-f224-5d5f-9e96-ab5b393f1d45 | note | STAGE / FREQUENCY: Prior to commencement
58717dca-87bb-5b66-abd5-2054ceace3fd | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
eebebbd9-90fa-5b1e-a340-3b15f2e230e6 | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘Approved For Construction’
c54ee8ef-5028-5c44-8879-309a5e84aca0 | note | INSPECTION / TEST PROC: Document and Review
51966de1-71d6-5f9f-becb-440e4ca94006 | note | INSPECTOR / APPROVER: Engineer. Geschke
a3068e18-861c-58b5-a0a9-61341bc910fa | note | HOLD OR WITNESS POINT: Witness Point
c02d639c-f156-46c0-8aac-45ca7e582666 | checkpoint | 5.01. Check set out of excavations
2665e13a-a99e-508c-bf8f-d71a642783df | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
0e450620-477c-5853-8581-3e364e3a0b9d | note | RECORDS: 'Before' Photographs
81905228-62ae-538a-b029-64fe4784235e | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
3b5c57c9-c43f-517e-a13d-2f33e3d570f9 | note | Minimum falls
dd8ebc67-2944-556d-b010-8072e8eec1c9 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
011c505c-8ea1-5ac0-adbf-18c7591fd5c0 | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
64522603-ff9c-5cd7-8af7-4c7e0ed3dde3 | note | INSPECTION / TEST PROC: Visual Inspection and Document
58f3b849-35f3-54f9-b453-3955b667f7af | note | INSPECTOR / APPROVER: Foreman. LLB
5805d0e0-7b59-5984-bc30-1e00c4219c8b | note | HOLD OR WITNESS POINT: Witness Point
87706547-3b3e-4837-98fd-26899ab6dffa | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
95ac44a3-32b4-5314-b736-9c77fa10a7c0 | note | STAGE / FREQUENCY: Each delivery
eed63013-45b5-53e9-8d53-f05c21e13810 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
c8fd1126-67cf-5fda-b9f6-a82724b69336 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
b29f9846-719d-5266-b7e6-b88fd95c9938 | note | Grade or class matches design
a2f974b7-70a5-5776-9e01-e2eb433db8ed | note | Size and thickness matches design
05c4deb3-6568-583d-942b-867cec9c67d5 | note | Supplied items are free of defect
fb05d6ae-250b-5ba2-a740-f4ee786938a8 | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with “SS”.
a3565e50-03fc-5c2e-8d00-b8768e418380 | note | INSPECTION / TEST PROC: Visual Inspection and Document
6130da30-f262-555f-bf18-eecec82dfdcd | note | INSPECTOR / APPROVER: Foreman. Geschke
1fefc1be-204e-5075-8f03-bf78679fbcef | note | HOLD OR WITNESS POINT: Witness Point
510d2402-4920-4c87-acf1-970ca8744a9e | checkpoint | 6. Check deliveries of materials
1e6e0193-b4d6-5f29-9740-a1e73806fe42 | note | STAGE / FREQUENCY: Each delivery
f64ca00a-6265-59f8-af7b-f38c315eecf1 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
faec38c2-46a6-510d-b1b7-8fd3b607b7f4 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
155b108c-98f8-51c4-8b11-f8ab6508c567 | note | Grade or class matches design
d1419075-5a0b-5d44-8ba5-2d9682c2070c | note | Size and thickness matches design
4f1d0c8f-4dae-58ae-b0a9-420ceae255a1 | note | Supplied items are free of defect
90f6f2de-4317-5d42-8f76-7908ba55f8ec | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with “SS”.
bc8f32ac-7b9c-5167-b0ec-45abef3c3772 | note | INSPECTION / TEST PROC: Visual Inspection and Document
7cda8038-aa44-5e75-9fed-183d5df89bef | note | INSPECTOR / APPROVER: Foreman. Geschke
f838943c-e28b-5912-86f9-2b5e07b62206 | note | HOLD OR WITNESS POINT: Witness Point
db316d77-a270-4ad2-b406-a6c08d5fd900 | checkpoint | 7.01. Check below ground pipework - pipe joints - HDPE-HDPE welds, DICL- DICL/Other Material Flange, GMS-GMS Rolled Grove Gasket. If HDPE- HDPE welds:
98fa3a4c-724d-5c0b-8b63-b65bdff6ddbb | tickbox | Standard Bead Profile Test
16abc97c-920b-502d-9e30-0f487d34fc9b | tickbox | Standard Destructive Tensile Test
8285020c-52a3-5d48-8cf0-5e0ac8443fce | tickbox | Standard Ovality Test If DICL- DICL/Other Material Flange
63423429-4e0a-581f-b041-c8bed31e532e | tickbox | Gasketing Record GMS-GMS Rolled Grove Gasket
f1d06b56-ca4a-5367-b72c-ac998dca2347 | tickbox | Gasketing Record
b21b4846-4b92-52c2-9631-9ead5e583f9c | note | STAGE / FREQUENCY: Upon installation but prior to backfilling/ 1 test per 50 pipeline welds approx.1000 l.m
b595184e-f0de-57ab-b20e-0065c60f7033 | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Gasketing Record QA 18 Standard Bead Profile Test Certificate Standard Destructive Tensile Test Certificate Standard Ovality Certificate
98c0b5a5-bbfd-5f5b-aa0e-3be970f6a625 | note | SPECIFICATION / STANDARD: ISO 13953 , ASTM F2620- 20 & ASTM F2928 AS4087 AS1110 & AS 1112 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
a78585bb-981a-5da9-9e5f-39bedf97ad3b | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
8c2ce16a-60db-53d5-8b57-74d859f66eb6 | note | Bead size to be uniform, symmetrical and free of contamination and air.
142698ba-ccd2-54da-9f76-6e6477a5a9ac | note | Bolt tightening to be completed using the correct sequence
eb077647-d525-59a3-b10f-7c641d2ccd0b | note | Final torque on bolts shall not exceed manufacture specification.
8348e531-78a4-501f-8865-19333a7e8c50 | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
9264d18f-dff3-5d37-b1fd-184dc1446a14 | note | INSPECTION / TEST PROC: Document and Review
8695b945-df67-555a-a249-e6944f64f535 | note | INSPECTOR / APPROVER: Engineer. Geschke
ef277171-229d-5f09-bb34-e11ceae03691 | note | HOLD OR WITNESS POINT: Witness Point
5730c3ed-eb08-4f57-b4ee-95a216c0c7a9 | checkpoint | 7.02. Check below ground pipework - pipes and fittings
d75cc0c4-1303-5585-a9e5-f630c06dec24 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
8c9fbb5b-9251-533e-b4c1-bbacbc081db1 | note | RECORDS: 'During' Photographs & As-built Survey
1e5ac1c3-244c-5aa9-a221-c676d55fea3b | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
8a92603c-4586-5d63-90dd-0bb4ae4f3d5c | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
0e4a51b0-cf72-5a64-87ab-e24111414f17 | note | Joints, fittings and connections match design
e33119a6-faa9-5507-b787-b4bad1b7c2c2 | note | Alignment and position are as drawn
b5281bc3-cc11-5987-a12c-452035160bec | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
be61d492-ed7f-5313-949e-7ebe0aedd940 | note | INSPECTOR / APPROVER: Foreman. Geschke
e0caba70-9488-5d28-bbb8-d978531e1137 | note | HOLD OR WITNESS POINT: Hold Point
dc9d9202-e771-4ad5-9107-1c851aadcda4 | signoff | hold point
3f61aaab-cbcc-427e-9c9d-d9e55a5f6563 | checkpoint | 7.03. Check below ground pipework - Hydrostatic pressure testing. Standard Hydrostatic Pressure Test
618205e2-8d59-57b7-a1dd-897fd3e15274 | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling.
30e7f5b1-ca4a-5cd7-9578-f62fa1d9f2a4 | note | RECORDS: Standard Pressure Test Certificate QA.6
7d242dc6-bf18-5ee3-89bb-6e3a1fe1f78b | note | SPECIFICATION / STANDARD: Clause 2.3 of WSA 03 1999 & Clause 18.3 of WSA 03 1999
38cb4ae5-f72f-57aa-aa6b-6e5f90dbbe68 | note | ACCEPTANCE CRITERIA: Pipeline and joints are watertight up to 1,700kPa pressure for two hours
00ab9910-42b3-5405-85e0-f31c0a3e75bf | note | Pipeline is flushed free of all debris
f988d4e3-5a98-597f-8325-e67a537e3b84 | note | Test Passes MRWA Water Supply Pressure Test for PE Pipe
92a45a50-acdb-590f-8d2a-77e3bfebedf9 | note | INSPECTION / TEST PROC: Document and Review
45447483-73a0-54a9-82d5-549161a7826c | note | INSPECTOR / APPROVER: Engineer. Geschke
f9b9603b-7248-5dc7-9c49-d0c283a322d6 | note | HOLD OR WITNESS POINT: Witness Point
c635f57f-7458-43de-93d3-9915c90bc2e3 | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
a8b0dd34-1b10-5ed4-bdb2-dc7f6a7eaffb | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
678d3073-b154-50bb-8ecf-83143b994e44 | note | RECORDS: Photograph
3200ff23-c0d6-5f0f-86fc-af9db6618382 | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
8840b0ea-37be-5a0c-a857-a9edeec6d690 | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
ac67c88e-7711-59d1-bf70-30dab9082a37 | note | Thickness of surrounding aggregate shall meet or exceed specified depth
a6912cd1-6f97-5a26-ad5e-e9f7ed6f166c | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
3a08a059-fb65-50cb-bb2b-3c2693147dbe | note | INSPECTION / TEST PROC: Visual Inspection
d60e5c1b-3358-5e50-bca4-f00db62399cc | note | INSPECTOR / APPROVER: Foreman. Geschke
724fd185-9755-5ba5-8921-90b4702a7850 | note | HOLD OR WITNESS POINT: Witness Point
7c0527bd-c8e3-4f29-8b2c-fd38a011b5c9 | checkpoint | 9. Check Completed Surface - Make Good
011af4e6-799c-5136-881c-9442e624414a | note | STAGE / FREQUENCY: Prior to practical completion
1b45c13c-1371-527c-8816-a43e3bf2a53b | note | RECORDS: 'Upon completion' Photographs
22a8bf79-4486-50f3-9a06-114c23f71ecb | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
a0426b34-528e-585b-abf3-7801710ffe58 | note | INSPECTION / TEST PROC: Visual Inspection and Document
7cb7b782-d3f0-5736-9696-e568fbd4ee22 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
20eafcec-1f10-5575-8bc4-d61a5d7d9379 | note | HOLD OR WITNESS POINT: Hold Point
298d19e1-79d3-4be5-a255-a68670130989 | signoff | hold point
c08fd398-fe5e-4e1e-8794-ebc2bc085b44 | checkpoint | 10. Obtain ‘as built’ documents
d527ac6c-7d2a-53b0-94b7-aa8b0aea05cb | note | STAGE / FREQUENCY: Prior to practical completion
1e52f69b-22e2-5c0e-bf21-e77d6393600f | note | RECORDS: ‘As built’ documents
8635faaf-c1f8-537a-a1b1-f642ae8fa3c6 | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘As-Built’
5f6caa1c-f11f-569a-8261-71fb2b8a7327 | note | INSPECTION / TEST PROC: Document and Review
2ecb18c4-cafb-5ef3-b726-0e8e177ace0b | note | INSPECTOR / APPROVER: Engineer. Geschke
6c3e4348-a972-52fb-9bc2-b9d0cef6e25c | note | HOLD OR WITNESS POINT: Witness Point
5534b54e-22e9-4c37-9f22-604c2e0ebfa8 | checkpoint | 11. Obtain operating and maintenance manuals
c809a988-b86a-508e-a8c1-1d401c13f47f | note | STAGE / FREQUENCY: Prior to practical completion
99d4673a-c923-575a-a4f3-c3927edc07be | note | RECORDS: Manuals
8534cfc1-c465-5277-8510-dcc8821b9bac | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
8bfc08d5-6761-5a83-ab37-3af8bb2fef6d | note | INSPECTION / TEST PROC: Document and Review
d398e188-b639-5a04-8ad5-9fb46f08d4f4 | note | INSPECTOR / APPROVER: Engineer. Geschke
613359f3-d5f6-51c2-b7dd-7e51b9b46be2 | note | HOLD OR WITNESS POINT: Witness Point
7dc3f517-ef8e-4d40-b459-20de1749e7e4 | checkpoint | 12. Obtain guarantees
c447385f-c709-5a09-b509-70b8ad51b3b7 | note | STAGE / FREQUENCY: Prior to practical completion
4448bc97-2df2-5df1-ac96-db82844ad9fe | note | RECORDS: Final commissioning checklist
6f72b667-f082-5c1c-b3bb-1f4137d90f1e | note | INSPECTION / TEST PROC: Document and Review
031ae120-47c3-57ee-b5b5-1772bcc2e16f | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
77909dc2-a864-5eb7-92a4-9fca84ca9ae5 | note | HOLD OR WITNESS POINT: Witness Point
075287be-ff7f-4801-b96f-ba2be369e3dc | checkpoint | 13.01. Check above ground Hydrants - Signal and Flow Test. Standard Flow Test
41d8081a-4f1a-5c33-b435-a7c42f880831 | note | STAGE / FREQUENCY: Upon installation / one test per hydrant
1292d535-dcf2-5aa9-82c6-a653d2939dad | note | RECORDS: Standard Flow T est Certificate QA 6E
f72c66da-092f-570e-a626-5a1d62367b9e | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
cc12bd83-ce71-50b5-adfe-3febf5da1d31 | note | ACCEPTANCE CRITERIA: Hydrant flows up to 30l/s
e36a3d5e-9fe1-589d-95d4-eb481eb2fd66 | note | Hydrant tagged and signed
cfbe5007-17a4-5857-8729-ad7711b08f54 | note | Bollards installed
41d69ae3-d7db-54d3-a219-8b3281dc8992 | note | Signal sent to Building Sub FIP
8e761cf0-0b20-5513-b22b-c2e955616968 | note | INSPECTION / TEST PROC: Visual Inspection and Document
6cb4f9d8-e48b-5731-b21b-d93d369c841c | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
8dd9dca5-6700-54ac-96fe-e92ea5abbcde | note | HOLD OR WITNESS POINT: Hold Point
01801fe0-2caa-4dd9-bb40-36b246074505 | checkpoint | 13.02. Final commissioning & inspection & independent report
8a3503c5-6bd3-56ed-a864-24de1eb169d1 | note | STAGE / FREQUENCY: Prior to practical completion
5c0bb83e-f67e-5719-9f5a-99693ca471da | note | RECORDS: Final commissioning checklist Independent Report
da895d53-72c3-547e-abff-fd18492c80f4 | note | INSPECTION / TEST PROC: Document and Review
87d5f6e2-73cb-5431-8e07-09844a510507 | note | INSPECTOR / APPROVER: Independent Engineer. Geschke
868d8a22-3723-5bc3-8cca-04e965aad211 | note | HOLD OR WITNESS POINT: Witness Point
343de0d1-cbd5-44fb-8cac-777fe847ce15 | checklist | ITP - Gas Sample Excl. Backfill ACOR Review |  | ITP - Gas Sample Excl. Backfill ACOR Review
671d6f10-ce6e-44ef-827a-ae369fefc44e | checkpoint | 1. Approve specialist subcontractor
496b387a-d700-5710-9a90-18a675573ed7 | note | STAGE / FREQUENCY: Prior to awarding subcontract
6f683c03-953a-50fc-a861-18dee32d67b0 | note | RECORDS: Refer to Overall Project ITP – for Written approval Geschke Quality Management Plans
4d9f1429-415d-5eae-aa83-5ef78b3dcac7 | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
594754a0-0c40-5036-9dce-0529fa331f0c | note | INSPECTION / TEST PROC: Document
ccc5146d-8718-5fe9-86a1-ef67d36bcd50 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
fd83cdca-a65a-51bd-9e61-5de24f153f5a | note | HOLD OR WITNESS POINT: Hold Point
7da9883c-cdbf-4a64-8ba4-f86157802d0b | signoff | hold point
7098d316-7ee4-4f3e-9a3c-bc24e08cb18d | checkpoint | 2. Approve Samples
46ed0d11-185c-50dd-9ffc-8f6ca41734f3 | note | STAGE / FREQUENCY: Prior to ordering materials
869f3d75-30fa-5f63-9f4a-8dabc6fecbe8 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
a7c2957c-e8ba-5e4c-82aa-2f9cf22f85a1 | note | ACCEPTANCE CRITERIA: Samples is marked with ‘Approved For Construction’
49f8ee1d-528d-5380-a481-117153bdeb51 | note | INSPECTION / TEST PROC: Document and Review
f855bf97-655e-5586-b442-6eaa099f9d83 | note | INSPECTOR / APPROVER: Engineer. Geschke
857e54fe-56ab-5a4d-a741-6c42e26a7fd1 | note | HOLD OR WITNESS POINT: Witness Point
d22147d0-16df-448f-aecc-a0cfec1f1e42 | checkpoint | 3. Approve technical details
6cc9a826-a805-5124-b0c2-3210573272e3 | note | STAGE / FREQUENCY: Prior to ordering equipment
284bcd5e-02e6-503c-9743-c1ad76e48a2a | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
8a937939-7ad8-5fdc-b251-66bde28c3604 | note | ACCEPTANCE CRITERIA: Technical Data is marked with ‘Approved For Construction’
194df86b-bfef-5928-b6ff-1fe44c850808 | note | INSPECTION / TEST PROC: Document and Review
e2742c67-bc3d-51c1-a67a-d5d73c735dbb | note | INSPECTOR / APPROVER: Engineer. Geschke
a8f91949-8c51-52f7-9083-f8b2df60d1ba | note | HOLD OR WITNESS POINT: Witness Point
d090f8f5-a882-45b6-b750-961a136af914 | checkpoint | 4. Approve shop drawings
2f31e7e4-75d1-50e7-9c66-b9ee990b8fcd | note | STAGE / FREQUENCY: Prior to commencement
340c5532-828d-5a05-9d4c-8363a20371dc | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
c5a56fad-9ce4-5961-a2bc-380acbe002b4 | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘Approved For Construction’
3c5dc06a-a652-595f-acc7-2a5e988ae718 | note | INSPECTION / TEST PROC: Document and Review
7e5af1f2-a3e8-5106-bff1-ea939da4aac6 | note | INSPECTOR / APPROVER: Engineer. Geschke
1781a06d-e091-59eb-a095-44e1bfaca395 | note | HOLD OR WITNESS POINT: Witness Point
33c3412d-6bec-42e3-b8d2-72be010d0993 | checkpoint | 4.01. Approve shop drawings
0568526a-23ad-5b9e-af78-2a3680c38394 | note | STAGE / FREQUENCY: Prior to commencement
dbd7330c-2db1-5bd4-b624-20b970978e16 | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
f0c3b466-5d32-5cca-bd58-ebec8415ca5d | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘Approved For Construction’
36869acc-aa87-59c9-a65c-7918c026579a | note | INSPECTION / TEST PROC: Document and Review
d4be9d57-2b28-589f-9bf6-9d57cb44f8af | note | INSPECTOR / APPROVER: Engineer. Geschke
a64595a8-20d0-5b3b-9321-830f075f58c2 | note | HOLD OR WITNESS POINT: Witness Point
a074154b-4bcd-4cbd-b2db-bbc52baaed32 | checkpoint | 4.02. Approve Method of Work Plan
c75000d4-cc33-5fc2-aa0e-e91cc6c1a866 | note | STAGE / FREQUENCY: Prior to commencement
4b7cc142-ef8a-58ed-8b98-05a2a012ab3e | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.26.10
2470ecea-f8d8-59b5-94b2-0ae657a72201 | note | ACCEPTANCE CRITERIA: Construction staging plan to execute the works
8f1bfc06-f298-58e0-827c-397c21ecb19b | note | Pipeline construction schedule
7a75774d-d8a9-5c5c-bb81-9d34ef6d6837 | note | Nominate temporary supply
e5dec5df-116d-5c79-88ea-7823089ec505 | note | Nominate safe work measures
374c6526-1827-5911-89cb-65f0c1f50254 | note | Nominate notification procedures
06a15cf6-0527-5cc7-ae66-f8adef2fa299 | note | INSPECTION / TEST PROC: Document and Review
171b183a-40e2-5bdd-a44a-d500c80b18ae | note | INSPECTOR / APPROVER: Engineer. Geschke
333b19cf-9845-5853-91dc-b7093277e683 | note | HOLD OR WITNESS POINT: Witness Point
1d19412d-1237-4f33-b897-6bc4a32ce1b0 | checkpoint | 5.01. Check set out of excavations
07f415c2-03e0-5892-8481-5d008f7896b0 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
cf6f6676-adf3-5095-89b0-386921c1bae2 | note | RECORDS: 'Before' Photographs
4a62f733-3e8a-51e4-889c-760ba4194c47 | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
713abc41-8031-5724-9d80-f0f2db48ff2e | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
7861c880-dc1d-56a0-b24b-bd8dfb6982ef | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
9262f319-7cf2-5ae6-941f-3789ed7ffc8c | note | INSPECTION / TEST PROC: Visual Inspection and Document
518a5679-654b-5113-9213-277bbd4efbe8 | note | INSPECTOR / APPROVER: Foreman. LLB
d045c521-cc92-58e1-8583-7864618d3644 | note | HOLD OR WITNESS POINT: Witness Point
8481a04d-237c-4a4e-b9e0-9937a22f2340 | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
a75ef8ec-e18c-5bd0-a38a-619e4e304a00 | note | STAGE / FREQUENCY: Prior to commencement / each TMP
de4d7408-8f22-59e0-8900-83c6b2ff2dae | note | RECORDS: Copy of Consent and Traffic Management Plan
7a4e50cb-093c-52d3-bdc3-83ce40655d1e | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
7b0782c6-dcd5-53e8-beeb-317c332f097b | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
3d68582b-9540-573a-9a3e-fe4fdb6f417c | note | INSPECTION / TEST PROC: Document and Review
f4ce49f8-610f-5931-8a93-42145361e7c6 | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
d2980a11-c7c3-59d7-9e14-d972261fec86 | note | HOLD OR WITNESS POINT: Hold Point
a58fd169-da77-45d7-9e6f-a638d152d575 | signoff | hold point
c670c269-538f-4f0d-89f3-42e35bac0be3 | checkpoint | 6. Check deliveries of materials
bb69ac26-a6a6-5653-afcd-29e27ae95f6c | note | STAGE / FREQUENCY: Each delivery
5652aa40-ba69-5bf1-9113-c2f4fb76bbc4 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
4544fd56-d211-599a-a79c-8784555aaf86 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
1cf852c4-02c3-5aa8-956a-3ed20fcd84c0 | note | Grade or class matches design
aa5a6fc5-b425-5c70-937d-70e2c48fa1aa | note | Size and thickness matches design
af08e233-6419-5590-926f-8d13906d88a6 | note | Supplied items are free of defect
324f0b44-9168-5abe-95ac-f43f6b19002a | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with “SS”.
990a751a-2300-56b6-8f13-2c795ec5850c | note | INSPECTION / TEST PROC: Visual Inspection and Document
eeae8004-7ce3-539c-997e-3141bafd4c13 | note | INSPECTOR / APPROVER: Foreman. Geschke
3ea0a583-ff17-5b03-9a97-e99ab8c1d340 | note | HOLD OR WITNESS POINT: Witness Point
466a40f6-4e96-4ce3-b4f1-5c843e403c13 | checkpoint | 7.01. Check below ground pipework - pipe joints - HDPE-HDPE welds, DICL- DICL/Other Material Flange, GMS-GMS Rolled Grove Gasket. If HDPE- HDPE welds:
d26138b5-2d57-58e7-8b2d-7df6f13e247c | tickbox | Standard Bead Profile Test
a7c64d46-e3c4-5707-b2d1-b049b11cdb13 | tickbox | Standard Destructive Tensile Test
ac8a5336-85ce-5f54-ae15-6e16d61f98f8 | tickbox | Standard Ovality Test If DICL- DICL/Other Material Flange
1c9d3e15-e477-5a36-8557-390562ce7c6f | tickbox | Gasketing Record GMS-GMS Rolled Grove Gasket
5fb87adb-8604-5c3b-a71c-6ac74386d47f | tickbox | Gasketing Record
5ddd593d-d0b9-5266-a354-99e9eac2f6b5 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling/ 1 test per 50 pipeline welds approx.1000 l.m
1766cf85-e559-5448-bf9f-cad17ccb2f0f | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Gasketing Record QA 18 Standard Bead Profile Test Certificate Standard Destructive Tensile Test Certificate Standard Ovality Certificate
160bd11b-0f2b-54f9-a64b-c28f19f3ee78 | note | SPECIFICATION / STANDARD: ISO 13953 , ASTM F2620- 20 & ASTM F2928 AS4087 AS1110 & AS 1112 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
4ac04a2d-bf6b-5d39-914a-3a5e054eb8bd | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
553ba4fd-473e-5369-9993-c6bc6e727f75 | note | Bead size to be uniform, symmetrical and free of contamination and air.
a8eeaa5c-a882-5056-8a08-10592057314f | note | Bolt tightening to be completed using the correct sequence
d2e22e20-cb4c-5314-9d62-bb17dc76e51a | note | Final torque on bolts shall not exceed manufacture specification.
bf7e9ab8-a92d-5487-b9af-699420d89597 | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
04561309-967b-5285-ab05-daa36e4d8710 | note | INSPECTION / TEST PROC: Document and Review
ada2821a-231d-520b-a434-a751fd5edd41 | note | INSPECTOR / APPROVER: Engineer. Geschke
03a43aaf-5f1c-5004-932f-8fc97e65d956 | note | HOLD OR WITNESS POINT: Witness Point
1eb79384-0a93-42d0-93a3-0e480f8d6d25 | checkpoint | 7.02. Check below ground pipework - pipes and fittings
4fe2007b-b329-5289-a13a-364735806d70 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
2fbe44ca-9c36-5e84-bbe8-bb7df11ee47e | note | RECORDS: 'During' Photographs & As-built Survey
43dae345-971f-56b6-9e91-2278fc2b242b | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
4c2cbf75-22c1-5325-8c95-9c96e2181673 | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
a8c356bb-bd24-5a4a-a459-60caa9ed32f6 | note | Joints, fittings and connections match design
a0b9e1cf-82e3-58bc-877f-e52a3dd852e5 | note | Alignment and position are as drawn
0026a383-cfce-5a21-a511-560a1390d1f5 | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
c8b48d8e-ed3c-51e1-9567-2acbd9c983dd | note | INSPECTOR / APPROVER: Foreman. Geschke
8143eddf-123c-55c4-a2b8-6955abd19c8f | note | HOLD OR WITNESS POINT: Hold Point
c995b968-4dd8-4d6c-8682-0375260a72af | signoff | hold point
9c4cc0f7-f5a4-4ba3-8386-492ef179a8d4 | checkpoint | 7.03. Check below ground pipework - Air pressure testing & swabbing. Standard Air Pressure T est
0a64ede4-b5a1-5c6a-b79b-ca600b6fe06d | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling / one test every 750 lm each pipeline
517b1812-ecd4-5ebc-ba42-1dba7cdc0d46 | note | RECORDS: Standard Pressure T est Certificate QA.6
f5800c30-bfe6-542b-b7af-5c6be54e4467 | note | SPECIFICATION / STANDARD: AS 5601 ACOR Consultants Civil Specification Section 6.26.8
633dc20d-f840-5e1f-b6fe-d5b26d5d541d | note | ACCEPTANCE CRITERIA: Pipeline and joints are airtight under the greater of 7 kPa pressure or 1.5 times the working pressure for 5 mins
021ac26e-b066-5f68-a7fa-bfde923f20f3 | note | Pipeline is flushed free of all debris
147080c8-b990-5215-ab6d-dc94c9c5467d | note | INSPECTION / TEST PROC: Document and Review
026d2afd-ab6b-51ac-b19a-ccce85913479 | note | INSPECTOR / APPROVER: Engineer. Geschke
ffa1066e-6e07-54c7-8b8b-b0235050d755 | note | HOLD OR WITNESS POINT: Witness Point
e3c2578d-0607-4656-88e4-a044ca9933e1 | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
6ae219ac-cfb8-581e-9786-6de836e7c042 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
6cf826f0-adb8-5d56-862b-fd96f092f1eb | note | RECORDS: Photograph
14ea34b7-b0c1-52d9-94f3-ced873d06d48 | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
29fd624d-44e2-59e1-a298-d40b63e08842 | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
9e43bb58-b0c2-51bf-8548-1a9f4da0fb21 | note | Thickness of surrounding aggregate shall meet or exceed specified depth
4dced626-cd69-5d44-bc63-56c37a2092d5 | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
c7886db4-2c53-51e1-97f5-bf26839ad4e2 | note | INSPECTION / TEST PROC: Visual Inspection
e951d3d8-3de2-5bc0-99c2-a369387351c2 | note | INSPECTOR / APPROVER: Foreman. Geschke
aeb40601-9a00-553a-a7b6-7db29a86ff1b | note | HOLD OR WITNESS POINT: Witness Point
88dab91b-ae14-4a3f-867f-c5bb0a90917c | checkpoint | 9. Check Completed Surface - Make Good
0324c152-2a24-5c54-9503-f4e12ab801ac | note | STAGE / FREQUENCY: Prior to practical completion
e2c1c1fb-1db8-59cb-bf73-89b9a44ace9e | note | RECORDS: 'Upon completion' Photographs
70c252bd-b075-5f80-b847-48765b0418d1 | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
ecc707b1-f81d-5e3e-9372-949b944c9704 | note | INSPECTION / TEST PROC: Visual Inspection and Document
84932a19-b440-5d95-8bbf-24d92cac004a | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
f761dcad-7e10-540f-b969-3116768a9e3f | note | HOLD OR WITNESS POINT: Hold Point
030374e8-b6ab-456e-a4c6-dd6abdd8fc44 | signoff | hold point
8768ad2b-e4ad-4fa1-8254-a36ad43b4fab | checkpoint | 10. Obtain ‘as built’ documents
e2fff48d-3b74-5ece-ade5-82a6d582e48c | note | STAGE / FREQUENCY: Prior to practical completion
a5703fcc-d7b2-5021-a773-20001876953b | note | RECORDS: ‘As built’ documents
57724346-2be0-5f87-b5e5-6363eab1d605 | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘As-Built’
3900035e-7cda-5272-9764-6a1540bc369b | note | INSPECTION / TEST PROC: Document and Review
0409c82a-e520-505a-9593-a19cd47c7b79 | note | INSPECTOR / APPROVER: Engineer. Geschke
0e7d7720-e3e4-5c4e-b0d5-ec8c45148868 | note | HOLD OR WITNESS POINT: Witness Point
b5d8741d-44da-4964-b7cf-ed0b746c16a7 | checkpoint | 11. Obtain Regulatory Authorities’ certificates and approvals
72ad07ef-bef9-529f-8dc0-d93cefec321a | note | STAGE / FREQUENCY: Prior to practical completion
27a81666-2360-5035-8b79-74563dfd48e1 | note | RECORDS: Certificates; Written approvals
4991094e-563e-5b56-9b48-417493cbef98 | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
feb211b5-d763-5082-b31a-c318a59dea29 | note | INSPECTION / TEST PROC: Document and Review
5bbca821-96b3-5923-bd05-f15a47702a7f | note | INSPECTOR / APPROVER: Independent Authority. LLB
7758c069-cd33-5672-8a9e-250a84030a7b | note | HOLD OR WITNESS POINT: Hold Point
ad6277ba-38fc-4396-ba1d-367ccc9c4e75 | signoff | hold point
da42e49e-adeb-472f-bc90-e3a85fff7864 | checkpoint | 12. Obtain operating and maintenance manuals
84e329ce-bfa2-5a25-9f14-06ebfc9bd7fe | note | STAGE / FREQUENCY: Prior to practical completion
24d46654-f8ac-5867-941f-6529d821ebc0 | note | RECORDS: Manuals
192c5ab0-6280-5f82-aad5-e1183b79fc1f | note | INSPECTION / TEST PROC: Document and Review
a4a503b2-f7ae-59bd-a48b-a6fd5adca975 | note | INSPECTOR / APPROVER: Engineer. Geschke
4d3ca1c0-9e2c-5e05-b107-765a591ac85d | note | HOLD OR WITNESS POINT: Witness Point
a0e8403a-9b44-47d7-8dc0-4a4c3cab6a4d | checkpoint | 13. Obtain guarantees
e7766b11-9d1b-5fb7-b564-e9bca7f0903d | note | STAGE / FREQUENCY: Prior to practical completion
90cb13c3-d3be-5203-8ef6-eaaa59cc1924 | note | RECORDS: Final commissioning checklist
4d2322a5-f7df-517e-8197-b93065d74195 | note | INSPECTION / TEST PROC: Document and Review
a0acb72a-1a9c-5edc-bdc1-7bbe3190b4f2 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
d101bad5-7603-5d74-8021-b26b3ed80cd5 | note | HOLD OR WITNESS POINT: Witness Point
e294b12c-a328-4e29-a207-1c286b8a211f | checkpoint | 14. Final commissioning & inspection
b0611274-f633-51e2-aff1-154e97720515 | note | STAGE / FREQUENCY: Prior to practical completion
6a240028-ef89-5d97-b9cb-25b219a0d2a2 | note | RECORDS: Final commissioning checklist
013656f9-0795-5223-ac64-8b66c62a3473 | note | INSPECTION / TEST PROC: Document and Review
be422495-29ee-5a60-9590-2e0e8074d19b | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
934a9b3e-74b0-5809-8d29-5a1e43009b47 | note | HOLD OR WITNESS POINT: Witness Point
777ca1a8-0744-486b-9efe-8f958f03e3a9 | checklist | ITP - Sewer Rising Main Sample Excl. Backfill ACOR Review |  | ITP - Sewer Rising Main Sample Excl. Backfill ACOR Review
4772c32d-a7f3-4559-bce7-f1fb1661f668 | checkpoint | 1. Approve specialist subcontractor
dcc703be-23a5-5e3c-9cd0-2d9b55e7e9a1 | note | STAGE / FREQUENCY: Prior to awarding subcontract
9cf2e9ea-98b0-5ece-bafd-9a9a61e7a3d0 | note | RECORDS: Refer to Overall Project ITP – for Written approval Geschke Quality Management Plans
64e6f1a4-b630-5433-b833-0a49f1064112 | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
d32c6e32-0562-5a16-ae71-8258744716f7 | note | INSPECTION / TEST PROC: Document
84d2045b-5f32-5eff-999d-1a109d5b0787 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
7f7ffe1c-3bdb-56bd-8f83-d488f3151f05 | note | HOLD OR WITNESS POINT: Hold Point
ea24958c-f3c3-49cd-b125-de46f7bfe12d | signoff | hold point
1dbfa2a1-dfaa-4b43-8f84-7b8613959e56 | checkpoint | 2. Approve Samples
5ac2a19d-a2a7-57fe-aae3-1be2bb44386e | note | STAGE / FREQUENCY: Prior to ordering materials
d1e4f190-19ba-549d-9cba-6305a3a8948b | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
cb12d97b-b9ce-51df-bac9-8a3f5e1bf6ea | note | ACCEPTANCE CRITERIA: Samples is marked with ‘Approved For Construction’
16110012-0d2f-56aa-9118-dcbb7b772ca9 | note | INSPECTION / TEST PROC: Document and Review
cf2f36f4-e6d5-542f-9281-86fe98e8f7b6 | note | INSPECTOR / APPROVER: Engineer. Geschke
cc24cec7-7fba-53db-b7c4-35b6a9f26997 | note | HOLD OR WITNESS POINT: Witness Point
6d67f65d-6144-4ee4-a7d8-bce9212a4ec7 | checkpoint | 3. Approve technical details
271a06bc-555f-52a6-8b24-68b9dd250695 | note | STAGE / FREQUENCY: Prior to ordering equipment
835cef2c-decf-5a0c-a858-1457360d12b7 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
1ae73058-d214-5d4a-8a3a-dc61974a5e2c | note | ACCEPTANCE CRITERIA: Technical Data is marked with ‘Approved For Construction’
6292f5a9-d6e7-594a-aad5-652aadea2cd5 | note | INSPECTION / TEST PROC: Document and Review
09fda7ea-c5e4-567e-8f66-20405ac1a0e2 | note | INSPECTOR / APPROVER: Engineer. Geschke
b998a165-384d-5a2c-8164-3ec9dd9ff169 | note | HOLD OR WITNESS POINT: Witness Point
06a8ebbf-244c-46c3-be3a-2dfda2152acc | checkpoint | 4. Approve shop drawings
d897eb5f-1ee5-57f0-b19d-db8f3b8ff999 | note | STAGE / FREQUENCY: Prior to commencement
4200d5ff-ca69-5588-9be3-b00f2535e55f | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
f2158d95-f86e-5fda-b89c-950bafd3fcbb | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘Approved For Construction’
302de6e8-ceae-5253-b025-99b218aa3c54 | note | INSPECTION / TEST PROC: Document and Review
4def3052-d5b0-5645-929e-092e913426ca | note | INSPECTOR / APPROVER: Engineer. Geschke
79d90f5e-65d3-565e-8b7e-6fbaf3c2c4de | note | HOLD OR WITNESS POINT: Witness Point
fc6b9763-c728-4c1a-ad1f-d62094596318 | checkpoint | 5.01. Check set out of excavations
a1f0d873-4d2a-5e34-b0b1-a606975d325b | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
a42b2a99-45cd-570e-8991-f22be8457bbf | note | RECORDS: 'Before' Photographs
aa9dd44c-b08e-563a-a435-85ec06f1e0ff | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
3c82231d-dbdd-5087-94c1-ab6ceb2ceb5d | note | Minimum falls
f4faa753-414f-5335-87de-99c6821cc18a | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
59251294-6f3b-5ea3-ad96-96e4197b1767 | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
4e28d8cb-4d34-552f-b3cc-8b2e96360108 | note | INSPECTION / TEST PROC: Visual Inspection and Document
10edb87a-4def-589e-b50c-fd4b6b7dc399 | note | INSPECTOR / APPROVER: Foreman. LLB
7c9ea1f5-d312-5295-8061-fcb3f3a661cf | note | HOLD OR WITNESS POINT: Witness Point
06e7425a-e7ff-40ce-8fc8-96b03dce430b | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
c9806893-5c21-5692-bc3d-1b15f8f08cd0 | note | STAGE / FREQUENCY: Prior to commencement / each TMP
616c7f20-fc90-59c0-aa30-0e302fd1b1e7 | note | RECORDS: Copy of Consent and Traffic Management Plan
2264114b-39c4-56d4-8c29-c2137eba059b | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
ffd9820a-5076-5337-8675-b9d4961afc60 | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
caa53df0-2c6f-5d0c-b38e-bde269171f79 | note | INSPECTION / TEST PROC: Document and Review
38956498-eadf-5785-9654-b6d17ce93b77 | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
082f7225-b4b9-50b2-bacb-d4e0538d61a8 | note | HOLD OR WITNESS POINT: Hold Point
b1393a66-aeb7-41a2-8062-a30c97e600f5 | signoff | hold point
1eb945e0-d077-477f-b61d-e57e2cbafcba | checkpoint | 6. Check deliveries of materials
ad797b21-cf81-5d6d-9234-4c9da7318891 | note | STAGE / FREQUENCY: Each delivery
2d175e00-c498-5094-90f2-678964ead77e | note | RECORDS: Delivery dockets name, signed and dated by Geschke
dd9f55b6-0f2e-5f0d-9197-6080049d7298 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
ff09e6ae-50bf-5f86-b912-66f7cbbd5324 | note | Grade or class matches design
660cdfea-59f0-56d2-bbd6-cffcf82a7e64 | note | Size and thickness matches design
1452bd7e-aa08-55cb-a94e-3bc8e97200f5 | note | Supplied items are free of defect
3fa4cae7-6a9b-511c-87d8-fadca399b8df | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with “SS”.
c43efb4d-0f0d-54bb-89ce-4c7bdb7e4126 | note | INSPECTION / TEST PROC: Visual Inspection and Document
a5ae04d3-f226-5976-a1cf-c438108dd1eb | note | INSPECTOR / APPROVER: Foreman. Geschke
578f75e0-bdd5-563d-99db-c60e622d4d67 | note | HOLD OR WITNESS POINT: Witness Point
fc5872c6-970c-4980-ba82-bdb7c9b050a4 | checkpoint | 7.01. Check below ground pipework - pipe welds. Standard Bead Profile Test Standard Destructive Tensile Test Standard Ovality Test
4412cdbe-3060-56fc-91d7-6c678707cf35 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling 1 test per 50 pipeline welds approx.1000 l.m
2dd51a4d-146b-5014-83d6-aaea8020f913 | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Standard Ovality Certificate Standard Bead Profile T est Certificate Standard Destructive Tensile Test Certificate
38f9b064-8405-57d1-ae86-5661882c8a17 | note | SPECIFICATION / STANDARD: ISO 13953 ASTM F2620- 20 ASTM F2928 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
b8d0fa14-95be-5129-a8da-0af4475b79b1 | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
b6d22c27-6986-568f-8465-4f4f44dfdc4b | note | Bead size to be uniform, symmetrical and free of contamination and air.
d6dd41d1-6d74-5bc9-b30d-0b26d45fcaa4 | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
058277b0-486c-514c-87a4-52760423cfb4 | note | INSPECTION / TEST PROC: Document and Review
ff7c73d0-56cc-5bc6-b01d-d7325ab293e6 | note | INSPECTOR / APPROVER: Engineer. Geschke
706502a4-a264-5e81-8b57-4bddbcf79a3e | note | HOLD OR WITNESS POINT: Witness Point
536a4f7f-5d1c-4ae2-8146-2931894b12fb | checkpoint | 7.02. Check below ground pipework - pipes and fittings
e9279361-43bf-5fa0-aa6d-0a70262eeb3c | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
6fa13aec-ee40-55ae-a2a1-d592ed4df5c9 | note | RECORDS: 'During' Photographs & As-built Survey
6dcc5d8f-5024-5017-b8d6-60e0b0d273d6 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
eb8cce39-b887-560e-8128-87717c03d298 | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
d00f8223-db66-5c96-b5e0-64c9280e1229 | note | Joints, fittings and connections match design
f27267e8-5f41-59c8-b11d-d5483dd43c2a | note | Alignment and position are as drawn
519e5a5f-dc5c-5cc9-94df-f2fa54f03b6a | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
6b913bdc-bdf4-5211-bdae-2d88c2ea39b4 | note | INSPECTOR / APPROVER: Foreman. Geschke
0fe9534c-f2b6-5f55-80f9-48434b008038 | note | HOLD OR WITNESS POINT: Hold Point
3319829a-b740-485c-a0bf-253ec72c18fd | signoff | hold point
7de54b76-0482-43fc-97ae-ed5d7acd8549 | checkpoint | 7.03. Check below ground pipework - Hydrostatic pressure testing. Standard Hydrostatic Pressure Test
8cf7c05a-d0b2-5506-aa06-f93b904bd008 | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling
20ad7b08-9d1d-5a23-a262-255cf2339973 | note | RECORDS: Standard Pressure T est Certificate QA.6
5cdc53c1-f0d4-5c02-96f8-6ca66601a488 | note | ACCEPTANCE CRITERIA: Pipeline and joints are watertight up to 1,500kPa pressure for two hours
2b11b2ef-d3ab-5ea0-a0e2-9e0a1d283173 | note | Pipeline is flushed free of all debris
d73581c6-abaf-5213-a61b-6ce7b6c9591b | note | Test Passes MRWA Water Supply Pressure Test for PE Pipe
b67b797e-7129-5057-9f49-da5aa766c993 | note | INSPECTION / TEST PROC: Document and Review
2dd557b2-d1d4-5079-abb7-564c6048a96f | note | INSPECTOR / APPROVER: Engineer. Geschke
33c256f0-49fe-536c-a928-50a273d94feb | note | HOLD OR WITNESS POINT: Witness Point
f7de9ebc-5210-4252-b272-5216c90e1081 | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
bb0f3eaf-d4aa-5757-a4b4-ffd1b023071e | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
843909e3-c5a7-584c-ae34-dae05a6882da | note | RECORDS: Photograph
4fc4d14a-23b8-58e3-9775-bfcf5f26aec3 | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
36af4650-046a-5a3d-8a0c-01d8acd442e8 | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
ebc0fded-f87a-5337-9dc1-5c84b4e7b681 | note | Thickness of surrounding aggregate shall meet or exceed specified depth
607efb65-a578-5a2b-9d25-74e7512dac65 | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
9fc9a78c-a49e-58bc-bc3b-2e6ad459bf67 | note | INSPECTION / TEST PROC: Visual Inspection
b4a6bc55-648c-5f98-94a2-ce16857d425d | note | INSPECTOR / APPROVER: Foreman. Geschke
863e471f-65c4-58ed-8b0c-dd98a6e46601 | note | HOLD OR WITNESS POINT: Witness Point
931b5016-b437-45dd-92bc-0fcd904ab6f1 | checkpoint | 9. Check Completed Surface - Make Good
833dee9c-9b12-57dd-a4db-819b300a4fd7 | note | STAGE / FREQUENCY: Prior to practical completion
a3449adc-d430-5780-91c2-7abada92f2b1 | note | RECORDS: 'Upon completion' Photographs
ab35138d-3507-514f-9a06-2f87b7bd9af6 | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
71329f47-b9dc-5c2d-b961-cdca57a5a4a1 | note | INSPECTION / TEST PROC: Visual Inspection and Document
3e8e808d-88ad-5efe-a987-54d7efde6c2f | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
5f38c2dd-c909-5673-8560-3dbff2674b5b | note | HOLD OR WITNESS POINT: Hold Point
54dd546b-283a-4dfb-9736-cd98cc68a63c | signoff | hold point
d6033f90-cff7-408e-a9cb-61f77be51f18 | checkpoint | 10. Obtain ‘as built’ documents
2267ab1d-d8c6-56da-b18d-1c3b4b4e6efc | note | STAGE / FREQUENCY: Prior to practical completion
de2444fd-1ca9-5c1b-a735-fcc55622d855 | note | RECORDS: ‘As built’ documents
c3223fae-f245-5554-8389-681786fb1efe | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘As-Built’
26d0c427-ba91-58c4-9c43-8e34c67bfc57 | note | INSPECTION / TEST PROC: Document and Review
92a24ecf-7670-5ff8-b276-f6c623e67a20 | note | INSPECTOR / APPROVER: Engineer. Geschke
c782bd3e-cb8c-5117-a163-92d2a1a1253a | note | HOLD OR WITNESS POINT: Witness Point
e77544cb-5dfb-452e-a8ec-5991674c9d7d | checkpoint | 11. Obtain Regulatory Authorities’ certificates and approvals
ad599002-9f69-581b-8d3c-08577afee67c | note | STAGE / FREQUENCY: Prior to practical completion
69bd40b3-8f15-520e-b90c-f31d90dd0ab4 | note | RECORDS: Certificates; Written approvals
c66112c4-bdcf-505f-9aa9-4273ffc33fc9 | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
b5652b38-ad00-52ad-b40d-bc5a89dcb359 | note | INSPECTION / TEST PROC: Document and Review
1d86a882-3cf9-5a28-ab5c-e277cd22589d | note | INSPECTOR / APPROVER: Independent Authority. LLB
cd32a808-e1d2-5b2e-966b-77a42a0d486c | note | HOLD OR WITNESS POINT: Hold Point
6f1a865d-3f89-49c4-92ee-bff2590a58db | signoff | hold point
cc5cd6fb-da0c-4b54-99c9-f7ec5f64a6c5 | checkpoint | 12. Obtain operating and maintenance manuals
dce51794-101a-5a3d-ba93-76fbd14c6feb | note | STAGE / FREQUENCY: Prior to practical completion
eba4f0bc-0d43-5214-a83b-f82965466d8d | note | RECORDS: Manuals
fa18fd84-0406-5e10-9935-96d7073f7ec4 | note | INSPECTION / TEST PROC: Document and Review
1a2fb4b4-90f2-5c3f-85f9-c6efaf7e87b9 | note | INSPECTOR / APPROVER: Engineer. Geschke
ad22b398-cc5f-532f-a0a4-a2a0edfce5a2 | note | HOLD OR WITNESS POINT: Witness Point
15d7dfc3-a282-42de-9fd6-2f07e0aeb7c5 | checkpoint | 13. Obtain guarantees
a357a619-e154-5e32-a85f-e768074b5d46 | note | STAGE / FREQUENCY: Prior to practical completion
25473ad8-bca6-5048-9b6e-ccbdc8134e13 | note | RECORDS: Final commissioning checklist
cab77e06-4136-5aec-aaea-fd0f6995c612 | note | INSPECTION / TEST PROC: Document and Review
a65e7c70-c517-5ce1-8f98-4f91f5012167 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
3cafd75f-5e2b-5617-aa5c-fb63ca5ed773 | note | HOLD OR WITNESS POINT: Witness Point
b02974a1-e9ba-4293-8a73-e789b042fdb0 | checkpoint | 14. Final commissioning & inspection
7bd21a50-ecac-5955-9239-4b970c2829f2 | note | STAGE / FREQUENCY: Prior to practical completion
bc34cd23-2ecb-5dac-9b1a-4a8b85aeea4c | note | RECORDS: Final commissioning checklist
0fd3e5f4-14a3-51fc-8f42-9c683b90bfbf | note | INSPECTION / TEST PROC: Document and Review
bae8e390-bb24-5d3a-990f-464d9ffa47c0 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
53ab3bb4-4be3-5ad1-a8b8-aee94243974a | note | HOLD OR WITNESS POINT: Witness Point
24906e38-1b9a-4002-9864-48bffb87fac0 | checklist | ITP - Storm Water Sample Excl. Backfill |  | ITP - Storm Water Sample Excl. Backfill
514d35dd-d824-445d-9656-72faf7bb307f | checkpoint | 1. Approve specialist subcontractor
68438da3-6b95-591e-941f-3343c67ba54d | note | STAGE / FREQUENCY: Prior to awarding subcontract
3cb3974e-5b2d-5c2c-92af-15cd18da9afa | note | RECORDS: Refer to Overall Project ITP – for Written approval Geschke Quality Management Plans
69454e7e-3bbf-5fb1-864f-0b1e10c0e825 | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
c4c58d1c-43ac-5e39-8abc-71c7ef41547c | note | INSPECTION / TEST PROC: Document
f2aa319c-921b-5290-bc52-dc20de17b8e4 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
dedab546-cc60-5e59-830a-26eaee3150b9 | note | HOLD OR WITNESS POINT: Hold Point
c15b0214-b3ff-41ec-8746-6e7458278bef | signoff | hold point
dd8cadb4-b08e-479d-aacd-e27d844419e3 | checkpoint | 2. Approve Samples
805a5e4b-ed13-56a6-88a2-9265f2321a52 | note | STAGE / FREQUENCY: Prior to ordering materials
c804e365-5634-5c1a-8780-1beca7f3c8bc | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
752a60df-03a0-53b0-807e-e2d7a26a2c68 | note | ACCEPTANCE CRITERIA: Samples is marked with ‘Approved For Construction’
e63a3de3-0826-5854-bd7e-85a7e11e670e | note | INSPECTION / TEST PROC: Document and Review
f906e0ae-6b81-525c-a16d-90575622615e | note | INSPECTOR / APPROVER: Engineer. Geschke
c650fadb-39b0-5650-9f16-1d79c7a44486 | note | HOLD OR WITNESS POINT: Witness Point
03af39cc-b1a3-4e84-b024-f073da3667ae | checkpoint | 3. Approve technical details
beff59cb-0044-5a1d-bdd1-4ac0ef43850a | note | STAGE / FREQUENCY: Prior to ordering equipment
dbc2b02d-725d-546e-b1a9-36a2e1ab424d | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
2d12a695-cb85-5d15-9cf1-e62e497bfd5a | note | ACCEPTANCE CRITERIA: Technical Data is marked with ‘Approved For Construction’
332035d1-7e73-5a75-aafd-cd5ba26a67d6 | note | INSPECTION / TEST PROC: Document and Review
5524a9c9-249d-50ad-a2cf-a6bafb856b9d | note | INSPECTOR / APPROVER: Engineer. Geschke
14d7efe4-fa50-5bbe-8aa3-c9ff09d80946 | note | HOLD OR WITNESS POINT: Witness Point
e70b287a-58d8-4fe7-a557-df93179b0055 | checkpoint | 4. Approve shop drawings
d0cbd97b-9fa3-5092-839e-df1388aef239 | note | STAGE / FREQUENCY: Prior to commencement
21857f0f-4025-5ec3-b452-91c0a5047211 | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
12959208-98cc-57bb-8bff-e2010ccc0c95 | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘Approved For Construction’
aca300f4-287f-5223-80da-64b9695179f8 | note | INSPECTION / TEST PROC: Document and Review
0addb466-7460-5166-be8a-928d3457b747 | note | INSPECTOR / APPROVER: Engineer. Geschke
6a23b860-134f-5cbf-bf4f-29cad1a9bfcf | note | HOLD OR WITNESS POINT: Witness Point
c29a9d2b-51a1-4376-90f8-6228190d05c6 | checkpoint | 5.01 . Check set out. By Delta
f4641516-40ba-576b-ad33-6999195f12a9 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
066a155e-6cc6-52bf-9cb4-e4149bb76c71 | note | ACCEPTANCE CRITERIA: Set-out of pits is marked with pegs and alignment matches design layout
a7c11485-6846-56ce-8eb7-fd6015702fe5 | note | Height control point is marked within 40m of works area.
70abd909-cc71-56d8-9b3f-6869693ce010 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
a8af62b7-7803-5100-b81e-78572263e611 | note | INSPECTION / TEST PROC: Visual Inspection and Document
281dbf4a-79a4-53f9-8929-e5a4cfadd8a8 | note | INSPECTOR / APPROVER: Foreman. Delta
edd83278-d04c-5cb7-98d1-47db7c9fb9a2 | note | HOLD OR WITNESS POINT: Witness Point
2a1c5e77-5ef7-4904-8cc6-0002e0226785 | checkpoint | 5.02. Check excavations
75fe58ef-afce-5896-ab8d-77973a957b80 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
afa6c56d-d205-5b72-b6ec-f8e90e7e0447 | note | RECORDS: 'Before' Photographs
4eed7a45-96a5-5918-8c10-24ca57ccbab4 | note | ACCEPTANCE CRITERIA: Alignment commences at outlet and proceeds upstream
1aad287f-95cf-50c3-ad04-3a215cf92dc1 | note | Minimum falls
8deb2069-4e1e-5e69-8520-054fc3af12e7 | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
63f22dfe-2438-5f2e-a64f-3d5f5bed21a4 | note | INSPECTION / TEST PROC: Visual Inspection and Document
d09d809f-58ff-5ea7-a5ff-df84d7bd389c | note | INSPECTOR / APPROVER: Foreman. LLB
a2cab3d5-b3d0-55b4-b59d-718b6b0f0bab | note | HOLD OR WITNESS POINT: Witness Point
b476af5e-7318-4615-a2d6-ef7eeed9213a | checkpoint | 5.03. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
8019f7e0-b896-5578-bceb-cc644789d3b4 | note | STAGE / FREQUENCY: Prior to commencement / each TMP
fd25178b-ae49-5ac0-9627-51ee74828a98 | note | RECORDS: Copy of Consent and Traffic Management Plan
7c5ffa43-a707-5c50-9d3a-d62087ad625e | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
dbbf5379-07a8-5987-8f71-63356085985c | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
c6f316a6-5b46-59ba-9ce9-7abc1c84c263 | note | INSPECTION / TEST PROC: Document and Review
9e2c5994-9a8e-55c2-a7ce-79b3cdf556cb | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
95293938-b075-5a03-9b5e-f532b780fa30 | note | HOLD OR WITNESS POINT: Hold Point
eef8b553-1853-48fd-b2ef-b700400d15d9 | signoff | hold point
a55e2729-9b82-46e6-b776-f0e6672aed08 | checkpoint | 6. Check deliveries of materials
d1408abf-04e2-5455-808e-4482645f5fe6 | note | STAGE / FREQUENCY: Each delivery
8ad453f9-2c54-50ab-9428-bf5176f60c79 | note | RECORDS: Delivery dockets name, signed and dated by Geschke
13733a5d-644f-5c64-95bf-f802ebe0ee19 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
df3f9580-476f-5788-8610-0a79e1fb1f11 | note | Grade or class matches design
dd052f1b-65b6-54ec-9934-e3e0790ed1a2 | note | Size and thickness matches design
6c53c7af-1b61-5ad1-8a52-853bbe138e9f | note | Supplied items are free of defect
0b4838ca-0531-5721-bdd5-596d7b4025b5 | note | Marking, packaging and preservation is fit for storage / construction
5e0a2b03-c3c0-5445-b149-5d656582adc6 | note | INSPECTION / TEST PROC: Visual Inspection and Document
01fc1441-3f39-5abc-a6a1-648ca901a4d9 | note | INSPECTOR / APPROVER: Foreman. Geschke
3ec62dda-2eaf-5381-81a0-a85c42634661 | note | HOLD OR WITNESS POINT: Witness Point
590e9438-631b-4648-8d4f-11b161e010e3 | checkpoint | 7.01. Check below ground pipework - rubber ring joints
5993cc7b-6ce9-52eb-b762-60de941daa7f | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / one test each grid
8cf6d5d5-dcb7-5c36-b32a-7d8aafafb258 | note | ACCEPTANCE CRITERIA: Joints are secure and flexible
feb84c71-17e4-598a-a28c-3f8721aebd32 | note | INSPECTION / TEST PROC: Visual Inspection
81fda2d8-d6e1-588a-85e1-74bc1c7b5c95 | note | INSPECTOR / APPROVER: Foreman. Geschke
b55d5bfa-8691-54c4-a4e3-92ab37fbb65d | note | HOLD OR WITNESS POINT: Witness Point
44a4ec5d-9960-44b2-ac7c-c10df8969d82 | checkpoint | 7.02. Check below ground pipework - pipes and fittings. By Delta
ae9e68f3-b245-5646-834c-14a960818170 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / once per grid
b094bf71-b437-533d-87f3-5f1568d5bdd5 | note | RECORDS: 'During' Photographs by Delta & As- built Survey by Delta
4a61b084-01e0-5c51-8672-8bf1bba09971 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
06261f41-1453-5b9b-aa0b-866ee0369065 | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
8619032f-b0fc-5166-9ff4-c71758ab058a | note | Joints, fittings and connections match design
1a8c180e-ef2f-5bee-8cce-173f4d05a361 | note | Alignment and position are as drawn
a0d3e03a-be8a-5302-8227-ffd8273fadb9 | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
1471a1f4-c046-566f-945d-cab2ce679516 | note | INSPECTOR / APPROVER: Foreman. Delta
842138b6-b448-5501-b6d6-90b374aa3950 | note | HOLD OR WITNESS POINT: Hold Point
600838a0-9c58-435b-8a85-a320921aa670 | signoff | Hold Point
28919ae3-e90c-4d6a-8ca7-a8ef1b6b172c | checkpoint | 7.03. Check below ground pipework - bedding, haunching, surrounding and encasing
1e5bebe5-540f-528c-87c3-539a1c075b04 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
5341ab65-3ff1-5a36-81e0-141857a629ee | note | RECORDS: Photograph
4c3c0e3c-f438-5230-ba6f-1b64a4117b3c | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
a0839974-9739-5a90-9937-20eadb9a0679 | note | ACCEPTANCE CRITERIA: Constructed using approved material
1a500c76-22f9-544c-8c27-8bd7496c090c | note | Thickness of surrounding aggregate shall meet or exceed specified depth
8d83392f-a013-59d5-a019-250947e035ff | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
f2f40603-761b-56b9-be4f-ec450569bda2 | note | INSPECTION / TEST PROC: Visual Inspection
07787061-cbb9-5522-99ef-37864d4eed8d | note | INSPECTOR / APPROVER: Foreman. Geschke
3cf05c74-049f-5e16-903e-31b7887a2bcd | note | HOLD OR WITNESS POINT: Witness Point
0ba3cf25-056e-462d-b35e-21d722f5e228 | checkpoint | 9. Check Finished Surface - Make Good. By Delta
d4f18f06-d18b-515a-afe8-1c6a39fceb58 | note | STAGE / FREQUENCY: Prior to practical completion
35e9ec55-1937-5af7-872d-e530d4f1e54f | note | RECORDS: 'Upon completion' Photographs by Delta
8a025264-9721-5341-a5d0-6bcc57703906 | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.18.5.12
69f51369-a310-5489-94d8-edb842106dc1 | note | ACCEPTANCE CRITERIA: If works are in existing roadways, paving or asphalt has been replaced.
7999ece7-a32b-5756-8fdd-952954b52c84 | note | Finished surface is free of obstruction/debris and matches finis
92f96a56-c409-5e66-8b49-60b6a1a9a7cf | note | INSPECTION / TEST PROC: Visual Inspection and Document
4cb51087-07a8-5609-9ddd-cfc7e3953a22 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Delta
8a54c217-e7d3-5123-9697-7feb61916380 | note | HOLD OR WITNESS POINT: Hold Point
edc049ca-77c0-4e2b-acde-a1de402cd733 | signoff | hold point
9d1e8bc2-8ce2-475f-afa3-ee59556dbafd | checkpoint | 10. Obtain ‘as built’ documents. By Delta
d9815776-bfc5-56d8-b704-b57a564fb24a | note | STAGE / FREQUENCY: Prior to practical completion
87f35993-00fb-56a1-a408-b82fdc3b9980 | note | RECORDS: ‘As built’ documents by Delta
61a44ab9-98b2-5f0f-ab07-fa4e5263eaec | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘As-Built’
2db8a05d-7844-5af7-bf39-1af443fc5ed1 | note | INSPECTION / TEST PROC: Document and Review
44debc30-4449-5179-8613-ebae4627552b | note | INSPECTOR / APPROVER: Engineer. Delta
575ec631-ef85-52ff-aaf3-43eff683160d | note | HOLD OR WITNESS POINT: Witness Point
9ab23a42-697a-469c-8da7-b7d84832468a | checkpoint | 11. Obtain operating and maintenance manuals
1d21a6e0-5a15-566b-a5ce-81787cd7d906 | note | STAGE / FREQUENCY: Prior to practical completion
18fdabcc-f116-5909-9b27-a813d7ef5d2b | note | RECORDS: Manuals
87ee5968-ebe7-5c22-8fee-5b8c259d86a8 | note | INSPECTION / TEST PROC: Document and Review
54c7ab96-fbda-5520-b46a-112aae36dc7e | note | INSPECTOR / APPROVER: Engineer. Geschke
283618a2-76cb-560b-90fe-48b5e51a0f33 | note | HOLD OR WITNESS POINT: Witness Point
9b3af6ad-13fc-490c-8c2e-8a26c4d2fd41 | checkpoint | 12. Obtain Guarantees
0e013afd-5bb8-5946-80af-27c5f898cf2a | note | STAGE / FREQUENCY: Prior to practical completion
06b4a433-d07b-51e1-816c-e013ce805525 | note | RECORDS: Written guarantees
7d1b04f6-46a3-5d52-844d-469011b2c4b6 | note | INSPECTION / TEST PROC: Document and Review
a85c6891-a917-5860-b229-728244331ed9 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
88527067-4780-5a17-9cae-fe29b5f2ae52 | note | HOLD OR WITNESS POINT: Witness Point
4b2a4e29-2c33-483f-a2d8-80193d2927d3 | checkpoint | 13. Final commissioning & inspection
919ae103-1c9f-5d40-ad51-6ba14c7cb6bd | note | STAGE / FREQUENCY: Prior to practical completion
ef72ea90-4e41-5360-8a53-eddcc67d1657 | note | RECORDS: Final commissioning checklist
150d6508-042e-552e-bb86-f295a5810bf7 | note | INSPECTION / TEST PROC: Document and Review
376396e0-9198-5b59-b7cc-02f0e5849aa2 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
722df9c0-31c9-525d-9236-cfe1532c910a | note | HOLD OR WITNESS POINT: Witness Point
30598531-8dce-449c-8e99-e2fdf77694f2 | checklist | ITP - Subsoil Sample |  | ITP - Subsoil Sample
d01b6e12-35d9-43c1-8695-c5d42b7ad9f7 | checkpoint | 1. Approve specialist subcontractor
0159adad-104b-5762-9c24-6868603cb7be | note | STAGE / FREQUENCY: Prior to awarding subcontract
894815f2-6a65-5078-81e6-9df95dfbd1d5 | note | RECORDS: Refer to Overall Project ITP – for Written approval Geschke Quality Management Plans
ff612384-b3fc-5151-93ec-04e9c0519634 | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
a2ff57eb-d360-5278-bbb2-b1f123bcae1e | note | INSPECTION / TEST PROC: Document
598133f5-e992-5630-bd47-50def7fc8b17 | note | INSPECTOR / APPROVER:Subcontractors Authorised Representative. Geschke
4099f9f5-54ce-55d5-8e01-64e75a610345 | note | HOLD OR WITNESS POINT: Hold Point
c3d80a88-4871-442b-8770-3091610d84c5 | signoff | hold point
887d4ea9-9c3f-4065-ad4c-b57c3363cca2 | checkpoint | 2. Approve Samples
9c861551-577d-5dac-9703-dd3a0c9f0a29 | note | STAGE / FREQUENCY: Prior to ordering materials
e8d1cace-953f-5a0b-a4b7-5fa81e858aa8 | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
8ae12bcf-6a44-5d69-b10d-7b72320e4cd6 | note | ACCEPTANCE CRITERIA: Samples is marked with ‘Approved For Construction’
f6adcd12-98af-5f70-98fb-da9f53a56463 | note | INSPECTION / TEST PROC: Document and Review
9482c8d0-d917-51f5-a596-4ed4e62bb3b0 | note | INSPECTOR / APPROVER: Engineer. Geschke
10dd5607-1848-51ca-b381-55a9940bc869 | note | HOLD OR WITNESS POINT: Witness Point
45bf483b-4400-443a-946d-da32c7514010 | checkpoint | 3. Approve technical details
7cb7444a-e4ff-55dd-bd8c-f4911951cdbf | note | STAGE / FREQUENCY: Prior to ordering equipment
6cfa8ce1-d2e9-5e37-8d0a-2c2948d2baba | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
53a1468d-a7e1-5979-9243-823259e2a6d6 | note | ACCEPTANCE CRITERIA: Technical Data is marked with ‘Approved For Construction’
5276957e-1621-5e22-a4b8-cd91a862ca2f | note | INSPECTION / TEST PROC: Document and Review
ae3e10b7-dfbd-52da-b5d3-7ac2756ae9ff | note | INSPECTOR / APPROVER: Engineer. Geschke
c46d5628-4329-504c-8e4b-6d135ea4a43c | note | HOLD OR WITNESS POINT: Witness Point
05ee4cbb-5784-4b2a-997a-30450ca1ee01 | checkpoint | 4. Approve shop drawings
c7593188-8ec3-54c9-8f03-426e76e3d50c | note | STAGE / FREQUENCY: Prior to commencement
46dfc537-e7a5-5a05-8aa4-f9e68c78742f | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
3b740173-18aa-5175-bce1-c9975ff98558 | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘Approved For Construction’
707075f2-9e4b-5418-b92f-4c53ddc7a901 | note | INSPECTION / TEST PROC: Document and Review
3596c461-1289-59ca-b85f-0b2e97b39a13 | note | INSPECTOR / APPROVER: Engineer. Geschke
0c8ca3c4-a592-5854-adb3-28959be8d45e | note | HOLD OR WITNESS POINT: Witness Point
9227e489-f770-4006-82a8-f672297a6ffb | checkpoint | 5.01. Check set out - Works by Delta
5923d45f-0595-576d-8c75-bf020bff2ee1 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
1a1af850-4fc2-5905-869e-1be31881e393 | note | ACCEPTANCE CRITERIA: Set-out of pits is marked with pegs and alignment matches design layout
33358cb3-709b-5077-8ad5-e6e82d9dbf6d | note | Height control point is marked within 40m of works area.
f5dcd7b5-58f0-569e-a63a-0c32609adf56 | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
ae336e4d-5948-5a15-b8d5-5a3d398eae2d | note | INSPECTION / TEST PROC: Visual Inspection and Document
4e22b595-ba4c-5683-8fb2-609a1df5826c | note | INSPECTOR / APPROVER: Foreman. Delta
09ee24bc-303d-5283-8017-513ef40a24ab | note | HOLD OR WITNESS POINT: Witness Point
96a4979f-ed0e-4e28-829e-e81cad47a385 | checkpoint | 5.02. Check excavations
51e4a3e9-e9a1-5749-81d0-87f07f836c45 | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
84eb9581-fe9f-593e-9f95-ef03d6f24734 | note | RECORDS: 'Before' Photographs
c5cb3906-c3c7-5f00-937d-7d8d0814d8fd | note | ACCEPTANCE CRITERIA: Alignment commences at outlet and proceeds upstream
abed271b-969f-5f86-b573-dd60810a7212 | note | Minimum falls
6aa20458-1ee9-5f32-9748-6e6d029b9f8e | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
27f9b1f4-143d-5185-a7aa-9cf23d749ef9 | note | INSPECTION / TEST PROC: Visual Inspection
59db2560-c93f-5d3f-b29b-3972e6272b7f | note | INSPECTOR / APPROVER: Foreman. LLB
d3ba4b1f-a4c2-51d3-9648-ca193b0d19c0 | note | HOLD OR WITNESS POINT: Witness Point
b59e0799-c56d-40f1-9a82-c3dad507460f | checkpoint | 5.03. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
e5fae846-c7e1-592e-a88b-8e361d756b29 | note | STAGE / FREQUENCY: Prior to commencement / Each TMP
1caa2069-54ac-54c3-b7ce-1632ec38aab2 | note | RECORDS: Copy of Consent and Traffic Management Plan
e689b575-34f3-5685-8744-e09a6e2d1b4b | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
379ea7af-f402-5e9e-b85a-2ef343da6a51 | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
d643211b-6a32-5a42-accc-18ef654ac5e8 | note | INSPECTION / TEST PROC: Document and Review
6eeccf5e-3330-5d6a-aefd-53a8ed5828cb | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
e6f316dd-1dd0-5477-a916-2a8fb671f713 | note | HOLD OR WITNESS POINT: Hold Point
d61f88cd-2eba-4326-8b54-9ffc7047b0da | signoff | hold point
bcacdde4-8f7f-421a-a258-0b10d859d924 | checkpoint | 6. Check deliveries of materials
48a40da2-46ce-55f6-b90d-7aebbb8ea91d | note | STAGE / FREQUENCY: Each delivery
72138ca7-831e-57d8-a164-2ef55c71387b | note | RECORDS: Delivery dockets name, signed and dated by Geschke
823c2321-43b3-51d5-bb03-a357f5065959 | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
a453c28a-8c75-53ba-98ce-f97b6c919f93 | note | Grade or class matches design
12c103d7-02c4-55d3-9ff2-dda520ea6c36 | note | Size and thickness matches design
e323aa18-851a-5092-ab11-0adea81858c0 | note | Supplied items are free of defect
5b5a88ac-44f8-5259-8d1c-053bbc715548 | note | Marking, packaging and preservation is fit for storage / construction.
b65fdf9d-6967-51af-a1bf-741f30f79578 | note | INSPECTION / TEST PROC: Visual Inspection and Document
ba3a9571-e687-5176-85fb-78019351e8a7 | note | INSPECTOR / APPROVER: Foreman. Geschke
22a4d4ad-e2ca-5796-9681-0ee8c90a9ee5 | note | HOLD OR WITNESS POINT: Witness Point
b970245e-c54d-46eb-9fad-a8d2beefae6e | checkpoint | 7.01. Check below ground pipework - pipes and fittings
af90dced-7da6-5886-8059-6c533e21796a | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
02c16be7-6e3c-5d31-a883-677e38736729 | note | RECORDS: 'During' Photographs & As-built Survey by Delta
78e8c847-0169-5a1d-a243-9a4c83841645 | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
12febe1f-a7f2-5ea6-bcbf-122bf8fb0919 | note | ACCEPTANCE CRITERIA: Joints, fittings and connections match design
b451adff-b664-579b-93be-97ef7db1d64d | note | Alignment and position are as drawn
41173cf8-875a-5cbe-987c-6c4ea88de7ee | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
de1599d8-4f69-58ed-b8a1-2267aec5f0f4 | note | INSPECTOR / APPROVER: Foreman. Geschke
f96b1f12-c4cd-55f1-a97e-82a98b9224ab | note | HOLD OR WITNESS POINT: Hold Point
0bfffe4a-6744-4862-869f-ed29ce665632 | signoff | hold point
d0db848a-d316-4646-b058-416ece1b235f | checkpoint | 7.02. Check below ground pipework - high ends and flushing points
7aeb3fa8-dc11-56ce-8527-5272d88d2518 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
250e815e-b8a6-5cb3-8ce2-27c5a0236389 | note | ACCEPTANCE CRITERIA: Capped at surface level with hinged lid, cast iron box in concrete surround 300 x 300 x 150mm
fc68bb3f-bad6-5ad6-b1ff-22bdf64a297e | note | INSPECTION / TEST PROC: Visual Inspection
14a235d7-5030-530b-bad5-f190fcdfd788 | note | INSPECTOR / APPROVER: Foreman. Geschke
9937e6ea-570e-51aa-b05b-9ea487b5c77e | note | HOLD OR WITNESS POINT: Hold Point
9c62a3d9-b269-4d29-b96a-8e741f5a291b | signoff | hold point
7fdfe9aa-0034-48df-9c34-7c16846d497b | checkpoint | 7.03. Check below ground pipework - haunching, surrounding and encasing
02ab062c-737e-5176-93e2-d534bab75e85 | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
41329d83-b216-5e13-9ea7-652a9c04cffa | note | RECORDS: Photograph
bc51876b-7817-5bb8-b019-90f467daa82a | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.19.3
ad736fb6-ab4d-5651-aa90-bd4831407edf | note | ACCEPTANCE CRITERIA: Free draining granular material
59abb907-2d7e-5143-bc6b-ab6fbf3a6f0f | note | All faces of filter material in contact with topsoil or similar shall be covered in geotextile
bcefd8f0-a4fe-54fe-a4ad-428440098931 | note | Material used is as specified and approved.
32e169eb-8d0d-5a7b-a317-3d0cd425518a | note | INSPECTION / TEST PROC: Visual Inspection
3bbac634-c12d-59ba-8c2f-982a887d69c1 | note | INSPECTOR / APPROVER: Foreman. Geschke
d386b70d-c541-5a4f-98d5-c4a007d8eec6 | note | HOLD OR WITNESS POINT: Witness Point
8c3a94e1-c8f1-4b7d-9c78-a945f5ff1216 | checkpoint | 8. Check Completed Surface - Make Good
af7fad3b-ab51-5613-9a31-a5784b200c6c | note | STAGE / FREQUENCY: Prior to practical completion
bcb99cbf-6f6f-5c41-bdfa-df696a4071bb | note | RECORDS: 'Upon completion' Photographs
86a97775-5a53-52e2-a0d5-f0ae17334d55 | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework less depth of works by others
6d9a878a-8913-5c51-9827-811f18bc0ff9 | note | INSPECTION / TEST PROC: Visual Inspection and Document
1e04539a-8c89-5b52-92cb-6da0cecdf724 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
55fa4827-5283-5f6b-ac56-73b5a9361238 | note | HOLD OR WITNESS POINT:
d0ba936b-2afd-55c0-9058-0e75622d86ba | note | HOLD OR WITNESS POINT: Hold Point
e7cb4412-35fb-49bb-a756-ef3cd1d5330d | signoff | hold point
b67eb590-6a28-4a20-899f-967d6feb5d95 | checkpoint | 9. Obtain 'as built' documents - Works by Delta
0e54df50-b3aa-5e2b-bad4-66655b9c24c3 | note | STAGE / FREQUENCY: Prior to practical completion
e4e7a170-9b93-5d23-915e-bffb07632de4 | note | RECORDS: ‘As built’ documents by Delta
c1c60be3-e084-52fb-abd3-baa9902ba39b | note | ACCEPTANCE CRITERIA: Drawings are marked with ‘As-Built’
e9258001-45e0-5e09-95dd-0948a886c467 | note | INSPECTION / TEST PROC: Document and Review
25cf659c-176e-5021-b3ba-e32b04ce171c | note | INSPECTOR / APPROVER: Engineer. Delta
815eb81a-7bf4-515c-96ac-114080ad270c | note | HOLD OR WITNESS POINT: Witness Point
3ac5b1cc-0a56-4207-b956-2f773d49a4ff | checkpoint | 10. Obtain operating and maintenance manuals
1a27cdba-8f64-5420-8441-d925b97658fb | note | STAGE / FREQUENCY: Prior to practical completion
c362c635-8c26-5d64-9f90-4e8bdafa48d3 | note | RECORDS: Manuals
2a7958f7-ab78-56be-8ef2-ad75516ca38f | note | INSPECTION / TEST PROC: Document and Review
991b3527-a68a-5afb-bd7c-666a4756afa5 | note | INSPECTOR / APPROVER: Engineer. Geschke
e64301b7-6bfb-5697-acda-5ac4d9489d3f | note | HOLD OR WITNESS POINT: Witness Point
927137c3-09d1-467f-9fc6-55912ebc4d6d | checkpoint | 11. Obtain Guarantees
2661309d-cefc-5ae1-ab10-43a475423310 | note | STAGE / FREQUENCY: Prior to practical completion
efa9069c-141b-519a-80ea-c2172683c582 | note | RECORDS: Written guarantees
e072951e-1351-56b4-beff-9aa68e5d6087 | note | INSPECTION / TEST PROC: Document and Review
343f0be8-deba-5bd1-b415-7f2349cd6653 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
bc23bfc7-f06c-54ad-9840-d6f998d53626 | note | HOLD OR WITNESS POINT: Witness Point
1641720b-f5aa-4439-9578-fa76f6b37940 | checkpoint | 12. Final commissioning & inspection
57e5a17f-147a-528d-bf7d-d988cf51c946 | note | STAGE / FREQUENCY: Prior to practical completion
13b93443-3282-50df-9f74-b3c2e20321d1 | note | RECORDS: Final commissioning checklist
212dea82-4edd-56ca-8c21-b97ba3f60503 | note | INSPECTION / TEST PROC: Document and Review
ed9bfa10-181c-5bf3-aa97-5d55c1272062 | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
64e0ec46-5b68-5005-ab44-b10c6b340cbb | note | HOLD OR WITNESS POINT: Witness Point
4bc58886-032e-48b6-85d5-c2d811c7f333 | checklist | ITP Trench Compaction - Various Services |  | ITP Trench Compaction - Various Services
aead651b-78c5-445b-8734-5c34bc5c2bc8 | checkpoint | 8.01 - To assist with the requirements of not only test results but ensure supervision to assess the competency of the construction methods a Level 1 GITA tester will be on hand to express an opinion on the compliance of the work practices. Geschke Plumbing are to compact in 150mm layers with Trench Pad Foot Roller.
f84b686e-10fb-5cc8-a357-b7da67065018 | note | STAGE / FREQUENCY: During compaction
d7ece903-8908-5608-922d-ae4ffa3d3719 | note | RECORDS: Written document by Level 1 GITA tester. Geschke mark-up of backfill type, test & observation location by grid
c43c6922-aa91-5dde-a35e-3b0ee99d691e | note | SPECIFICATION / STANDARD: AS 3798-2007
585e8b85-0ae1-5e81-b001-95a2ee947207 | note | ACCEPTANCE CRITERIA: Geschke are to compact in 150mm layers with Trench Pad Foot Roller
8dd290fd-fe8e-5158-b115-77177ba0f262 | note | INSPECTION / TEST PROC: Audit Activity
318ca935-0b5d-5c58-8f39-d052a1a7d9a7 | note | INSPECTOR / APPROVER: Geotechnical Testing Authority. Geschke
07d89956-40a0-5b40-bb81-9e266f37ed22 | note | HOLD OR WITNESS POINT: Witness Point
79c66eff-dd28-489a-a0be-bea819768e22 | checkpoint | 8.02 - If Stab Sand is required for back fill this will be delivered 5% stab sand as per approved material. 5% stab sand on 100 slump poured straight from the shoot
b88f97c3-7ac6-5afc-a610-203c004091a1 | note | STAGE / FREQUENCY: Prior to installation / Each pour.
b0b2a679-4730-5453-ac29-a54262f90d86 | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
d024b64d-a4da-5154-88ea-483071b07992 | note | ACCEPTANCE CRITERIA: Stabilised sand mix meets 100 slump direct from concrete truck shoot
3cdb2b3b-081a-5acd-8e8f-bb8e07dd4899 | note | INSPECTION / TEST PROC: Document and Review
5d10decf-e957-56bc-8d41-fe870bd35c5b | note | INSPECTOR / APPROVER: Foreman. Geschke.
9750872f-bb9d-5e1a-9626-46a96ce730dc | note | HOLD OR WITNESS POINT: Witness Point
de08c45a-6749-435f-9931-99b422da7922 | checkpoint | 8.03 - Testing to be completed in backfilled zones with 1 test “through” 2 layers every 40 linear meters. We will test our trenching through 2 layers at finished height less topsoil depth. This test will be completed approx. every 40 linear meters.
858a29b2-c50d-5026-b1ba-bf2e3d94b047 | note | STAGE / FREQUENCY: Prior to completion / one test every 40 linear meters
4ac44db5-6ac4-5003-8d8f-b258d8e91b48 | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
51ce7f5a-2c6b-5c14-9de1-270b02271f49 | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
536a95ea-42d6-54c3-aeaf-bde00d753647 | note | ACCEPTANCE CRITERIA: Rapid HILF Compaction Testing shall meet or exceed 90% or an equivalent density of existing ground found adjacent to the trench alignment. This shall include one field nuclear density test through 2 layers or between 150 - 750mm below finished level every 40 linear meters.
2db5c342-2ec1-58e7-b96e-44e41515f800 | note | INSPECTION / TEST PROC: Test Activity
3b2f4e33-4b35-5231-9ad5-9bb3e04084be | note | INSPECTOR / APPROVER: Foreman. Geschke
1a30cc23-e5de-5827-8ecb-6b16926e2458 | note | HOLD OR WITNESS POINT: Witness Point
806fcdd4-66ce-46d5-88c8-d6ab6ee64f23 | checkpoint | 8.04 - Testing to be completed adjacent to work zone as required by digging back top soil layer and testing in ground. One test in existing ground adjacent to work zone through 2 layers at finished height less topsoil depth.
57ffa341-d02f-5cfd-a578-90cc6e593ac1 | note | STAGE / FREQUENCY: Prior to completion / one test as required
45351f72-4d16-5f89-b042-60f1ca8028d1 | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
4c31c9f7-3897-5572-8ed7-ecced84cec96 | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
1bf9898a-3f4f-58aa-b480-a5fd722e7c5f | note | INSPECTION / TEST PROC: Test Activity
d96bc6b5-ab3c-51e0-8fc0-1ac30877d719 | note | INSPECTOR / APPROVER: Foreman. Geschke
872b11ec-0bf3-55c5-b1ff-ea950d9dd8c0 | note | HOLD OR WITNESS POINT: Witness Point
cf1d5c68-1a89-410b-b37d-8db63ae75cf2 | checkpoint | 8.05 - Compaction Test Results. Test Results as per above test plan.
fe869550-edc0-58ff-9721-7198bdc5512e | note | STAGE / FREQUENCY: Testing as per above
fa5823f2-5c80-5ac6-9f8f-47ef260db768 | note | RECORDS: Standard HILF Test Certificate
77e119b1-33fd-56c2-a994-6d7c3f6682c4 | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
25d69bbe-d32e-5528-a393-40777f09bc7d | note | ACCEPTANCE CRITERIA: Rapid HILF Compaction Testing shall meet or exceed 90% or an equivariant density of existing ground found in the trench alignment. This shall include one field nuclear density test through 2 layers or between 150 - 750mm below finished level every 40 linear meters.
3d60d9ca-134c-5db6-bcc4-1de5c03f84be | note | INSPECTION / TEST PROC: Document and Review
d64f942a-92f8-51a6-800b-352298273d58 | note | INSPECTOR / APPROVER: Foreman. Geschke.
4f11e61f-fb8c-54f4-82de-19b5a1ee0ba8 | note | HOLD OR WITNESS POINT: Witness Point
30c7f5dc-de1d-4f2a-b8a0-bce640b2dc84 | checklist | QA 4 - Installation Test Sheet (Waste, Vent, Downpipes etc.) |  | Installation Test Sheet (Waste, Vent, Downpipes etc)
41b6558f-a744-4c1f-b9ab-4e975852fe15 | checkpoint | Installation Test Sheet:
906caaff-e77b-5de1-8d33-ffce0834b694 | textbox | Drawing No.:
3356ffc8-8389-50f1-9abe-bf3d3dfcc0d5 | textbox | Rev.:
640fd2ab-6a53-49bd-9594-bba55fc04300 | checkpoint | PIPE CLIP HANGERS
2af50010-0bc3-5a3a-bc43-a518c07f234f | textbox | Details:
0c5851c2-70da-566d-a9d2-2c837720cc81 | textbox | Tester:
6e91f99e-ad01-50c9-9216-e4609aa2f7c7 | textbox | Date:
4f7035b1-4b20-5a81-9115-64d8e0af3214 | textbox | Notes:
e8c37028-7b5f-4dbe-ab25-e435ef591283 | checkpoint | MATERIAL AND SIZE
ef71596f-adcf-5645-b8a1-460b6f19d06d | textbox | Details:
c26e8d8b-cb97-5e90-b2a6-373cbc787766 | textbox | Tester:
ccffaec4-3a6f-5085-8db2-dd6cba30d0a6 | textbox | Date:
4e7725cc-29f4-595c-8fad-82b799ca0da0 | textbox | Notes:
e07ebd42-5ca7-451d-aca1-c229ac94a7c8 | checkpoint | ALIGNMENT
bee26fc4-fbc5-5df4-9cbb-5b8dfb929827 | textbox | Details:
04997130-4bb5-5913-9dbb-5f790f35fe85 | textbox | Tester:
04eaaa5d-a9c7-5533-9783-c85aac3c58ce | textbox | Date:
9d3c30cf-32a2-5ecb-8d49-f582ba88dbed | textbox | Notes:
6ef1e8c7-aacb-4863-b67d-e553432f8309 | checkpoint | LABELLING AND IDENTIFICATION
0442ce42-d121-5681-9056-d3c67a1703b6 | textbox | Details:
a426a860-c490-5bdb-b64b-660042a13896 | textbox | Tester:
5a896dea-b0d2-5ec5-9eba-661b0928c962 | textbox | Date:
18d684d7-313f-5d42-a54a-1854c4f9566c | textbox | Notes:
0e07d1f4-fd7a-4310-957d-d3847bfde8a7 | checkpoint | JOINTING
0e3ddc0b-1317-5215-9276-905a67b5bbc4 | textbox | Details:
589739fc-141e-551b-bcc3-950e48520341 | textbox | Tester:
d6d70d41-e7f9-5ff9-af73-503d39b1b421 | textbox | Date:
51d003ae-b96a-5d89-b808-2f88a7931507 | textbox | Notes:
3d7e0117-f494-4e2d-95cc-3a7adf061217 | checkpoint | PENETRATION SEALING
9b2c8686-0172-597c-8c12-36d4e1eb579e | textbox | Details:
7c5d2a78-4024-5d0d-bd3a-690b4bbebc0e | textbox | Tester:
1ebefbe7-98f2-58e1-b3d9-780fd36ee7bc | textbox | Date:
3382deb3-0b72-58c7-a9d8-90c5ffaee9e6 | textbox | Notes:
6376e7a2-1916-46ca-b298-aa947cd2750f | checkpoint | FIRE STOP COLLARS
aac5e4ad-433d-56b1-a096-d85bf40e490b | textbox | Details:
bed196ba-853f-5576-bd67-574d2c57e6f9 | textbox | Tester:
990f5e05-2dcd-5ec0-a4c3-cafe3e5077d1 | textbox | Date:
9544cf22-52f8-53b7-96b6-d1e402ecb109 | textbox | Notes:
bc4bb464-d638-4612-a01c-94c20a55fe9f | checkpoint | TESTING
6f01a272-2982-591b-815d-8f19ad758858 | textbox | Details:
2238000e-710d-5812-b357-795120df4680 | textbox | Tester:
60905c15-2a00-5f09-8f16-1dc73aee2657 | textbox | Date:
63371588-b82d-540e-9bd3-b0f54fed9203 | textbox | Notes:
efb20be5-1cf5-45b0-b7f9-b72d558f825f | checkpoint | AUTHORITY INSPECTION (if applicable)
ca7e1409-108a-5904-84d6-91131f0df3b7 | textbox | Details:
9ea79b13-f27d-5d57-a752-b440e192a012 | textbox | Tester:
ac1000ad-e0b2-5b0c-8ae4-b372be9ef0ea | textbox | Date:
7257ee9c-2a6f-5cbf-a730-2c04fb05da3a | textbox | Notes:
d80cae6d-9d12-4787-a946-dff494a4d533 | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
38e3b6b6-2578-5d15-9c13-524904e54b7e | textbox | Details:
dbadde48-2ffe-575a-b52a-c9e987275833 | textbox | Tester:
09f4d066-9ce3-5215-8579-d7f266099b6f | textbox | Date:
ed1b41b5-6760-52c3-8a17-5aa7b9711e57 | textbox | Notes:
a85a9320-f16f-4398-be51-785257d4b0df | checklist | QA 5 - Installation Test Sheet (Cold Water, Hot Water & Flusher Line) |  | Installation Test Sheet (Cold Water, Hot Water & Flusher Line)
68d983e7-1756-495e-971a-3a691afa7913 | checkpoint | Installation Test Sheet:
81a1d949-f22d-5ea9-972f-b450c60ed010 | textbox | Drawing No.:
f5899904-95b5-5f71-b0bc-2377d35abd2e | textbox | Rev.:
99b6330c-f12a-4290-819a-6f2568dc0c91 | checkpoint | PIPE CLIP HANGERS
e215e2d5-d61b-55b7-b7c4-2d83a148a5dc | textbox | Details:
cf6dfb5b-54bc-5b6e-a864-d906f2000e68 | textbox | Tester:
41f7ba76-4b1a-53e0-a2a6-87f197f5fe65 | textbox | Date:
4ca26751-2ca6-5566-8a47-615d35e324e1 | textbox | Notes:
2708424b-3b89-41e4-a171-d507c01df48f | checkpoint | MATERIAL AND SIZE
1a1757da-be6d-596d-8d75-f37b3e6e314b | textbox | Details:
b7eaabe3-83b4-50c0-a8ce-3ae0cbc89848 | textbox | Tester:
870250c9-5e37-5177-a588-97fc3767820b | textbox | Date:
3f3a6bcb-2d24-5f3c-b276-213dc4cab3af | textbox | Notes:
9b39123a-cb69-4680-9b20-4f6284773b49 | checkpoint | ALIGNMENT
7c7f8fe9-a8c0-5aa3-8dd7-8f6f31df1f2b | textbox | Details:
05aaaa16-092c-5437-84be-3e8cf88b540f | textbox | Tester:
09e77d6e-36f7-5682-855f-5110132a5cc6 | textbox | Date:
f21f2f3a-3d61-506c-b63d-7417e90e75b0 | textbox | Notes:
dff201fd-234a-4241-8444-a7fc2be42df4 | checkpoint | LABELLING AND IDENTIFICATION
45058830-afc2-57fb-8393-276ca1b28ae5 | textbox | Details:
3c71638f-2477-5feb-bef0-f913bbb4c9aa | textbox | Tester:
28cb07ee-8871-5ca0-8ca5-57bff650e9fd | textbox | Date:
4bb46535-0dc9-5d3f-8852-0e1b672f337e | textbox | Notes:
57d9dd01-7983-47ca-ad3e-64100ce45a2f | checkpoint | JOINTING
b4c15cd6-7551-53df-89f0-dfd9b9b98891 | textbox | Details:
21663479-045b-560e-babe-06716d1fc203 | textbox | Tester:
e0b5e481-a1b4-5d66-aabf-b1ecb30b6306 | textbox | Date:
77223197-560a-5c93-9356-3ead915875af | textbox | Notes:
b0326dfd-d13f-4421-bc28-aba778d7088f | checkpoint | PENETRATION SEALING
bf92df1d-6bf7-54b7-aa1d-284a03677ce4 | textbox | Details:
623bc954-99dc-5502-a25b-3ae36251612b | textbox | Tester:
9044c2ab-ab78-5c54-8ed2-db09e580f6ab | textbox | Date:
413c3bf7-1b67-5941-8da5-8df3192522dc | textbox | Notes:
ee2c404a-5f0b-423d-b59a-101d12b69a2e | checkpoint | FIRE STOP COLLARS
0fe4e770-e0e0-5f2b-bd42-2c3489b8a6c8 | textbox | Details:
a340537e-31ff-5fff-b3ee-a5594b5668dc | textbox | Tester:
3dab71ee-c072-58a8-9b77-4c333121640d | textbox | Date:
f32dacc8-0810-5b8c-a198-8bdb65f5679b | textbox | Notes:
6d2bdbca-98ef-4d95-8bf5-ad52346ef411 | checkpoint | PRESSURE TESTING COMPLTED (QA6)
747b954a-1c8e-568c-b1ff-f0117ca3ba90 | textbox | Details:
be8a8761-9e03-5fc3-8770-2f008996d998 | textbox | Tester:
cebf06aa-48bf-57ab-80c6-b22c4ae52146 | textbox | Date:
911b1ef1-f550-5850-b2e7-c101fac5d49c | textbox | Notes:
70b3815c-ff26-4c34-9986-c6994ea8616c | checkpoint | AUTHORITY INSPECTION (if applicable)
a986004a-b908-54ea-90e1-3075d2d41cc2 | textbox | Details:
800e2ab0-9a3b-5f03-b5b1-6d7617b8ab52 | textbox | Tester:
1fe0d09d-ff9e-5460-9d63-8b97bf2498fd | textbox | Date:
49611311-4f09-51a1-923a-18c3f96dfee5 | textbox | Notes:
df40deab-f582-4fcd-b5c3-7f622357d20f | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
89e07cdd-8740-5ba7-a28d-8ad9e467dda0 | textbox | Details:
2aae85a5-54de-53e0-863a-27f7cf1c978b | textbox | Tester:
b76e691d-4288-5ab2-bc1e-6dc5e21c7531 | textbox | Date:
a5a00e05-6417-5e57-a72a-0628145be067 | textbox | Notes:
b8e48808-27c3-427c-86b8-9d521ae56347 | checklist | QA 6 - Quality Control Pressure Test Report |  | Quality Control Pressure Test Report
ff9dd1de-0d71-498f-a699-0a7fca2d7670 | checkpoint | Quality Control Pressure Test Report:
a76a3c3b-423a-57f4-80d8-ee781664ff50 | textbox | Drawing No.:
4b602b00-15b0-5f49-a8b8-50b46d58d96d | textbox | Rev.:
c0ba4daf-2557-5e1e-be70-3de453387a69 | button | Test: | Air,Water
cd623fd9-4391-5d6e-bf2d-8967ae10c69e | textbox | Section
7e844d64-f037-5a50-bc14-7d1e31027d91 | textbox | From
f4db327a-1c87-548c-8366-e9f9298210c1 | textbox | To
7e25cf22-9b48-5c64-a6a2-0308a8d00e7f | note | Specified System Working
fb40819c-7583-5300-bc01-407bbde4d88a | textbox | Pressure (KPA)
e827930b-a62d-5a49-b2e8-bd9b3cd48d61 | textbox | Duration (HRS)
09f8468f-a83b-50e2-aecd-84208a81e386 | note | Specified System Test
f60b0878-4bb5-53f3-8886-dd99d2a5c987 | textbox | Pressure (KPA)
5dc499ca-fc9b-5210-a405-f6ce7cd8bd1d | textbox | Duration (HRS)
ee2fe745-67a7-4f32-a904-c399beb2fd66 | checkpoint | 1st Reading
d3523fe4-2d6a-5522-81a8-fb4489e336a5 | textbox | Time
9c51f8a9-c81c-5dd2-8678-7b831379ea7a | textbox | KPA
4764e692-0d71-51ac-90ce-f97962508da0 | textbox | Ambient Temp
8fa479d6-6ce3-4dca-9b3a-2ff14b646743 | checkpoint | 2nd Reading
348bc858-f500-54fa-9d24-223fa4a55e0a | textbox | Time
c9e982bc-b7b0-562d-ab1d-e84c9fbb39b2 | textbox | KPA
4e2d8844-1ed2-561d-92eb-2cd1514a9e42 | textbox | Ambient Temp
fe79b1b8-e6eb-45b9-b4b0-546e4ca5ddfe | checkpoint | Test Result - Passed?
0976cf18-aaf1-5796-b602-f31f2b0409df | textbox | Repeat
55c628ff-c1f7-47d4-81cc-f14723762340 | checkpoint | Sign Off
75705347-a7b2-5fc1-a294-1260ec776d58 | textbox | Geschke Pty Ltd. Representative
f21a0372-79a0-5e4c-b2c9-5bf448b85cd7 | textbox | Others Present
71e2a94e-e138-502f-b619-b94ea58b4515 | textbox | Date of Satisfactory Completion
95ce4af6-e123-4184-a8e0-e1f88a7fb035 | checklist | QA 6D - Quality Control Gas Regulation Test Report |  | QA 6D - Quality Control Gas Regulation Test Report
d1ffdcb2-221a-446a-a76e-5158606add0f | checkpoint | Quality Control Gas Regulation Test Report:
6d65609e-e906-5316-8b19-fc6ff30ab4cb | textbox | Drawing No.
f98de2da-8151-5db5-96bb-82870d950f4d | textbox | Rev:
2aa6c81e-93a7-4ce6-825d-c239ca06450f | checkpoint | Test - Flowing inlet pressure to project
0d06bd7d-cbd7-5205-b6ed-0ec795842b82 | textbox | Inlet Pipe and Size:
c8a56155-ffde-5274-b33d-18cf5a1ee7d4 | textbox | Spring range:
b15fa1f7-209a-5e6e-8c7e-68a99789c54e | textbox | Orifice Size:
6898a571-a52e-51e9-9f9a-5852a88b9efd | textbox | Model:
58b123a8-41a0-47ac-9e5c-7b66802d43ee | checkpoint | Section
6af74610-25d6-56c0-bf9a-cc4ce8fd5e1a | textbox | Section:
5de9ed46-edcd-563b-ab75-47511097da51 | textbox | Pressure (KPA)
eab37de5-c28d-4bac-88a6-806ed465c385 | checkpoint | Test upstream inlet pressure to regulation
c8f7da0c-1289-5ab0-ac46-88e20f28273a | textbox | Pressure (KPA)
d9e18efd-b3bd-40ac-89d6-a1b3b752e14f | checkpoint | Test downstream out pressure to regulation
f3463bb8-143b-51e9-b289-34472ba920cd | textbox | Pressure (KPA)
33aa935d-9fd1-5a35-8fc6-c2666e224345 | textbox | Duration (hrs)
386d8c75-fc48-46ca-a20c-77c77c8ac3d2 | checkpoint | Adjust out pressure KPA as stated on GPL shop drawings
0cb205a9-51a4-5e38-850e-31dc353cabf4 | textbox | Reading (KPA)
0a1fa5fe-30d3-4ba6-ac55-6802ae4e36d5 | checkpoint | Confirm outlet KPA does not fluctuate more than 0.8KPA
459494a9-5986-5e56-bf13-4d786a600c25 | textbox | Repeat:
9bacbcd2-07e8-4de7-9899-8674627cfcb4 | checkpoint | Sign Off
25d5dc6c-4812-5406-9f8d-d9f1877b868f | textbox | Geschke Pty Ltd. Representative:
5b4dbcfb-8fc3-5b84-b848-578a8d1d3c93 | textbox | Others Present:
36a7865f-2ee6-5618-ae5e-3e4c8207d6b4 | textbox | Date of Satisfactory Completion:
8a18cb42-d369-4804-9913-f604d5976272 | checklist | QA 7 - Commissioning Test Report |  | Commissioning Test Report
d446ec9b-0ffc-432c-a668-be69f783129f | checkpoint | Commissioning Test Report:
d8b10556-6315-5190-8a4a-122f0e7d7c92 | textbox | Zone/Grid:
782cbd5c-7764-53db-8fdf-f6358522df4c | textbox | Drawing No.:
39f5e9f8-070a-5498-b028-bc70f22a7a6e | textbox | Rev.:
2136b26d-8de9-43d3-9cf4-e5110d3d87c3 | checkpoint | Item: FIXTURE OPERATION - Pans, Basins, Sinks, Other
8f06d746-6d5d-5ba9-991c-ea79049d734c | note | Test:
ee9cdadf-96c8-5369-9bd0-d406bfb5151d | note | Performance Test CL 2.20
ed57333a-d733-5a44-accb-21e426cddf90 | note | Fill fixture with water remove plug
e610fe82-b5fc-5ff1-91e9-64ba1a6496dd | note | Test for:
65cb6bfa-db2b-5bbe-832b-cabe792686eb | note | Leaks
dff59d6a-d888-518c-b2d2-46e380ce4652 | note | Loss of water
d727a8a9-5cf3-5cc8-b5ad-0584aa4307ed | note | Seal in Trap
95b051de-7fd6-5b6f-aec9-9dae2b4ba9c4 | note | Induce siphonage in trap of adjacent fixture
1dbed039-f3f6-5329-82e7-45e82f8f7f56 | note | Complete draining of fixture
c6e7581a-d897-5417-8a46-3b08cb61e19f | textbox | OK:
f6109591-0844-5c0f-8afd-9d956122be03 | textbox | Not OK:
646a9e32-aff5-4d64-b111-cdfd7aa958d6 | checkpoint | Item: Water Supply
099e40ac-1871-5bf2-90a0-178c9da050c4 | note | Test:
0d7b80f9-471c-5dbd-936a-b64e9e43cc27 | note | Performance Test CL 2.20
3bfcaf18-a659-5f83-b160-585da6ceda43 | note | Check for adequate water volume.
cf162cba-2c63-5790-8565-51912d069eac | note | Flush out pipework
fd7edfdc-a4bb-5836-8d55-84a1528c5e64 | note | Clean aerator
6fe1c38f-eae3-5a68-b554-6acf9f493be4 | note | Water hammer
78c0866e-71b5-5190-9f47-d99a1492092d | textbox | OK:
d53ec313-bb78-568f-a3a0-43f73460606b | textbox | Not OK:
03166743-0f88-43de-9380-634242174b28 | checkpoint | Item: Flush Performance
a40c7aac-894f-57d0-87c5-117971851276 | note | Test:
cb6e14da-bf56-5d8d-828b-495380655588 | note | Performance Test
0894fb33-1f51-5b9e-87a8-2ab2e4703995 | note | Check for:
52db0bfb-dadc-55c4-9d1f-71c303e24999 | note | Water Volume
16501f0e-47f6-55e6-9769-5f95d9d57f8d | note | Duration of flush
9bdf0d1b-c41d-59eb-abea-30189dfb72d6 | note | Flush out pipework
f2533ff8-1b7b-57e5-a3f0-0dd2149941f0 | note | Water hammer
6ab3f1cc-e350-5afe-aef7-7da79ea776e4 | textbox | OK:
156f10eb-d0c2-5ef1-8cbb-0fb446c29021 | textbox | Not OK:
01755b5c-5b2b-48dd-9e91-54830ebae3fc | checkpoint | Other
8c4a65f4-7ca6-4e64-b6c0-8438d0f61555 | checklist | QA 8 - Below Ground Pipework Checklist - Fire |  | Below Ground Pipework Checklist - Fire
1d50323e-39b9-414e-ac24-67e2272787d9 | checkpoint | Principal Contractor Permits Issued
6d289ba8-1c95-40ae-a675-7e6951282ab7 | checkpoint | Set out pits depths and trench runs.
ee3a64ce-00d6-5093-9df6-8236684410e3 | note | As per DRG#
54c44535-194f-4162-b1f2-db3759b4213a | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
dccbb4d1-f485-5392-b415-941982aad3ff | note | Spec#: AS3500
8383b351-547c-59cc-8ee0-44a8aa5d5766 | note | MDPE SDR11 PE100 PN16
b5c3b74a-b0ae-4dfb-93a7-e013ca9e5b14 | checkpoint | Bedding placement and compaction and material meets specification.
02a4112f-259e-5604-946c-cc59cc96ce2f | note | Spec#: AS3500
fb1944f0-180e-5ac7-b65d-e62361a74867 | note | Packing sand encased pipe
bdff6b0a-827d-4254-8b2c-702a8d930998 | checkpoint | Jointing of pipes
c034410b-eea4-5a20-a300-b21508438f60 | note | Electrofusion and/or Butt Welds
a3ef53b1-e6f2-5efb-9536-5f66729e6d2a | note | GPLQA16 form
f5b50ba2-5f85-4159-b9ec-819a1c8106a0 | checkpoint | Connections to pits and existing services as per spec and Australian Standards
95c2ff63-4f1d-46be-9608-8ddb13d094c7 | checkpoint | Hydrostatic tests are carried out as required.
1d92c76a-d893-5de9-9f9e-dacd55a61c12 | note | GPL QA6 form completed
1a3154d6-c733-52e5-be53-bc9e32f9f0c2 | note | Fire system tested to 1700 kpa regularly prior to finished surfaces installed. Independent fire test at completion.
8883f8fe-7803-4d56-aa67-e675465e42f3 | checkpoint | Placement and compaction of backfill and material meets spec.
d1d5b543-0012-511d-bbb2-1092cd51023a | note | Compacted crushed rock backfill 80% to 100% compaction
26270819-408a-5f25-8a6b-da1383df13e2 | note | Detectable marker tape
a5baf6e9-de30-4339-8c02-fccda6258f39 | checkpoint | Temporary cover provided to open drain.
463f6d7d-3307-4b10-b014-d61af9ed380f | checkpoint | PVC/ Plastic caps to open ends
f3a82f1f-6913-40f3-87a9-6c3f3c727174 | checkpoint | As built information updated onto drawings
0e48f02b-9cf5-5e2c-a9dc-84ba278a4775 | note | Ongoing
b8d4ef5a-5a35-5cf5-9e77-831e46fccbcb | note | To be provided
1d4be0a1-03b7-44fd-8574-88138ae7596f | checklist | QA 8 - Below Ground Pipework Checklist - Sewer |  | Below Ground Pipework Checklist - Sewer
2c763ea6-062f-41bf-b433-359e70695b44 | checkpoint | Principal Contractor Permits Issued
353f7bc2-dc98-4743-83b0-3ac8465f50be | checkpoint | Set out pits depths and trench runs.
ebbbfd8a-0f75-561b-b873-e5f1ed1870e5 | note | As per DRG#
03330dd2-3571-46db-bd85-0365a9b34ca5 | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
f34d91d3-7b3d-5923-ae30-459fbb9ee30f | note | Spec#: AS3500
22a1b5c3-78ad-5a95-8ef6-aaf2b25743a9 | note | UPVC BEP Type ISO 14001
9212b08e-8b03-4d33-8fce-e38375dce909 | checkpoint | Bedding placement and compaction and material meets specification.
2f40e9c6-a1a4-547e-985d-932f23c16025 | note | Spec#: AS3500
78285f8a-e02d-5b0a-aa90-3fac8960a8ff | note | 75mm Q-Minus Bedding and Encasement to top of pipe
9ec7a5a6-bb75-436a-9dce-477149edf8e5 | checkpoint | Laying and jointing of pipes R.L’s and falls
ac51e97c-24bb-5a0c-a3d3-c860b8a52e1a | note | PVC solvent welded
7f17aad4-e68d-5503-8ccb-981eb3b365ec | note | 1:60 fall
46e199af-25d8-57fa-8be8-8f7615addec6 | note | AS3500
d8d00b2d-7263-5dbe-850d-2dfd06c5e5cf | note | RL’s as per hyd drgs
604a646a-4a44-4436-9334-5f7ac9359156 | checkpoint | Connections to pits and existing services
3b4808ac-6fed-4a7a-96ee-5c67fbbafdec | checkpoint | Hydrostatic tests are carried out as required.
15da8139-0567-53dd-a1b1-626302a78b66 | button | Air or Water? | Water,Air
f79e2bba-9266-5c6d-a5f2-af78e4bd2644 | note | Inspected and recorded by Independent Certifier or PIC
89743b6e-7267-40a0-b6a6-66e333da338b | checkpoint | Mirror tests are completed if required.
a6156d51-d3b8-4e3e-93dd-cbd62af6380a | checkpoint | Placement and compaction of backfill and material meets spec.
8786f827-8673-5a2a-bf51-079e1909297b | note | Compacted crushed rock backfill 80% to 100% compaction
e744dd0f-d9bd-4a71-86c8-f2fb6d078320 | checkpoint | Temporary cover provided to open drain.
3f0c6f04-8180-43b4-a2ba-5c56d6b31a63 | checkpoint | PVC/ Plastic caps to open ends
80cd55b4-62d8-46ae-8d6b-4d9b30a8b5a1 | checkpoint | As built information updated onto drawings
8d675dec-da50-512a-a407-c386218b9bff | note | Ongoing
1faf02d4-ebd5-5543-ac10-498c58057911 | note | To be provided
431fd9de-92a6-45de-b35b-f2c6809ac5c7 | checklist | QA 8 - Below Ground Pipework Checklist - Water |  | Below Ground Pipework Checklist - Water
f90857e5-534a-468e-afb3-7166c1c8d33d | checkpoint | Principal Contractor Permits Issued
7de1b2e8-1ca7-4374-b727-656004048499 | checkpoint | Set out pits depths and trench runs.
18c68d65-3221-54cd-8c2c-0f5594d8b496 | note | As per DRG#
9096bfc0-9305-4347-93e0-47b4b23f5415 | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
78ce1876-f9ac-583f-8bcb-d75d96a1655b | note | Spec#: AS3500
c5b3c7be-470c-5488-8941-81515c36374a | note | MDPE SDR11 PE100 PN16
f1e38d7b-4e19-4bac-a3c0-bcf2230f9daf | checkpoint | Bedding placement and compaction and material meets specification.
d32ea146-0396-55dc-9e27-0a54f74008b3 | note | Spec#: AS3500
46ab1b88-c0e6-51ab-9d47-96bbca35f0ff | note | Packing sand encased pipe
296355a4-15ca-48f0-ab28-1b2a163164e6 | checkpoint | Jointing of pipes
5fe7940b-aab8-5025-a28c-dc23c471bad6 | note | Electrofusion and/or Butt Welds
80c4be14-baa5-5aac-9502-2078090017f6 | note | GPLQA16 form
7881427c-dc28-4243-a9cb-fed4520e97d4 | checkpoint | Connections to pits and existing services as per spec and Australian Standards
c5ff60a2-43af-4aab-807b-90cf7918a8a3 | checkpoint | Hydrostatic tests are carried out as required.
baf76e8c-b0b1-544d-94e1-2cf1689737db | note | GPL QA6 form completed
e408556e-f8f1-5787-b545-9009388e2c86 | note | Water system tested to 1400 kpa regularly prior to finished surfaces are completed.
8d27db87-dd36-49c3-8a19-ee95498aed7b | checkpoint | Placement and compaction of backfill and material meets spec.
d1ffbe04-e4ac-5907-9602-398c5baf64a0 | note | Compacted crushed rock backfill 80% to 100% compaction
5e88c625-e0a1-5615-976e-14823d4c042f | note | Detectable marker tape
58a488b7-9bb4-45b0-92ee-ff13511edbdb | checkpoint | Temporary cover provided to open drain.
32167f32-b3af-42e7-b04f-86af98b4f657 | checkpoint | PVC/ Plastic caps to open ends
8a537a51-07c5-4421-97aa-71362b5bc8ba | checkpoint | As built information updated onto drawings
aaab9df4-8a31-59f0-a28c-4df4efb914a4 | note | Ongoing
402bed8f-60da-50a3-b1a6-22c2db272cfe | note | To be provided
8be8a940-e393-41d4-a98d-182bba01f2f8 | checklist | QA 8A - Grease Trap Checklist |  | Grease Trap Checklist
becf83e8-7148-42c8-ae7a-f1a62e3c743f | checkpoint | Set out of pits.
5a1425f0-6ac1-4ea3-a09d-272effa1a77c | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
fba8f50a-3d15-4596-8087-3e19e3ee1c7d | checkpoint | Bedding placement and compaction and material meets specification.
215b2a5e-df87-4bc4-8bc3-3580fb39d225 | checkpoint | Laying and jointing of pipes R.L’s and falls
e2eb0999-48d5-4fb9-b854-fd1a7af7ea58 | checkpoint | Connections to pits.
8964f786-3c2a-4b33-b9d2-c1eed5387eb2 | checkpoint | Baffle is in place.
6656fd4a-7c5f-4d09-8365-de9d26751d2c | checkpoint | Penetrations are patched and made watertight.
5169790a-511c-4383-91ca-393a48d0ec11 | checkpoint | Suction line is installed as per spec.
976278f9-24ec-418f-8f12-c69120404b26 | checkpoint | Outlet pipework is installed as per spec.
c3e057eb-aeae-4f23-bee6-8f7213a7ad52 | checkpoint | Vents are connected and terminated to comply with Authority and Specification.
4ff06aa9-b3c1-4166-9e2b-8d16b3ff8eea | checkpoint | As built information updated onto drawings
455b1f31-e378-495e-9e83-10bbd384a3ef | checklist | QA 8B - Stormwater Drainage Inspection Report |  | Stormwater Drainage Inspection Report
948e0f02-9668-4c92-ae31-24cb01679425 | checkpoint | Stormwater Drainage Inspection Report Details:
3b08284b-3e10-5e63-a1f4-db9c012b1e17 | textbox | Spec No.:
bb9667d1-67ac-5da2-9c88-5c182c182d9c | textbox | Drawing no.:
cb61e086-4f0f-5924-bc8a-08c60a0ccb25 | textbox | Zone:
09fa77d4-cde6-491c-8492-3d6036e8d27a | checkpoint | Pipe Lines
32d64238-d201-5287-ae20-cc485c6c5438 | textbox | Date started:
64020183-05b8-51cd-90c3-6f05595359b8 | textbox | Drainage Line Number:
002295a2-e3b3-5638-8854-01401a01f0a6 | button | Pipe Damaged? | No,Yes
030ade9f-506a-58f8-b4c7-823d2d3d1902 | textbox | Size and Class
cd91abea-6c7c-5390-b9bb-ef58e149699e | textbox | Jointing Required
50c4ac96-937e-5d49-8cd1-2d216101e960 | note | Bedding and Haunching
93c08671-6175-5f42-a0be-5802362664ab | textbox | GPL - Initial/Date
fd37dcea-a8e4-5aed-8052-a854dc2176ad | textbox | Builder - Initial/Date
28dfc02b-c59a-51b0-95ed-a69aad3df7ff | note | Backfill
d3c9b954-3a02-5db4-9d25-12fa6ef4de77 | textbox | GPL - Initial/Date
fa51978a-dc83-5038-b8e7-f376a2d03b7a | textbox | Builder - Initial/Date
b09ec8a0-1519-518d-a176-6ae553b6ea74 | textbox | Comments
c3f772c8-d8a8-59c0-8c01-1f9db23fb3f8 | note | Final Sign Off (Initial & Date)
fade6da5-1f84-54b7-b24c-f42bb64d0be9 | textbox | GPL
bd08a582-0a82-5238-a3f3-70cf87bc87a9 | textbox | Builder - Initial/Date
8e008786-3eb6-5bb2-bbaa-a5ac2ed552e2 | textbox | HCC/CARDNO
6c93bbe8-15ce-47c2-8d67-5e6fd6f2ad48 | checkpoint | Drainage Pits
cef1eb25-a3dc-5d33-a32a-f5507ef63c85 | textbox | Date Installed:
403a82f5-93de-5b12-88c4-a4bcb2f72158 | textbox | Pit Number:
5ce1f569-9acf-5b8d-b21d-88305361f40d | textbox | Pit Base:
fe923d42-99e5-5f2f-973c-c9e2b742575f | textbox | Step Irons - GPL Initial/Date
0621e4bd-54d4-5f23-8ec5-4815183f94b6 | textbox | Bedding - GPL Initial/Date
8a9e6866-1c3f-5902-9512-364555a5b1a2 | note | Benching, Grouting and Patching
a350a4d3-bf1a-5162-bfd8-8e27e31bf67d | textbox | GPL - Initial/Date
66b62c3b-460d-521c-bb74-b90fe4a4352d | textbox | Builder - Initial/Date
d7f2c46b-aea3-52e6-9909-12d2da38a1cb | note | Placement of cover
8930c515-b684-5b98-a7e7-c0bac0ca8fca | textbox | GPL - Initial/Date
bba9616f-aa0d-5fae-8ac2-25760d75aec3 | textbox | Builder - Initial/Date
0f33a7ca-8562-526d-b5ff-ddc09f8abb6a | textbox | Comments
629036d3-4bf4-56b2-8a6d-df03512dddd6 | note | Final Sign Off (Initial & Date)
d918e3ee-42f5-5ffd-9eaf-60a59984fa16 | textbox | GPL
704780cc-b28d-56d3-a5c8-7a343398aca8 | textbox | Builder - Initial/Date
c0a102b7-4ad5-5a2e-bc57-aa61052c9606 | textbox | HCC/CARDNO
ca48befa-0bb5-44c2-944f-d28d50a2fdc1 | checkpoint | Compaction Test Report No.
6db69d51-b977-544d-a749-bfdb7f942335 | textbox | Compaction Test Report No.:
948fe117-fedc-475a-9052-d5b2c0ebf94c | checklist | QA 9 - Non-Conformance and Rectification Report |  | Non-Conformance and Rectification Report
8de26f44-e29a-4cd4-80ec-6205f49b3345 | checkpoint | Non-Conformance and Rectification Report Details:
2b4a67cd-2e55-523c-878c-6bfa8b3e68a5 | textbox | Drawing No./Rev:
72154a03-78de-5969-a28a-e4e162cc5a40 | textbox | Zone or Grid:
2219f60c-0863-585e-890f-ee94a9b5c092 | textbox | Issued To:
10963ddc-643b-53ac-919c-cece6daec964 | textbox | Item Not Conforming
eecdf670-d40d-503d-9728-81d2ce06bf51 | textbox | Reason For Non-Conformance
09a406ea-b0ab-54de-ba53-e631fcda47c0 | textbox | Consequences: Impact On Time, Cost Co-Ordination Etc
c89f7adc-71c0-512b-acfd-30d3a9a1ea8d | textbox | Action Required:
b5534fc0-666c-5ba0-83fe-0f2eb06dd8fe | textbox | Date:
7917334d-7bd8-56ec-949d-dd354b658e4b | textbox | Rectification:
711e4492-f137-5d0a-843f-986294dcca6a | textbox | Date:
27eba4dd-a1f1-5192-be88-721592f9d40e | note | Note: Non-conformance register to be updated
5e057876-81ff-4936-ab1f-bf758b570fc2 | checklist | QA 11 - Equipment Calibration Register |  | Equipment Calibration Register
d9c90bdf-fa88-448f-9049-cf652b4c3d40 | checkpoint | 1
8ee1fcab-3da6-511d-9015-1685ad36500d | textbox | Equipment Type:
8144ddff-8f73-5693-9a22-8cbfb9b474b6 | textbox | Manufacturer:
d366d6e9-a056-5840-a013-05d855e285fe | textbox | Model and Type:
b8bcd9fb-bdf1-5846-bccd-7b031878562b | textbox | Serial No.:
aeb8caee-6527-5004-9730-516285e9efcb | textbox | Next Service Due:
bb1af169-6561-4a6a-912b-1aad8b32e009 | checkpoint | 2
5916b24a-ba09-5ad3-bbe0-2cc11bd9d882 | textbox | Equipment Type:
7b41393b-98d0-5090-9caa-c767d1d148f2 | textbox | Manufacturer:
0c180640-84d6-5484-b921-668c6b50e263 | textbox | Model and Type:
828c8221-0498-50fa-8bc8-b4f96b67ad84 | textbox | Serial No.:
a57e3e51-1573-57f3-9e37-085615e53def | textbox | Next Service Due:
0af221b3-f193-4985-9022-a048b8322418 | checkpoint | 3
a889b847-850b-51d8-9218-2aaf43511849 | textbox | Equipment Type:
81421c6a-12b6-5d8c-b7d6-67d27a66d9ed | textbox | Manufacturer:
d09aa1aa-4795-5327-9460-9212508d4f1a | textbox | Model and Type:
fa5b33e9-4eff-5c3a-a8db-123823d378e2 | textbox | Serial No.:
b59b6ea6-6eff-5bce-b559-bbdd5e742947 | textbox | Next Service Due:
2c32cfe9-9108-479f-b00d-1041fff0c015 | checkpoint | 4
5c18ddf0-820c-563c-aebb-4e4084a7629f | textbox | Equipment Type:
27078c5a-57a0-5836-82cc-a97249d9d1a0 | textbox | Manufacturer:
e433b39b-918b-5cd1-b808-f2bb30739fad | textbox | Model and Type:
3ef9ced9-6fb5-5519-89bb-055aab615fbc | textbox | Serial No.:
25138948-c22b-53a6-9ecd-950f1faad39f | textbox | Next Service Due:
6b9b481e-a213-4cef-9f8b-fc74b72a3469 | checkpoint | 5
6f2537d5-86f0-5304-842d-5f0c63f3dd9b | textbox | Equipment Type:
2a6b0c61-a271-5c40-b414-fd6befc0a092 | textbox | Manufacturer:
eee1650e-8976-532c-8691-9b8946095481 | textbox | Model and Type:
14709f3a-8a76-58c1-b60d-f8e9b3064f00 | textbox | Serial No.:
9239e27b-ffe7-5938-a8c9-248450facffd | textbox | Next Service Due:
ca1e6b2c-ad8f-467f-9734-8c04ef1cb336 | checkpoint | 6
534d69d6-efda-59e0-b1e4-6f217bcfd64b | textbox | Equipment Type:
7d037042-c513-5a88-b80f-c7d642ecdc79 | textbox | Manufacturer:
1481874b-7220-5840-b635-194261230b96 | textbox | Model and Type:
760b6cf9-87f9-5ef8-9978-c0782acee4d3 | textbox | Serial No.:
96152e6a-9015-5611-b2ab-24c99ce58433 | textbox | Next Service Due:
71bd1a22-3f41-4c2a-b878-af326e2dcdcb | checkpoint | 7
d64651f3-2bda-5fd5-8d97-acbf35b0b2cb | textbox | Equipment Type:
ff4fa0a6-d767-5500-b836-e7a13e35e0b0 | textbox | Manufacturer:
6dedfc63-3f39-57c6-8249-3561f95e1294 | textbox | Model and Type:
8a8ce29b-a93d-53b0-b93a-7066645cf858 | textbox | Serial No.:
9fedacd3-b24d-5fa7-8f26-923387257204 | textbox | Next Service Due:
0f443b0a-bdbf-4f7a-b9a2-b3a8e833a21e | checkpoint | 8
140738f0-f5cf-5c39-baf0-d2abba7c0f64 | textbox | Equipment Type:
d585d360-2d63-5ab0-baeb-9d65473a5b41 | textbox | Manufacturer:
5af66e0f-ebb4-5c06-a23a-d7c75db8e19a | textbox | Model and Type:
8a318c08-4b09-5c3f-9fdd-3c306a1014f9 | textbox | Serial No.:
750fc682-33bc-5c44-834d-1d9a5cce734a | textbox | Next Service Due:
0ce404c8-562e-4b89-a39f-e55a93b813c4 | checkpoint | 9
eefcbcc2-500e-5f51-b3ff-0cd8db7da199 | textbox | Equipment Type:
0e1c951e-1afe-593b-a374-4ccd167c1df2 | textbox | Manufacturer:
4b9833cc-3f45-500b-91a3-2e8a7efc805f | textbox | Model and Type:
27fa136a-bc0e-5a5a-9a4e-d5cfdbfbb73a | textbox | Serial No.:
0b129b36-2617-510e-8d1d-239965c3e2c5 | textbox | Next Service Due:
fd722a7e-1b44-49b2-8dca-944fab3e50f4 | checkpoint | 10
00d1ef19-3fff-5a6f-9efc-61ac6a5572f0 | textbox | Equipment Type:
b2505237-cc5b-5b99-9124-cedd489a9a47 | textbox | Manufacturer:
acadc640-a8b4-5a4a-a5e7-670f43768cbb | textbox | Model and Type:
ff9be98b-e8c7-59df-be3e-f202abfa122e | textbox | Serial No.:
332a9239-6935-59e9-9239-e1dee88df756 | textbox | Next Service Due:
4bcfbeac-ff66-449c-8f3b-7ad8362538ca | checklist | QA 15 - Pre Cast Slab Penetration Placement Checklist |  | Pre Cast Slab Penetration Placement Checklist
be7dcd95-dd91-4fb4-953b-3e4f5a31ca21 | checkpoint | Pre Cast Slab Penetration Placement Details:
194e75eb-24da-5a9f-af80-77e7e27315a2 | textbox | Drawing No. / Rev:
ce478967-9bba-5db8-b5db-f134e054f018 | textbox | Slab No.
e06c4a81-512c-5343-afdd-c4658455998b | textbox | Total: Sewer - waste penetrations
14b71c4a-befd-5b5f-bbc7-ada2a6f2d89b | textbox | Total: Stormwater penetrations
da3b9079-fb37-5070-a0ac-f749df254b84 | textbox | Total: Water
0257275c-bf86-5438-a733-d8fcafd9b304 | textbox | Other:
980e81e7-354e-4bbd-b07b-88dd97e72f84 | checkpoint | Geschke Representative Sign Off
0a06f72c-80d5-4042-bca7-dd9fa9dc9d1d | signoff | Request Sign Off
5c0d77db-0d20-45b5-94e4-8b9a4659b9f5 | checkpoint | Construction Company Representative Sign Off
a6a49bae-700c-4d26-956b-88e68dc3df64 | signoff | Request Sign Off
9f26b7af-4e78-41a9-8665-c20d317a9502 | checklist | QA 16 - PE Electrofusion Welding - Field Operational Sheet |  | QA 16 - PE Electrofusion Welding - Field Operational Sheet
ed9b9f43-afdb-48fe-a065-2a45c680bcd0 | checkpoint | Operator Details
ec404fa4-1fa4-5d15-866e-cdba7ba20990 | textbox | Name
b731af76-5568-5521-8244-3333295fc048 | textbox | ID No.
6158fdf5-eaf6-5b8b-aad8-7a201935f368 | textbox | Company
de11d1ea-1a08-53c5-8723-9b78263bf314 | textbox | Address
04f263ac-da79-4119-8d31-93667a1d8408 | checkpoint | Welding Machine Details
37608110-9840-5c1b-96fc-7a28510211f4 | textbox | Manufacturer
e268d098-97a1-5622-819f-4b0c50ec3185 | textbox | Type/Model
eba708ed-9189-5b02-9eab-a6655346fcfb | textbox | Serial Number
8341950a-b6c7-5a25-ba37-20b7c5eb2a61 | textbox | Year Built
3557af0a-d73e-4947-902d-55a7f93896e1 | checkpoint | Actual Pipe Size
d18d5664-dc97-5419-a431-5de3dfdc04f3 | textbox | Type
ecc17638-90b5-5cac-a7f5-11015e76419e | textbox | Brand
9cfd04f5-d395-5115-9695-5fcdad51819e | textbox | En
61b61cbb-ffdf-5eb2-bf41-9ffb37f5603e | textbox | OD
da05ebcd-c3b0-5e4c-b8b0-c9e27fb87eaf | textbox | Ovality %
b6437e00-e1a8-4aa5-b3a9-170ca57c9fda | checkpoint | Fitting Data
845a4462-fa0e-5028-aa25-b3ab3e125d0c | textbox | Brand
d7119c50-8b87-5145-96bd-a2c1f8c6afa0 | textbox | Type (Coupling, Tee, Reducer etc.)
1a4d57f9-cbf2-4717-959b-fad752358c25 | checkpoint | Unit Setting
11f996e4-0828-55c6-9bc9-d1bc7de87fbb | textbox | Manual
84e37238-1b15-5498-a58d-4159bda0eba3 | textbox | Automatic
a422f27c-8c48-4133-b6eb-779cee7495f2 | checkpoint | Preparation
793cb235-f7a0-58ff-8c49-34d3a544438d | textbox | Cleaned and Peeled
b96c9a2a-6527-53dc-89df-aab1bfb59a36 | textbox | Pipe/Fitting Clamped
5cc781df-20b8-4d93-b813-3c72ff2c556e | checkpoint | Welding Times
5190ff59-9a75-5fa1-af39-54e91688c417 | textbox | Joining Seconds
66e77fe7-8ac7-5aa6-b9fb-7f3c589e4681 | textbox | Cooling Minutes
329794ce-47e5-4867-a3b9-cf44c76afbb3 | checkpoint | Conditions
bf572a8c-fa5e-5e2a-b7ff-ee03c64e4f37 | textbox | Ambient Temp
7a1fe8e3-80ef-5fd6-b2db-8f9c60df7832 | textbox | Weather
439b00fb-e937-50f0-9feb-1d4a5e9a02cd | textbox | Preventive Measures
a322c255-89f9-4fa6-97f1-b4debcca37fe | checkpoint | Power
a8f13c70-4a3c-5d0b-b526-8b2b2f3ba78d | textbox | Mains
94931d68-3352-527f-b4dd-7d392fdd0ffc | textbox | Gen Set
b92fe560-5ffe-4d3d-a799-912d2a306369 | checkpoint | Operator Sign Off
abad7287-9a96-4982-8d63-1e9701038f14 | checklist | QA 17 - Water Meter Accuracy Test |  | Water Meter Accuracy Test
0576786d-43ed-4257-ad4e-5a43b0a2f53c | checkpoint | Water Meter Accuracy Test Details:
dd82a570-217a-5d1e-bca3-9bf8f4af3125 | textbox | Date:
c7e067a4-d314-5ed5-b4b7-d24db57d9269 | textbox | Project:
ed9c37e1-1d72-581f-bab6-c15669b2ead5 | textbox | Location of Water Meter:
9d060be2-2c22-5f7a-b7ff-c765876dd0fc | textbox | ID Number of Water Meter:
5c1e2b64-0d08-5c66-b6ff-b9a79857fb74 | textbox | Model & Manufacturer:
2d7e036e-00e9-5853-a7ba-25c2d7adc25f | textbox | Current Counter Reading:
300ea535-73fa-5060-90b9-c70fccfcfa82 | textbox | Zone/Appliances to be Metered:
7c4f0245-f9ab-5546-bd7c-cdd2e47035a2 | textbox | Pulse Rate:
1bab8ba8-87c3-418c-9ec8-2111f8131e85 | checkpoint | Measurement Apparatus
181ed9a4-4784-58e6-a188-b2071e85b5cb | tickbox | Bucket
f3b706d2-8001-5dc5-89b1-a810bd4293e5 | textbox | Bucket Size
e871c596-c4a4-51bd-b252-5b43330820f2 | tickbox | Water Meter
079d5dca-271d-5cd1-b81c-1b5c39d3feb4 | textbox | Calibrated Date:
c30a3f1c-f98b-567c-886b-a28f9daaa7a7 | textbox | Other
4ce6fa8d-ed84-4d8d-bebd-34f56751a5fa | checkpoint | Measurement Method
87208288-cf37-5f07-94d7-834e1f084daf | note | Isolate all fixings
a65665e9-6e95-517a-b614-e1d2ddda5622 | note | Place bucket at outlet of fixture and fill
da156aa2-4606-5431-b8fd-14c091bbb864 | note | Fill in completed counter reading and minus "current reading" to measure accuracy
92322ccc-4508-54fc-8e74-47d01dd13705 | textbox | Completed Counter Reading:
caa89c75-4512-5918-94ed-1103738dc3f4 | note | Accuracy
a2e481fa-cc52-5f30-986a-d6e97486b208 | textbox | OK
d254d3d8-6a71-5edc-979e-48c7089b9f6d | textbox | FAILED
c29151f9-834e-50b1-8c61-446eb32ffb68 | note | Replace Counter and Re-Test
50832aad-20fc-5563-b201-046fb971439f | textbox | OK
34375bcb-f422-5b2d-b89f-207720adaea4 | textbox | FAILED
589b79cc-ef6d-4634-a1fd-b961482ecbad | checkpoint | Pulse Check
e87986fb-8c0e-5e7d-b547-f2ae4fa8d963 | note | Method:
9b669773-5ddd-54c7-ac19-c091b81cec6a | note | Connect multimeter to the 2x wire connection points on pulse kit and set multimeter OHMS
ac63aff7-dd08-53a3-a143-c621cc3a5d27 | note | Turn a fixture on and wait for pulse reading on multimeter, then stop flow immediately
47497137-5995-5b9f-9249-5956c5efd8e7 | note | Measure bucket contents:
58b6f3e1-d809-50f6-9018-44d616777419 | textbox | Pulse Registered: |  |  |  | OK
1ab828f8-fdf7-584c-b040-a32b450984ce | note | No Pulse - Install new pulse kit and repeat process
687d871e-803c-57a5-aed5-3967000c85cb | note | If Pulse registered OK
14a7381e-c7bb-55ca-946b-fd6f1549dea9 | textbox | Pulse Accuracy: |  |  |  | OK
d194b284-b545-59e2-8241-916ae5d6a15a | note | (Bucket contents match spec at top of page)
ddd3042f-f026-57fb-994b-c94270b1dbcf | note | Failed - Install new pulse kit and repeat process
c8bdeaa7-b264-44a8-84e3-ca228f89f3b6 | checkpoint | Sign Off
10f1449c-fc86-5423-bd39-125e1b1a1070 | textbox | Name - Geschke Representative
8cc79509-cc97-4520-8c71-c4d747e077bc | signoff | Signature - Geschke Representative
ad51153e-fef8-4c58-bdc9-a34c96aa2884 | checklist | QA 18 - Gasket Installation |  | QA 18 - Gasket Installation
163de1c3-327e-4b30-af58-a2603ea5fe69 | checkpoint | Gasket Installtion:
1af59c57-6752-5bd1-bb63-85976252e637 | textbox | Location/Identification:
624829c3-34d6-5aa1-9d57-b7e9277db895 | textbox | Nominal Bolt Size:
5323c000-a961-5978-aede-c24b3e3da7dd | textbox | Gasket Contact Surface Finish on Flange:
9359b105-aa1d-5b63-a69f-965231420759 | textbox | Lubricant used:
7924bf92-0481-5703-b13b-9eeeb20bb59f | note | 1. Galvanised nuts and bolts – must use good quality lubricating oil on threads
b3e1d69a-fac4-58ff-a353-c41873227735 | note | 2. Below Ground Galvanised nuts and bolts– must denzo and plastic wrap full flange and cover bolts
6ea7e554-64d9-5015-a829-a2feebd43c52 | note | 3. Stainless steel nuts and bolts – must use anti seize / molybond on threads – must return 24 hrs later to tighten in sequence and required torque
57cfe5f7-6181-5650-8984-b6f30dcda026 | note | 4. Galvanised nuts and bolts on stainless steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
eba501c6-c128-5f50-a6a5-4298d2bcf0d7 | note | 5. Stainless Steel nuts and bolts on galvanised steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
88ef45dc-313e-550c-a9ac-3df1d2dc4f88 | note | 6. Zinc bolts, nuts and washers rust when used externally – use galvanised
61ded462-9cb0-4973-aae9-de95d482e7e4 | checkpoint | Visually examine and clean flanges, bolts, nuts and washers. Replace components if necessary. Alignment of flange faces is very important and maintain support of the flange, pipework and valve at all times
cab3c31b-90d3-45af-af9b-c4e7268ae855 | checkpoint | Lubricate bolts, nuts AND flange surface AROUND BOLT HOLES, not on flange/gasket surface, or use hardened steel washers. Use anti-seize on stainless steel threads and nuts or on galvanised bolts and nuts lightly oil with good quality lubricating oil. Insert bolts in locations 1 to 4 as indicated in the below diagrams.
ea9c5e9b-9e20-479f-9bc4-f8752e47235c | checkpoint | Install new gasket. DO NOT REUSE OLD GASKET, OR USE MULTIPLE GASKETS. Gaskets for water applications must be EPDM potable water gasket PN16 type. Gaskets for gas need to be AGA and GPL approved
f9c2c41d-670c-48bd-83e4-258574a64f7e | checkpoint | Number bolts in cross-pattern sequence according to the appropriate sketch below with a marker pen, black or white
40485a72-398a-4e1e-bc9a-fd260de228c8 | checkpoint | IMPORTANT! HAND TIGHTEN; then PRE-TIGHTEN BOLTS to 7Nm torque, but DO NOT EXCEED 20% of Target Torque. Target torque is required to be supplied by Gasket manufacturer / supplier – seek from GPL foreman
5c2b0c65-9603-4a65-a093-d1f5840163e0 | checkpoint | Check gap for uniformity.
1bc72e06-feec-4d54-98ed-12d75526df74 | checkpoint | Use the appropriate cross-pattern tightening sequence in the sketch below for Rounds 1,2 and 3 and/or Round 4 (each sequence constitutes a “Round”)
7fbd1bcd-3a61-44eb-8687-8f77bb65fbc5 | checkpoint | Final Torque
85b7b70d-336c-5050-8901-edd8bbe7e4ba | textbox | Final torque*: |  |  | (Nm)
53def9e2-a251-5f1e-b5ac-0fa021593f44 | note | * Refer to gasket manufacturer spec with torque chart on next page and GPL advice
b5a5ecac-624f-50e1-a1f7-c2a160ca6e42 | note | Lubricate, Hand Tighten, Pre-Tighten bolts (5% of final torque) (as mentioned in item 5 above)
b84986e6-2702-5d7e-aa50-9864cf3718f5 | textbox | Round 1 – Tighten to: |  |  | (Nm) | 1st torque value in torque chart* (20% of final torque)
d3bd60c0-9437-5ff1-aecf-0ac9d155b949 | textbox | Round 2 – Tighten to: |  |  | (Nm) | 2nd torque value in torque chart* (50% of final torque)
83e94b56-401d-5865-be23-16a9d3916fbe | textbox | Round 3 – Tighten to: |  |  | (Nm) | 3rd torque value in torque chart* (75% of final torque)
87bc77d4-6b8e-5f67-ae5e-868f01e9db9a | note | Check gap around the circumference between each of these rounds, measured at every other bolt. If the gap is not reasonably uniform around the circumference, make the appropriate adjustments be selective bolt tightening before proceeding.
4e1b585d-cc3f-55f2-92cf-0b8df2662c20 | note | Final Rotational Round – 100% of Final Torque (same as Round 3 or 4 above). Use ROTATIONAL, clockwise tightening sequence starting with Bolt No.1, for one complete round and continue by selective bolt tightening before proceeding.
1f0fd84b-0c5d-52be-babb-bdcac87b732f | note | Short-term bolt preload loss can occur between four to twenty-four hours after initial tightening due to bolt relaxation. Consider retightening to help recover this loss.
249f8cab-48f6-5dfa-93b2-1996c44e7fc9 | dropdown | Tightening Method Used: | Hydraulic Torque Wrench, Impact Wrench, Manual Torque Wrench, Other,Hand Wrench
ef8e83e3-629a-5048-a794-60f48e73ca58 | textbox | Other:
b4974c16-53e9-5d9a-b8c9-43acea0e99c4 | textbox | Where was torque information provided from:
8502f5bb-6aa4-51a3-aa96-91c30f8766ec | textbox | Joint Assembler Name:
9645b871-4146-4e9e-847f-88d108c9328c | signoff | Joint Assembler Signature
7d8103d7-2432-45a7-b599-a7853aca6b25 | checklist | QA 19 - Service Cross Connection Check List Report |  | Service Cross Connection Check List Report
e7c7f054-4913-4d52-8f36-bd7e49fbd025 | checkpoint | Service Cross Connection Check List Report Details:
305dddcd-d209-512e-a83a-f3ba180ad4ec | textbox | Zone/Grid:
c3f6285e-5b32-5046-a48a-42c8bd112fdc | textbox | Drawing No.:
ad942aaf-2a82-5679-9057-3105a810fedc | textbox | Rev:
b904fe9c-e734-4add-a09e-2972799a6a98 | checkpoint | Service to be tested
0c0291f3-dbfd-59e1-9e4b-60c835291ffb | note | Isolation of potable supply in general.
735c7515-bdbd-4a8e-a326-dc72db88d4df | checkpoint | Potable Water Supply
9c26d1eb-7a71-5f5a-86a1-764f7f9777da | note | Confirmation of service isolation at all fixtures.
38af6536-5189-5442-9b30-7afed1bca4d8 | note | Keep potable water turned off.
79405f26-472e-4d80-9ba5-91be1ffa52fd | checkpoint | Non Potable Supply
37b09699-40d3-5fe2-a5b5-0de1a3aef0f9 | note | Confirmation of water flow for non potable water supply at each non potable fixture while potable is still isolated.
dc36b7f1-81c4-4cdb-9aa3-c62ab2a7e0be | checkpoint | Turn potable back on
609a057b-8a29-51e8-b6d7-5b6786c5ebc3 | note | Potable back on
28814290-6a83-4eb9-97a1-ebef8c88e825 | checkpoint | Non potable supply
20c3282f-0fc4-549e-b445-69c023c03891 | note | Isolate non potable water flow and prove that each non potable fixture has no water flow.
4e34a58f-41c2-4822-994e-f13041e25948 | checkpoint | Potable Supply
0be594fb-5d48-54da-b783-b0cea341f8e5 | note | Check all fixtures that receive potable water are still getting potable water.
64a245b1-8b4e-416f-ae54-587d76061ff0 | checkpoint | Pipe Identification
06132254-7bc6-5f0f-8b9e-bf667d9a1ad9 | note | Confirm recycled water piping is identified by colour and labelling.
6daff378-ac78-4f11-a569-fb96fbe4e288 | checkpoint | Other
463aa5dd-33bb-4f85-b6df-901de5bfabc7 | checklist | QA 20 - Fire Hose Reel (FHR) Test Report |  | Fire Hose Reel (FHR) Test Report
6f552193-cbb4-4be6-8d51-7b274883bd98 | checkpoint | Fire Hose Reel (FHR) Test Report:
b8b1cd96-de62-51d4-be6f-6bf1236c21f2 | textbox | Location of FHR:
e4413c06-1560-5722-8acf-8b5d5a22f968 | textbox | ID Number of FHR (If applicable):
757981bb-51f3-5d9e-ad26-7c93f8d51c0a | textbox | Manufacturer:
782d8fc1-c596-529a-b7ec-705bbf30defa | textbox | Model:
f1ffb03e-ada9-5905-b4f7-829223030857 | textbox | Size:
25b0134a-c972-514f-a99a-3834964dcaab | note | Aust. Standard Flow Rate: 0.33 LPS @ 210-230 KPA
6b9ace36-7886-5229-bd85-8fe287b3c56a | radio | Measurement Apparatus: | Bucket
6cc078e6-57ad-50c4-832c-3796e776a0d0 | textbox | Bucket Size:
d7e1acd5-985e-566e-a38a-86bde0102462 | note | Measurement Method:
25118e21-73db-5c7b-85d0-c7660741dfb1 | note | 1. Connect pressure gauge and outlet to end of hose
8ef90496-a90e-528b-8edb-09ed5148c339 | note | 2. Note static pressure reading on gauge
d4a53c5f-6bf4-5120-be4a-bfc036c4bbef | note | 3. Place bucket at outlet of FHR and fill
1ab0bb3c-d12e-40f0-9559-ac8df58ee53f | checkpoint | Reading
bcada545-2dea-5c27-b0e3-27abb0c8ae35 | note | 3.3L
9ae7dbda-daae-51a2-849c-a4eea8e1e5d5 | textbox | TIME (sec)
33032a1c-ba0a-5b45-8e7a-02a184ff0679 | textbox | Flow Pressure:
a2bf51ad-fa27-5eb2-8d52-e0e29771eaf6 | note | 6.6L
4cf8b00f-e8c0-59b7-b8b5-893fc213d5b7 | textbox | TIME (sec)
b990106b-a24b-5ca6-95b1-3a02c2cc711d | textbox | Flow Pressure:
7544c1ca-4553-57de-9620-edca3f345906 | note | 9.9L
15c238ee-d9b2-5c48-8083-5db125244185 | textbox | TIME (sec)
9c20396f-3a26-5c6b-a75c-d22e68197d08 | textbox | Flow Pressure:
15c53562-950a-4293-a616-8c766cf71101 | checkpoint | Completion
5d74d8de-31b2-52b9-aff1-90a1fd1b07f8 | textbox | Geschke Pty Ltd. Representative:
2fe36308-4568-59b7-a523-8e0bca7f9d02 | textbox | Others Present:
7eb8fa85-d343-53ae-8064-81adf4069d59 | textbox | Date of Completion of Satisfactory Test:
45d5288c-abde-48ec-a6f4-6ff95d332e9f | checklist | QA 22 - Hot Water Service Maintenance Log |  | Hot Water Service Maintenance Log
fc01286a-8fd7-4901-8a98-d933cc72346a | checkpoint | Hot Water Service Unit Details
1dc36e09-89d5-51af-bc94-c4e61ff601a5 | textbox | Purchased from:
3889569f-333d-5278-b941-06888ca01593 | textbox | Make:
e7f3b2e8-6784-531a-bd4b-6a07a4a00830 | textbox | Model No.:
ba5ad87a-3168-5d20-a925-a4a2dff32d32 | textbox | Location:
6ada9a94-5924-5331-b481-fabe89ee05dc | textbox | Room Designation:
fe513441-698c-58e0-a2f0-6d3dd28ea02e | textbox | Installed by:
9e6f3057-b48e-5777-a757-a5685528a3e0 | textbox | Installation Date:
952dc2e5-2834-5159-b5ff-e7276393236d | textbox | Number of units in series:
6d7ad5ff-4088-5178-9179-ddb956fade4a | textbox | Prescribed temperature set on unit or combined package:
7062723a-2b9d-4c7e-9f84-d95fe5b38f9b | checkpoint | Does installation comply with manufacturer’s instructions
f2cb44da-f5b2-415f-9e45-718764a91549 | checkpoint | Does installation comply with current requirements of the local water supply authority
cf3d4ba0-f1f6-4aed-abf3-0cd5d0baa18a | checkpoint | Clean Pump Strainers
66e48676-fd74-4719-bfe1-c00493a514c6 | checkpoint | Clean Hot Water inlet Strainer
07c574e6-47d9-43f2-b82d-9d2196075c7d | checkpoint | Clean Hot Water Return Strainer
a39710e3-833e-4f5d-9aa4-34026c039145 | checkpoint | Confirm all Valve Isolation reinstatement
febdea56-ec8e-46e2-8bef-a67035b34e6a | checkpoint | Confirm Unit is Operational
cb495b53-2766-4f8d-ac9f-9b533f4ac0db | checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
8ce9f242-fd06-4077-b836-61d869dc560a | checkpoint | Commissioned By:
2df40c0a-6d66-5689-a7c8-b29469929431 | textbox | Name:
35d974e6-f234-5f2b-9714-c0711956ec38 | textbox | Date:
c055b039-2902-44bc-a50c-b11915a721dd | checklist | QA 23 - Boiling Water Service Maintenance Log |  | Boiling Water Service Maintenance Log
11ea6cac-ad98-4576-9860-708e10162a38 | checkpoint | Boiling Water Unit Service Details
2bef0f46-a468-5b9d-a883-2ac29ea644d6 | textbox | Purchased from:
0b174930-3aa8-5484-8426-d06d847ff7ba | textbox | Make:
02a07482-c192-506c-ac56-0bbf3050fe89 | textbox | Model No.:
d2df4809-13ab-53ea-8401-f3812c2168c6 | textbox | Location:
f4ef8d16-1b7b-5aa8-b600-0fc9eb695224 | textbox | Room Designation:
13cc7018-789a-5650-850e-65d9cc8d45f2 | textbox | Installed by:
0f80b1b9-c205-5922-a7d3-43ef6090d694 | textbox | Installation Date:
3d2d1cd9-198b-40df-a7f6-bb2fe79dd93f | checkpoint | Does installation comply with manufacturer’s instructions
e531bc96-0e73-45f8-ac95-87d565f0e689 | checkpoint | Does the installation appear in good working order.
caf4abd1-209f-4840-9d4e-77b36f79737d | checkpoint | Confirm all warning lights working correctly
878628fb-644b-4f09-b3c0-80a28e66d4d4 | checkpoint | Confirm filter is clean
7bb85470-c2ae-47d1-a38d-bf9bdf4bb3a2 | checkpoint | Confirm Unit is Fully Operational
ebea4f5c-45b8-42bb-85e5-35a565af6443 | checkpoint | Commissioned By:
7756d0ff-95b6-595a-869a-576fc70671b6 | textbox | Name:
6c95fe4a-026c-5d6e-a4ad-776c63702118 | textbox | Date:
880160ac-05d2-494e-a335-fc0a9e352a98 | checklist | QA 24 - Hose Reel Register |  | QA 24 - Hose Reel Register
83146a69-f514-4ad2-8c3d-f78c0cf26aba | checkpoint | Hose Reel Register
06ed3d58-8b0d-5bbd-b2db-f80a3a2f53b0 | textbox | Ref No:
edf955cb-2cba-5ad7-bbb1-c9de00888e6b | textbox | Building:
0ad7d9c8-91dd-50d6-a0b5-5603c8943644 | textbox | Zone:
54b7e781-f2d7-5ffa-a8a2-b7f996879af1 | textbox | Level:
4b2defe9-1b2c-53da-8cb1-83dfadb215e4 | textbox | Adjacent to:
6189004f-4444-5f17-9f6e-6f096f3800e8 | textbox | Length:
076b45e7-058f-549c-b146-e5918c1641c0 | textbox | Date Tested:
ac8bffe4-86cc-5ee2-a529-7519e13b974a | textbox | Flow Rate:
e35a15ca-1acb-5b60-b699-b6c509990e33 | button | Obstructed Access | No,Yes
038cd678-18a6-5df0-bfbf-70b374794044 | button | Operating instruction visible and legible | No,Yes
045bb13b-554e-5ac1-9e30-74216cb9c510 | button | No leaks throughout hose reel mechanism | No,Yes
f78d5501-c658-57b3-ae77-a20f0b187192 | button | Hose runs freely through guides | No,Yes
f02dd9ef-dfa9-5bd2-bbd7-4406883f7059 | button | No signs of corrosion | No,Yes
23384c99-a99c-4449-bd37-f3531004ca79 | checkpoint | Result (Pass / Fail)
b3c22abf-5347-4f95-b245-ea517f006db4 | checklist | QA 25 - Butt Welding Checklist |  | Butt Welding
63895bcb-8b84-49d2-a404-90f15a6bf9fc | checkpoint | Operator Details:
02f4dddc-1c12-5a16-9b1d-ba85dbfb9d33 | textbox | Name:
e6738561-8f3d-5b29-a873-5de819e4cef1 | textbox | Company:
b32c8194-44dc-53f6-af2c-471defb73fc7 | textbox | Phone:
efdf6bce-f735-5a20-a1c4-fa222199e2b3 | textbox | Address:
4522e1e2-846c-4071-af80-e08532bed67f | checkpoint | Welding Machine Details:
ab3d936e-0d22-5078-bf1e-fead02fd126d | textbox | Manufacturer:
93bfdc16-f91b-5ee0-b239-c233cde8a074 | textbox | Type/Model:
4d2f20e4-0a17-508b-bf01-6d1dbbdc02fa | textbox | Serial Number:
2fda1674-0101-569e-924c-810d7094bfa5 | textbox | Year Built:
44059f33-e399-4c7c-8530-094fdd41ba2c | checkpoint | Pipe / Material Details:
3f7f292b-1181-5d9a-8289-e85f7746d5bf | textbox | Dn (OD)
25c35a3f-bd74-59ad-8c9f-5a2f2cb91e3a | textbox | SDR
0aa6d1dd-aa62-5cab-ab5f-892ea3b537f6 | textbox | En
ff4fb2af-c8cd-5392-a4a7-2f75f0ead9c6 | textbox | Type
e3a007c3-fa2a-5eca-b1d3-edd85be2f29e | textbox | Parameter
dc295cc3-ac19-5074-ad33-9a238f796f7f | textbox | SLP
feab8b68-6b43-54db-84c0-19f57818b56b | textbox | SHP
f5ad7e01-f369-4e10-82e0-8f2494b08394 | checkpoint | 1
3766dc02-56a3-5188-a4a4-664207107e49 | textbox | Time
bf66520c-69b1-58e3-8886-6c7b149643e8 | textbox | Ambient °C
f21873eb-d3db-52ca-8a4c-bd96e6221373 | textbox | Heater Plate °C
0071f7b9-778c-54cb-bc22-2e4373147318 | textbox | Drag Pressure
e2af5016-16e8-5d9a-a7db-e0eab2ef3df6 | textbox | Bead Up: P1 (Kpa/Bar)
e6bf9cdc-f42b-5d9d-ad20-3a50cc1f1ddc | textbox | Bead Up: t1 (Evidence)
1a1e4242-a593-55c2-8ee5-c5f64b557fe6 | textbox | Heat Soak: P2 (Kpa/Bar)
81d2839b-ba20-52ca-bcfa-71457690b1cf | textbox | Heat Soak: t2 (Seconds)
6bfcbac6-0d71-5a74-8b43-3482a28677dc | textbox | Change Over: t3 (Seconds)
359a3baf-77f3-557f-818e-eac70b1b1d2d | textbox | Pressure Up: t4* (Seconds)
a8ae423b-a49e-5a72-b8e7-cef27aec0316 | note | *t4 not applicable for SHP situations
961a42a7-f339-560c-8971-52e07fdb8a1b | textbox | Weld and Cool: P3 (Kpa/Bar)
1ae6b147-3e61-53a7-ae19-31a6bfcc6fc6 | textbox | Weld and Cool: t5 (h:m)
40923999-e8cf-5b43-8236-cd25f0155781 | textbox | Rough Handling: t6 (h:m)
54ba7dce-7b2d-5787-a694-22295e0cc874 | textbox | Bead Size: Min
42f947dd-ab26-5afb-9d6b-e34829cec953 | textbox | Bead Size: Max
b772da3f-5ecf-599e-ad26-91c16d0b573f | textbox | Comments
70d6da23-82c0-4347-8435-100b6cde4bd9 | signoff | Add Operator Signature
aaa4f8c2-331a-4517-911a-8f0d79bd8e00 | checkpoint | 2
135bb77d-ff50-522c-9ade-64c089bc47d5 | textbox | Time
3f3ce538-cf00-56c3-9c30-3711efda550b | textbox | Ambient °C
5279e177-5f55-51e5-956f-30a954ec0226 | textbox | Heater Plate °C
6d0f5daf-f7e6-52ed-affc-b9015c27140a | textbox | Drag Pressure
47884875-e76d-52c6-8f10-8e2dd902d9e0 | textbox | Bead Up: P1 (Kpa/Bar)
1dffe9bb-7a4a-5f6e-a487-66e6f9cec3f1 | textbox | Bead Up: t1 (Evidence)
e74229f3-160d-5170-b549-7b22829dde54 | textbox | Heat Soak: P2 (Kpa/Bar)
d1455b29-f03c-5943-9e70-c62f1c36dd19 | textbox | Heat Soak: t2 (Seconds)
01675794-8b4c-526f-9746-293fdf899dfa | textbox | Change Over: t3 (Seconds)
6ecc6606-920d-5bce-adc9-963e7ad5880f | textbox | Pressure Up: t4* (Seconds)
f2976049-8abe-5d2e-bb22-1f3142f8e2a2 | note | *t4 not applicable for SHP situations
1591c889-ebf8-5980-ad56-5a4b30d6ddb1 | textbox | Weld and Cool: P3 (Kpa/Bar)
199e06d7-f0b8-5236-aa47-7b642b00094d | textbox | Weld and Cool: t5 (h:m)
4074de52-f1dc-57ef-ae7f-40991d7e241c | textbox | Rough Handling: t6 (h:m)
dc21d6fb-43bb-5ed2-b802-81194bcf5a69 | textbox | Bead Size: Min
ab7218a7-ed52-58aa-a405-57b4446389af | textbox | Bead Size: Max
5b745744-5f7e-5615-a979-8566d82da558 | textbox | Comments
585720fc-cfff-4894-a021-c98aebb94a72 | signoff | Add Operator Signature
47d322db-45fa-4689-8e7f-c76bf7161421 | checkpoint | 3
5878d00a-9270-5112-9b78-6c80808800a0 | textbox | Time
407d8204-7631-5c59-91e2-1b75450b93b5 | textbox | Ambient °C
f91530e2-2f35-58cd-93aa-410fd418d43e | textbox | Heater Plate °C
196fa7c9-0205-51fd-b0a2-35db1e163413 | textbox | Drag Pressure
4d04c9ca-12f8-5185-9165-ba3f7b0e9d48 | textbox | Bead Up: P1 (Kpa/Bar)
82e11993-c04b-59fc-99ec-d3141150a793 | textbox | Bead Up: t1 (Evidence)
820fd546-c325-5076-b250-3f008040d7f6 | textbox | Heat Soak: P2 (Kpa/Bar)
5746bc7a-bc35-52e7-9bf2-5c30670fe0ad | textbox | Heat Soak: t2 (Seconds)
fca46b26-54d1-521f-858a-d84fc8efc865 | textbox | Change Over: t3 (Seconds)
92a6cc04-93bc-5629-8a2f-df8b060a7c2f | textbox | Pressure Up: t4* (Seconds)
30ff0363-d043-507d-9ed7-3d17fc958506 | note | *t4 not applicable for SHP situations
07ab8d00-3ea2-5b73-af57-d54f30494138 | textbox | Weld and Cool: P3 (Kpa/Bar)
65f4a308-61a4-5dfb-9a4f-3313d99c2c05 | textbox | Weld and Cool: t5 (h:m)
84e4f02b-b804-5c33-ac72-1981392425e1 | textbox | Rough Handling: t6 (h:m)
84fae1ef-da17-59cc-a2a3-cd0f8a28d49e | textbox | Bead Size: Min
b7d24f57-40dc-51b4-9848-a6dc9c1f2c33 | textbox | Bead Size: Max
45099f02-a7fe-5f24-b16a-c21ba94c06cc | textbox | Comments
e79edf5d-158e-47e9-af99-b2c726665a07 | signoff | Add Operator Signature
7f722e74-7f56-4ab1-bd62-7fee88e72ba4 | checkpoint | 4
bdbdc777-d3e4-5023-aa90-aafbda248136 | textbox | Time
db6cb5ed-2b26-5a14-9483-bd99246d1f40 | textbox | Ambient °C
ed5aadb0-bc02-5148-b8a7-92a76221dce9 | textbox | Heater Plate °C
a91dd8dc-9fc7-592c-a261-5f6bd5c0c2cf | textbox | Drag Pressure
9e883bdd-9c02-505c-b859-7015bf312333 | textbox | Bead Up: P1 (Kpa/Bar)
36ed7075-c25d-5a8e-a190-0df0c384fec9 | textbox | Bead Up: t1 (Evidence)
f84b2a0f-6269-501e-afaa-7e8e8623ae79 | textbox | Heat Soak: P2 (Kpa/Bar)
3b51276a-fa0f-59d8-b501-947758dc88dd | textbox | Heat Soak: t2 (Seconds)
592d66e0-48c9-52c1-aa35-ac7b3c39db32 | textbox | Change Over: t3 (Seconds)
29b02a7f-1eb1-5434-bd70-b6ba4fdc0666 | textbox | Pressure Up: t4* (Seconds)
d08c0515-7d00-5ec4-be1a-45d1810d4a97 | note | *t4 not applicable for SHP situations
669d7e31-2da5-53b0-a01c-765873a28dbc | textbox | Weld and Cool: P3 (Kpa/Bar)
200a4c91-6b15-569e-a941-2b3e91dd8356 | textbox | Weld and Cool: t5 (h:m)
c82bd851-970f-5a71-b8a1-5bae89e20c5d | textbox | Rough Handling: t6 (h:m)
bf99f974-eee7-5dcc-91b8-dbf9fb3a7239 | textbox | Bead Size: Min
30a858d8-d6f2-503b-8438-31a9c1334409 | textbox | Bead Size: Max
22e3662a-51f4-5de3-a699-7c5bd62f073f | textbox | Comments
a8006ca2-b421-4722-b4dd-c2ced09c85d3 | signoff | Add Operator Signature
a8935b45-2b5a-47d4-8c7d-9a5d5f205760 | checkpoint | 5
74acf298-9e19-5ffe-95f2-5ada2a9a8cfa | textbox | Time
3948895b-2356-5ef9-9989-3e8c19d58400 | textbox | Ambient °C
92310b8f-08c6-5254-a888-c7fa8dbf8938 | textbox | Heater Plate °C
b72c8beb-e9c5-5569-8914-7c9dea8c35be | textbox | Drag Pressure
5d0e2989-dc85-5d0b-afd5-3623cc8d1b35 | textbox | Bead Up: P1 (Kpa/Bar)
948291c2-6c53-576f-9139-edc9bcf9f002 | textbox | Bead Up: t1 (Evidence)
a3c86e56-ab9c-5eeb-b38e-5fe3827d0102 | textbox | Heat Soak: P2 (Kpa/Bar)
7fd2907a-2153-5f49-978c-c96f3945aed5 | textbox | Heat Soak: t2 (Seconds)
53ce88c0-d238-5e8d-8521-93381d50ad22 | textbox | Change Over: t3 (Seconds)
2ec0d318-0063-5b2e-8fd6-89f3677176fa | textbox | Pressure Up: t4* (Seconds)
6f0e2256-c1a5-5afe-a40d-1d2e87151c67 | note | *t4 not applicable for SHP situations
12720e9c-2d46-5c43-ab52-7725e49d1a4a | textbox | Weld and Cool: P3 (Kpa/Bar)
ca6c70ef-6e37-5226-a96f-b405fbdbf301 | textbox | Weld and Cool: t5 (h:m)
31d1a5db-d3cb-5c24-88aa-8e7ebb533d2c | textbox | Rough Handling: t6 (h:m)
233696be-9373-5a68-872d-fa4b8dae0dd6 | textbox | Bead Size: Min
f297159a-26ec-5cfb-a484-40b3a28d3c13 | textbox | Bead Size: Max
25d54951-eb0f-513d-bf73-64b3a68ea777 | textbox | Comments
db32acfc-e6b1-4c59-8082-a91292dc6c5f | signoff | Add Operator Signature
8274942c-e600-4a64-a574-c726d243f350 | checkpoint | 6
6dfc23f3-1408-5124-b306-b6a3db334eca | textbox | Time
bea16f3a-bb3f-5ba8-869f-528d3787f492 | textbox | Ambient °C
0965759e-0a69-5fcd-9845-4fa359711af1 | textbox | Heater Plate °C
d7d6fe45-0d57-5a55-91c6-bda45150bc26 | textbox | Drag Pressure
f66788a2-cbec-5454-9dbf-5e4dabd27f9e | textbox | Bead Up: P1 (Kpa/Bar)
a7a2a540-434a-5530-8ba1-ae4084fe5a9d | textbox | Bead Up: t1 (Evidence)
9d853b82-d93e-5ee7-801e-bcfcdfd47706 | textbox | Heat Soak: P2 (Kpa/Bar)
b28d70a2-8e8f-5bbf-9016-25f0add685c4 | textbox | Heat Soak: t2 (Seconds)
e3e739a9-ac67-5ee8-905a-e2f60b68f503 | textbox | Change Over: t3 (Seconds)
56e4712f-982b-5497-857c-afb49f5086eb | textbox | Pressure Up: t4* (Seconds)
7bb33ea1-527c-59b2-9dcd-16f0c4f6a265 | note | *t4 not applicable for SHP situations
e13936da-0e1c-5208-aae8-684b1647b0e9 | textbox | Weld and Cool: P3 (Kpa/Bar)
ee302b32-3c45-54f4-9b7a-b18d9d013042 | textbox | Weld and Cool: t5 (h:m)
b67dfc1e-2792-5485-94dd-a9271e7cb83b | textbox | Rough Handling: t6 (h:m)
7144da0f-2a29-5070-b0ec-42b3a181dfff | textbox | Bead Size: Min
380e17e0-6686-5ac5-9533-c627b29eb874 | textbox | Bead Size: Max
7fea72c2-f356-59b2-a64f-e1dc53872378 | textbox | Comments
d33ff667-8f29-4b03-8748-929216635cfe | signoff | Add Operator Signature
cbb65417-db20-42cd-aeb9-ad13c4380cbf | checkpoint | 7
03e023fb-eb22-55c6-b72a-d4ff9f74f4cb | textbox | Time
da20d136-f74d-5be3-80a4-e86829d3e3ee | textbox | Ambient °C
9deb30c8-591e-5810-b997-628ff36f1393 | textbox | Heater Plate °C
e8e772b4-20cc-5531-8317-5a0dbd9924bf | textbox | Drag Pressure
cec7842c-d746-5399-8db7-66a025cd5cfb | textbox | Bead Up: P1 (Kpa/Bar)
3a26ec9e-223c-5b9d-a1ae-ad34f4d87c4d | textbox | Bead Up: t1 (Evidence)
06657ed7-04ba-596f-876a-70e517ec1c8e | textbox | Heat Soak: P2 (Kpa/Bar)
f71f255a-4b0b-52fb-af1b-c3c9d1250c08 | textbox | Heat Soak: t2 (Seconds)
74560db2-7498-5f64-a256-b6ebccb96743 | textbox | Change Over: t3 (Seconds)
4d4917b9-9622-5164-8f65-9f51bd1b2313 | textbox | Pressure Up: t4* (Seconds)
78ee33c8-c871-5a92-b843-06913f3b1a9b | note | *t4 not applicable for SHP situations
f82eb451-4397-5df1-8630-b013654be346 | textbox | Weld and Cool: P3 (Kpa/Bar)
5c4e322d-aaf3-59c2-8f45-93bd291ad274 | textbox | Weld and Cool: t5 (h:m)
805b306c-6ffc-5a33-80ab-60239fab5dc7 | textbox | Rough Handling: t6 (h:m)
afe8fe3b-3cf6-526a-b22a-1931ef4c465d | textbox | Bead Size: Min
5a63aa6d-8f73-52eb-8aeb-6cb319ab714c | textbox | Bead Size: Max
c9975607-fd8c-5434-85bf-d7b230770a7e | textbox | Comments
95c9bb88-6aea-47ca-8396-51fcc1f67f9b | signoff | Add Operator Signature
6db9650e-d876-419c-b38d-ceed7389eb66 | checkpoint | 8
da97e04c-3756-5f6e-a3fd-eef4c72c8d05 | textbox | Time
0340fd6e-8ed5-5f5d-8d27-08f9f5e1740c | textbox | Ambient °C
3f5770c1-e5c5-5d8b-9c86-62466d1d8b0b | textbox | Heater Plate °C
9e9e5989-f904-5cbb-8c62-215d658016d2 | textbox | Drag Pressure
11b9d25d-a403-50f4-bae3-9803e1206dcc | textbox | Bead Up: P1 (Kpa/Bar)
fc4fa360-4503-5783-a47a-789d26c65a75 | textbox | Bead Up: t1 (Evidence)
fcd520aa-2775-5b84-b103-61a3efefb1f9 | textbox | Heat Soak: P2 (Kpa/Bar)
f5cf3143-52bb-5f62-ac84-3848cfd9476b | textbox | Heat Soak: t2 (Seconds)
cd639e0e-fe17-5525-a9c2-dec5ca889417 | textbox | Change Over: t3 (Seconds)
b726985b-2ba5-5bfa-94de-8cb6ab270150 | textbox | Pressure Up: t4* (Seconds)
72daaba3-569d-5315-a30f-24707291d2e3 | note | *t4 not applicable for SHP situations
5e479c54-8ecc-57ce-9793-8e68498a912b | textbox | Weld and Cool: P3 (Kpa/Bar)
783a9e9c-3291-5e22-b8cd-1e266e011f73 | textbox | Weld and Cool: t5 (h:m)
55c70bb1-2434-5a62-a7db-d1de45f46f83 | textbox | Rough Handling: t6 (h:m)
1558da49-efaa-5b0b-838d-9466f87549aa | textbox | Bead Size: Min
e1f137b5-5e2f-579c-971b-7349cee606ac | textbox | Bead Size: Max
092a86ca-7cd1-5619-9873-1f5d601bb74f | textbox | Comments
6433988e-a28e-4f63-b2cc-03f88cc48377 | signoff | Add Operator Signature
cbeafb02-42e2-4823-ab98-cae9222d72ae | checkpoint | 9
e9c98848-0fdb-54d4-afec-8530e6135564 | textbox | Time
e0335c20-6346-50f8-a931-3778e1c427cb | textbox | Ambient °C
dc0d9ccf-e8c6-57fb-9308-03ebc97b8f08 | textbox | Heater Plate °C
3f3e060e-661a-5b70-83ba-664184bbfba7 | textbox | Drag Pressure
a0762402-3e37-59bf-bd33-f47605778237 | textbox | Bead Up: P1 (Kpa/Bar)
916684a5-c190-5879-bfc1-5ff0b64d534e | textbox | Bead Up: t1 (Evidence)
9f6b2cbc-03a6-5eb5-86fe-7353942b97de | textbox | Heat Soak: P2 (Kpa/Bar)
3d427f7f-fc9b-5a0f-aadd-d1a36287e987 | textbox | Heat Soak: t2 (Seconds)
50b07ac9-40a4-5d9a-a982-c88f6a60db98 | textbox | Change Over: t3 (Seconds)
766fbff3-5df3-5e1d-9924-bf314efdf5e2 | textbox | Pressure Up: t4* (Seconds)
972528b6-c0a4-5f3c-93a9-e24c11b3eee5 | note | *t4 not applicable for SHP situations
fb2308a2-ce57-587a-9e18-f2f1fbf900f7 | textbox | Weld and Cool: P3 (Kpa/Bar)
04abe229-ffe1-5400-91f3-ee38d2e4a968 | textbox | Weld and Cool: t5 (h:m)
38762975-5124-5bc9-ac6f-6a860e82bbb5 | textbox | Rough Handling: t6 (h:m)
dfa0988e-8373-5718-8bae-88446e9f0626 | textbox | Bead Size: Min
ec63a3af-e744-5443-9592-1c043b463b6d | textbox | Bead Size: Max
a3b9783c-e2b8-561e-8eb0-cd69b4ac4091 | textbox | Comments
b61d9290-2a45-419c-bd4d-81c0c662c618 | signoff | Add Operator Signature
99c81061-fce0-46f9-aaa2-f65adbcf4107 | checkpoint | 10
d57c60a7-8c59-56e0-b7c4-0bed2846c994 | textbox | Time
ba1c1097-0327-5023-825b-609a9f17172c | textbox | Ambient °C
b04d2c59-f0e9-51cc-a629-6d81f4ff47a0 | textbox | Heater Plate °C
feeed46a-db95-520e-bf88-951ddfc6a2ec | textbox | Drag Pressure
dcbbea23-94d3-5825-bdb4-3886c7e587ee | textbox | Bead Up: P1 (Kpa/Bar)
eeadb864-32f0-5853-b541-e5aaf14a22c8 | textbox | Bead Up: t1 (Evidence)
73e54b61-046c-5607-ac2c-f15a7a7055ce | textbox | Heat Soak: P2 (Kpa/Bar)
b233c84f-c4b3-521b-a5f8-d339a39e1620 | textbox | Heat Soak: t2 (Seconds)
d620501c-3139-5ff8-8392-2d8cea844a47 | textbox | Change Over: t3 (Seconds)
33fbcf72-6448-5496-bfc5-f0217453209c | textbox | Pressure Up: t4* (Seconds)
996e99f8-14d5-564c-934c-41e96e1c1018 | note | *t4 not applicable for SHP situations
c0093d0c-c8e3-5e84-bda6-7234533438e4 | textbox | Weld and Cool: P3 (Kpa/Bar)
ec0b4948-8a7f-524e-86cf-aeaa66d7674d | textbox | Weld and Cool: t5 (h:m)
284cb23d-a975-51ce-abf0-5b1d4a4c55d0 | textbox | Rough Handling: t6 (h:m)
0dde0aeb-a6a9-54b0-b0bd-a23f7e0e6ef8 | textbox | Bead Size: Min
030b818c-9384-501d-96a6-9cfa7d7d04b2 | textbox | Bead Size: Max
d79731ae-1228-55b8-97e2-e85e57898fe2 | textbox | Comments
cdc9be70-4442-4a58-b5a9-7031a2368aa5 | signoff | Add Operator Signature
11227531-7218-4f90-bd04-6e6a7a6a48db | checkpoint | 11
e27c33c6-6679-545d-bc82-36dad9117989 | textbox | Time
b9ebac07-aa52-59f0-a39d-35acd793f9d2 | textbox | Ambient °C
4d9dcbad-343d-574c-8ba3-5113b92cfc76 | textbox | Heater Plate °C
f6641e7b-802e-512c-8529-0d07920afc2c | textbox | Drag Pressure
2bc929e5-ce70-5191-9458-8c611c1928ff | textbox | Bead Up: P1 (Kpa/Bar)
d5ea948f-5a02-5cd3-b467-82ce6abf6c61 | textbox | Bead Up: t1 (Evidence)
454deb95-82a2-553a-aacd-18d5f22d2895 | textbox | Heat Soak: P2 (Kpa/Bar)
b3771b1e-370c-56fc-a791-785b696d4536 | textbox | Heat Soak: t2 (Seconds)
f912734e-1e70-5b32-8e2e-5441ac1c6d3b | textbox | Change Over: t3 (Seconds)
c0c2b7c4-0f2b-5ad9-a3b8-5a13d2e4c276 | textbox | Pressure Up: t4* (Seconds)
e10a624c-6b99-55e3-ba6b-905f445efb0a | note | *t4 not applicable for SHP situations
5f81f397-bdf9-5991-9f78-31e89fa9e1cd | textbox | Weld and Cool: P3 (Kpa/Bar)
1a4f2011-c291-5c50-9642-f8c472e2547a | textbox | Weld and Cool: t5 (h:m)
bc5c50da-5e50-5fdb-a0eb-165e2b938d29 | textbox | Rough Handling: t6 (h:m)
43e9f834-33cf-59ea-994c-6957f700a7e6 | textbox | Bead Size: Min
a7f69eb4-1333-51e1-a142-46ebd5d4e2a6 | textbox | Bead Size: Max
1ec159f2-c31f-518a-ab71-e3edb883b95c | textbox | Comments
841478f7-e07d-40e7-9cfb-72c13ba1fdea | signoff | Add Operator Signature
b7ed22b8-1e1b-46b0-bee7-0207b3b569b3 | checkpoint | 12
84579679-fb89-5558-bbd2-9df7674bd611 | textbox | Time
32d108ae-db9b-586b-a808-1ddd385c3981 | textbox | Ambient °C
da829275-9eac-5028-8b4c-ebcee46f0c5b | textbox | Heater Plate °C
1c438ca2-8cb5-5ce4-bd27-0b9d6f37318d | textbox | Drag Pressure
f0302998-9f0e-5a52-b046-c6b47bd7735e | textbox | Bead Up: P1 (Kpa/Bar)
e6d7f596-9296-50f7-a36f-4f98f2a7d0fe | textbox | Bead Up: t1 (Evidence)
cf518e76-eed2-53a0-9b5c-b3a7fda2ec33 | textbox | Heat Soak: P2 (Kpa/Bar)
dbcde07a-4853-52b0-a44a-8dc484f11af3 | textbox | Heat Soak: t2 (Seconds)
4db5bc3f-4994-507f-8dfc-bc9e9ce14eac | textbox | Change Over: t3 (Seconds)
f2037066-9f83-5ef0-8465-b2906802fa5c | textbox | Pressure Up: t4* (Seconds)
c40545ac-b3b4-536d-8aa1-dff080177030 | note | *t4 not applicable for SHP situations
b31b7f68-07e7-5f69-beb4-49db347a5b39 | textbox | Weld and Cool: P3 (Kpa/Bar)
8f83be78-ec32-53e2-a1f4-afa61c4e6bb6 | textbox | Weld and Cool: t5 (h:m)
ef774acc-1bf9-535f-ab9f-1ee85ddb75c1 | textbox | Rough Handling: t6 (h:m)
e8f92338-5d31-5ef1-86d9-5eb224c0203d | textbox | Bead Size: Min
50deefb3-42a4-519d-862e-af8194d8d548 | textbox | Bead Size: Max
20545b50-d69c-52b9-8432-1f2c8b18f9f4 | textbox | Comments
32130ef7-3c65-46c1-84c2-4a5fe69f407a | signoff | Add Operator Signature
2192c166-083a-4eb3-8358-5147dad4b903 | checkpoint | 13
16eca773-9635-5a38-9d89-1376f8f34d22 | textbox | Time
18d4d8bb-8051-5b8d-afc8-8e9fcf82b980 | textbox | Ambient °C
df802b7a-94aa-568a-8970-45d88d1ccfb7 | textbox | Heater Plate °C
96568c96-5d4c-5702-bb00-b9f4b689a17c | textbox | Drag Pressure
91b8adb7-f54d-559d-b3db-d5cd32990729 | textbox | Bead Up: P1 (Kpa/Bar)
d6a7140a-df60-5406-9d8a-efc0cb456071 | textbox | Bead Up: t1 (Evidence)
ff9b3560-1e99-532e-b868-c6e2e0b02726 | textbox | Heat Soak: P2 (Kpa/Bar)
3afe6554-027a-55a8-9cab-22984004d292 | textbox | Heat Soak: t2 (Seconds)
55b27fd1-0bbe-53b5-ada0-768db4ff7685 | textbox | Change Over: t3 (Seconds)
719f7ab9-f25c-51ca-896a-aac66843e3df | textbox | Pressure Up: t4* (Seconds)
074178b7-39a0-52e3-8e05-38756e878832 | note | *t4 not applicable for SHP situations
8be41b18-29d9-5a96-a785-a81c61433f69 | textbox | Weld and Cool: P3 (Kpa/Bar)
0b6e5712-0084-5d26-9dad-4d60f2205347 | textbox | Weld and Cool: t5 (h:m)
2dca7bf1-058e-577c-8a99-fe49272389df | textbox | Rough Handling: t6 (h:m)
3ecb8c12-5f12-5938-a8c5-affe7e2d5e35 | textbox | Bead Size: Min
ebf38b58-f26e-57a3-a8b2-9c907f102c18 | textbox | Bead Size: Max
c974d9c2-45a4-5b4d-9f53-02c22126b7a3 | textbox | Comments
afe8486a-c7fd-4f34-b926-806b6b0a2377 | signoff | Add Operator Signature
1294cf54-ec47-4d54-bde5-29369382935e | checkpoint | 14
a2a21cdd-6326-5518-af67-32e0c9ff67bf | textbox | Time
7646a5aa-6159-56af-b040-c33d747ec25d | textbox | Ambient °C
264d6db8-e893-51f5-acd0-315e3fa7d956 | textbox | Heater Plate °C
ec54c77c-ee8e-57ec-b326-4419ea3152d0 | textbox | Drag Pressure
98024807-322f-54b8-a8bc-38ed894faef9 | textbox | Bead Up: P1 (Kpa/Bar)
f6ec7b29-4340-58c3-af5b-a2eb17b6e01f | textbox | Bead Up: t1 (Evidence)
d8ac01cf-222e-5b5d-83a7-0970f82a0aaa | textbox | Heat Soak: P2 (Kpa/Bar)
c570a78e-c0c1-52a2-8689-d44451d00db0 | textbox | Heat Soak: t2 (Seconds)
3dbbe1df-c598-50c3-af1b-4a83ad4beb48 | textbox | Change Over: t3 (Seconds)
a963481c-1887-5725-921b-dca861c7a42c | textbox | Pressure Up: t4* (Seconds)
570193ef-36b7-55e8-ae39-797cfa20c08b | note | *t4 not applicable for SHP situations
fb374fef-0ec7-5365-b23b-e6b6c1b9c3a3 | textbox | Weld and Cool: P3 (Kpa/Bar)
b7292f9b-165c-5db6-a549-c03988946b8c | textbox | Weld and Cool: t5 (h:m)
a95d4724-892a-52b2-a03e-2c6801edd7ff | textbox | Rough Handling: t6 (h:m)
4660fbdf-8c7f-5f7f-b278-58cdffc39aee | textbox | Bead Size: Min
a8211d69-74c5-5341-83f7-b4885e62350d | textbox | Bead Size: Max
b135b75d-b34f-5e4b-aa35-74095aa90914 | textbox | Comments
6a6bae58-fb27-4835-bada-7ded1fa62e3f | signoff | Add Operator Signature
5ca8eb2d-2a01-47b6-b63b-4a1b7a56ed61 | checkpoint | 15
12314806-f17b-5416-8322-5227c68c7dc5 | textbox | Time
469a40e8-a416-5229-91f8-e8b35390a2ef | textbox | Ambient °C
6ea3a97d-cb41-574d-95a4-2de79b25a730 | textbox | Heater Plate °C
d607f14a-4696-5af3-9dec-68958d2bb0a1 | textbox | Drag Pressure
a0903ac4-ca26-5ea1-b852-2a870a43c168 | textbox | Bead Up: P1 (Kpa/Bar)
68691c9b-5aca-54df-bcac-1e0013ed6e82 | textbox | Bead Up: t1 (Evidence)
1f89bab0-b2a9-5664-86ad-3eeaa7c8a2f5 | textbox | Heat Soak: P2 (Kpa/Bar)
1644c3de-229a-5726-a5f0-4e7a7ed797d0 | textbox | Heat Soak: t2 (Seconds)
0dc50850-6872-57b4-bc65-9d1f32bad375 | textbox | Change Over: t3 (Seconds)
ba0b4566-0999-5a70-8b2b-1972db897538 | textbox | Pressure Up: t4* (Seconds)
57437549-8e65-553b-86b1-b24ff288794e | note | *t4 not applicable for SHP situations
976eca24-9309-538c-ad11-5eedfc27227b | textbox | Weld and Cool: P3 (Kpa/Bar)
e64fe706-bf25-5937-89b8-305fe26de978 | textbox | Weld and Cool: t5 (h:m)
77ef1f42-cb3c-5542-950b-e591d46554c8 | textbox | Rough Handling: t6 (h:m)
f6a42f75-0403-5452-902c-396bcc08c89d | textbox | Bead Size: Min
4f6192d8-450e-5c38-b249-95b829fbc483 | textbox | Bead Size: Max
30b1f49e-e0d7-5c77-a198-40d45053ab43 | textbox | Comments
1a901cfc-74ed-412f-a3e7-831246d6c92e | signoff | Add Operator Signature
a0ecb133-5a04-43fe-b444-0047d70140d0 | checkpoint | 16
4c6be8b6-8a0b-5df0-ae5f-2f1a933f6c29 | textbox | Time
dc81647e-0bd4-59d0-9bbd-2f34f8a33f72 | textbox | Ambient °C
4fa676d0-0225-54a2-9dc4-2b09bb848de8 | textbox | Heater Plate °C
2e13738c-5bad-5eea-955c-1c8522c3787d | textbox | Drag Pressure
9f205079-714c-53c4-b120-6efb2d137b7c | textbox | Bead Up: P1 (Kpa/Bar)
8e94a2e9-2e3f-5ca9-8e35-9842d2d6d24a | textbox | Bead Up: t1 (Evidence)
2ea29db8-b19a-5ba2-ac73-71cd9d566a44 | textbox | Heat Soak: P2 (Kpa/Bar)
77efe883-c9d3-5cc2-9341-7c3bdf9ceaef | textbox | Heat Soak: t2 (Seconds)
e29aee62-015e-523f-afbf-2cb78354038d | textbox | Change Over: t3 (Seconds)
6f59a524-db95-540c-a156-6ab3797de5f6 | textbox | Pressure Up: t4* (Seconds)
429c374a-17b8-5fe8-872f-19cf76bfe5f4 | note | *t4 not applicable for SHP situations
07dbaba5-5d12-5459-83a9-1787e2af3046 | textbox | Weld and Cool: P3 (Kpa/Bar)
3ef2012f-b74d-510c-92e1-bf0fddfc1866 | textbox | Weld and Cool: t5 (h:m)
4fae6ac4-9e3f-5457-ae70-1558a94425e2 | textbox | Rough Handling: t6 (h:m)
cb9d0f21-0f49-5747-9727-5694a3b9e981 | textbox | Bead Size: Min
090e7c9f-f1fa-5dbd-90d0-fc93f2007ec6 | textbox | Bead Size: Max
e50b9911-cf13-50ef-a418-5eb5c255fe42 | textbox | Comments
eff679a5-e98b-4353-b28c-98d5d75bceea | signoff | Add Operator Signature
de83a865-28ed-4051-9c23-5f77d656afdf | checklist | QA 29 Periodic Flushing / Copper Protection Test Sheet |  | QA 29 Periodic Flushing / Copper Protection Test Sheet
ce276f02-fb09-44e9-a280-feb568151edb | checkpoint | ITP QA 29 Periodic Flushing / Copper Protection Test Sheet
ab8fa540-30b6-51d6-bde3-523d57855133 | note | Copper systems are failing in the construction industry due to stagnate water being left in both hot and cold copper pipelines. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water. Periodic flushing of the systems is the only way to ensure this occurs.
50e1ef80-c2bb-5f4c-b247-235f10e19ac9 | note | The purpose of this ITP is to help you create the strategy to get this water out and replaced with fresh water every four weeks.
2d0a7326-2799-4fe0-983d-9b1e7639229a | checkpoint | Flushing Details:
78f33702-192a-5ad8-8f30-4932150e18b8 | textbox | Level / building being flushed:
f26dc47f-408d-5149-ae79-6c3de58b9f0a | radio | Time and Type of flushing: | Ring main –Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush., Non ring mains – Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)., Short branches of copper that feed rehau do not need individual flushing., Multi storey projects will require flushing on each level. Starting from the top and working your way down
b93e43d8-e685-5b29-b557-ae510bfad550 | textbox | Which fixtures are being used to flush the system (Point of connection and point of discharge):
83d9b7ff-a027-5291-9213-f3e873596164 | textbox | Start time of flushing:
dea240dd-ca78-5273-98bb-fe41e7a64d8f | textbox | Zone/branch to be flushed:
78ed448b-8202-5a38-84e1-5720c456eb51 | textbox | Finish time of flushing:
8054e604-4eda-5b44-af75-ca957468c1d2 | textbox | Zone/branch to be flushed:
004e008d-7566-4fa9-9d7c-f90e147c8e5c | checkpoint | Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated.
859edbb5-6aa3-40e8-90f1-1660b1e80df7 | checkpoint | Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case.
8e196e73-5abb-4909-936d-de94870bc742 | checkpoint | Have you set a reminder for the next flushing of this pipework?
c2a0e651-5b65-4b46-af1e-33526b0cebe9 | checkpoint | Have the hot and cold been interconnected for flushing purposes?
198f55f1-8ef6-4156-8e8d-dfbc13ed6fe2 | checkpoint | Date for next flushing (Flushing to be performed every 4 weeks):
ecec82e2-54f1-574e-a23e-889fb5a4dfaf | textbox | Date for next flushing:
699e071e-e11a-51e0-ac02-5c5129b858b6 | textbox | Test completed by:
be07a026-0dac-5673-a301-553fac141bbc | textbox | Builder Representative:
e0d0fe79-c08f-4c04-9bd6-53ddc56df2b4 | checklist | QA 30 - Fixture/Hydraulic Installation |  | Fixture/Hydraulic Installation
1a4a51d3-b119-47b1-b2e7-b616ce079a4b | checkpoint | What is being installed?
20c22c42-9cb8-45fb-b6b0-eac0685c5f61 | checkpoint | Where is this fixture being installed?
e2d3153c-b0b6-4495-aa75-0e369c7bea81 | checkpoint | Have all parts been connected/completed and tested? If no, please detail why?
4cea9b84-f33d-4920-a1e8-d8f7b461f571 | checkpoint | Has photos of installation been taken and uploaded?
1072155e-437b-4803-9a01-62431d973781 | checklist | QA 31 - Hot Water Service Maintenance Log |  | Hot Water Service Maintenance Log
d5b12f01-b38c-4d19-91ef-d0fc236f7d61 | checkpoint | Hot Water Service Unit Details
530b0310-c07a-5e80-a070-17b007e2a342 | textbox | Purchased from:
5777de97-52ea-5d6d-9df7-0525d3bb456c | textbox | Make:
5d0df250-df55-59cd-9c88-940cdffc4801 | textbox | Model No.:
3599a2ae-89e8-5d0a-8764-82f14d50e1bf | textbox | Location:
2f466ca3-d412-5da4-bbb4-82a78c443466 | textbox | Room Designation:
ad0b22f6-1b34-57ba-b49d-e20744bc3a4e | textbox | Installed by:
bd161c82-c71c-5b5c-a443-578529cabb20 | textbox | Installation Date:
f4626429-f6e2-569b-959b-984f89df20d8 | textbox | Number of units in series:
d309a8b0-92c5-5471-9805-6b3a821dff73 | textbox | Prescribed temperature set on unit or combined package:
3159a86c-34f8-4a62-8642-d575c52cf7e7 | checkpoint | Does installation comply with manufacturer’s instructions
c2ffc510-7955-4138-bdc6-8de813b4ff26 | checkpoint | Does installation comply with current requirements of the local water supply authority
07149d27-f642-4d2b-87c2-d2b11fc6c848 | checkpoint | Clean Pump Strainers
8effe75a-c6ae-43c8-b965-263ed29735ae | checkpoint | Clean Hot Water inlet Strainer
d4418b37-e91e-4b3e-8b44-34c42947c495 | checkpoint | Clean Hot Water Return Strainer
69ab73dd-d45a-4759-9772-f7fe408cf5a3 | checkpoint | Confirm all Valve Isolation reinstatement
a3b59e64-20a7-4435-80ce-cdc057594bd6 | checkpoint | Confirm Unit is Operational
6a74a191-61fa-4f88-8279-8b7daced3e2f | checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
867546ed-45ef-4efa-9ccf-1091c1b6e658 | checkpoint | Commissioned By:
5cdb323c-1c08-5fbb-99f8-2d1cb4c4943f | textbox | Name:
ad2612fe-e8b7-5f6e-a1c4-d57461472062 | textbox | Date:
33e7246b-556c-4848-8a51-ee2edaf40075 | checklist | QA 32 Installation of Underbench Boiling Water Unit |  | QA 32 Installation of Underbench Boiling Water Unit
f08d542c-7969-4644-9191-28ca63078515 | checkpoint | Location
9199cd80-41c2-5f62-86d3-d11932284780 | textbox | Building ID
97e6cbc1-451f-537c-ab65-700aa5cf77fa | textbox | Level
e517bb52-4585-588d-a53b-2a7914da136d | textbox | Room ID
4d6a0ee2-6cee-4e04-9529-68e25a6771cd | checkpoint | Unit Details
a12bf4e0-92fd-5123-a3c9-c24b40df54da | textbox | Brand
c0ef449a-e7a4-5314-bd15-a56ca7324478 | textbox | Model
87f357ca-c238-550d-a781-2eb2937a82a6 | textbox | Serial Number
b5512fde-909b-4006-afc7-4260e5c2525b | checkpoint-no-value | Installation Date
0197c378-b8d0-5c7b-8762-c274ecbb44c1 | date | Installation date
9a2cbcaf-dbe2-45b7-93ea-33ab6b481bbb | checkpoint | Photos
8b53aec8-236d-5344-b8e4-b0e5b97d6286 | note | 3 photos attached
00f7b133-e983-41af-aace-ead478a739b4 | checkpoint | Installed By
28fd7046-483f-5013-876d-8c606f35025a | textbox | Installed By
faace53a-e872-47ac-a2e0-4b6cb901bad9 | checkpoint | Builder Sign Off
074e01f1-5c19-52f8-8078-5f2be8794784 | textbox | Name of authorised person
10c9bf62-19c1-56a2-9eb9-34dd979b4294 | date | Date
013d6904-8899-4534-bbcd-441b24127676 | signoff | Add signature
6049ab2f-1a8c-4300-8de8-b69bcc5c162e | checklist | Safety Shower Functionality Audit |  | Safety Shower Functionality Audit
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
63922fd5-3fab-4270-bad8-3925ed035d85 | checkpoint | Accessibility
ade15d58-3790-50bf-a1f7-e2db69a2ed84 | note | Is the location of the product in an accessible area, eg, no more than 10 seconds away from the hazard and has a clear path leading from the hazard to the safety product.
6d285995-8afc-411e-af70-c587e557dcc9 | checkpoint | Identification
8d32269b-ab8b-5ae7-8edf-574f866dae2a | note | Is the safety product clearly identified with appropriate signage visible from the hazardous area
0d83adeb-57e8-4686-8959-267f30882c9f | checkpoint | Support Brackets
235b9724-eb88-5e17-bc8a-5b68d304cbe2 | note | Is the safety product securely fixed with corrosion resistant anchors and brackets
671313eb-ec08-42d1-9f86-1202ebc5fcd2 | checkpoint | Installation details
e309fc77-6df0-5306-8406-470601acb326 | note | Is the safety product installed at the appropriate height
c5ba7b43-4dd2-4209-a6d4-598d4f7a8dc4 | checkpoint | Exterior and operating instructions
d1649dcd-6189-566a-b9f7-5352c082111e | note | Is the safety product fitted with operational instructions and a test tag
552dd757-43ff-4529-9d40-9426a0344762 | checkpoint | External Damage
7921c28d-4d52-53c4-ada9-586844e3732e | note | Is the safety product free from visible damage
898f427f-26c7-4be2-aff3-2e3484eb6199 | checkpoint | External Corrosion
45e05eee-96cd-55bf-b98a-67c6fedddebd | note | Is the safety product free from external corrosion
7212c092-50da-4b8f-8c97-0ce8af825837 | checkpoint | Activation Points
c391ac62-3c3d-5846-8dca-1a2dd3fe2101 | note | Are all activation points secure and in good working order
2d9e7ecc-35e5-4dd8-a88b-1c31e1adff51 | checkpoint | Leak Test
7163c478-bf7c-551e-bef1-f641cd14dcd3 | button | Check that shower/eye/face wash has no leaks - shower rose. | Pass, Fail, N/A
975e395e-2dbf-51db-94d6-2c650a1b5ff5 | button | eye/face outlets | Pass, Fail, N/A
6fb95f6e-a299-5441-8927-86003f6548fb | button | ball valves - shower 1" | Pass, Fail, N/A
a7775387-e2ae-59ad-84a8-9d014ea903ef | button | ball valves - eyewash 1/2" | Pass, Fail, N/A
c5e33970-a539-4c3c-b255-16cc85bdd85d | checkpoint | Dust Caps
f2414467-1bc9-5eda-8715-a538b804f5b9 | note | Are the dust caps correctly fitted and in good working order
39d8c3e6-40d6-4aea-97f0-254d475f07d1 | checkpoint-no-value | Flow details
f6620535-dd20-5686-897f-08797d65de2c | note | What are the flow details from the safety eye wash outlet
e6c54148-3e4b-591b-b7b2-1c27f3f968b0 | button | Does the flow meet in the middle | Pass, Fail, N/A
16771440-ffad-53d9-89e5-739b163b262b | note | what are the flow details from the safety product with all outlets flowing
5841721d-902e-5878-8555-30e7826a0a15 | button | Litres per second | Pass, Fail, N/A
074a890e-7654-5679-aff2-5c28f5d6701e | textbox | LPS
7012e2f0-87da-4712-842b-10bcdf7f1ef5 | checkpoint | Temperature Test
cdda22ec-1e83-52ad-a3a0-ff819dd09dfd | note | Turn on shower, test temperature
2f271a33-656e-54f2-9309-967eee6edc94 | textbox | Temperature
694f7da2-ff36-40a8-98eb-14f88fd3e691 | checklist | TMV 12 Month Service Log V.040221 |  | TMV 12 Month Service Log (use a separate checklist for each valve)
e6c008f2-5f03-418a-9009-6ac8e0ecf628 | checkpoint | TMV 12 Month Service Log
6f50691a-1052-508d-8942-49e4f9fee3e3 | textbox | Building name:
4b152a5c-c292-5f2b-b65c-9bd875e1b6b0 | textbox | Contact person:
9009d3d3-e172-5e90-98c6-2424962fd352 | textbox | Address:
fe012bfe-2595-5101-b131-a979e02183bb | textbox | Phone number:
2474ad68-5cf5-5eb5-bfbd-2aa6b41ee866 | textbox | Make of valve:
b58ba77d-9724-59e0-b632-a2c01965168a | textbox | Model number:
cec86261-f94b-5a41-ac58-08fa2f04f68d | textbox | Valve location:
e0416798-48a1-5701-87e1-805195bb6fda | textbox | Room name:
07f0cc2d-796d-535f-ad26-3220c5fe212e | textbox | Date of service:
74dc33f9-1bd1-5c78-a8ca-969583863bd7 | textbox | Temperature: |  |  |  | °C
34c78806-8271-5c24-911f-9d7ebdc7ae05 | button | Element: | Ok, Faulty
7b702738-5414-58fe-a150-2d29a9bfc558 | button | O' rings: | Ok, U, S
42b01cf6-fa34-54d8-8d06-354262c6949c | button | Strainers: | Ok, Dirty
5b9b3278-8c97-5b0f-849a-0a296e4355c0 | button | Non-return Valves | Ok, Faulty
3364de9b-9acd-5733-b0fa-6204cd3ed21b | button | Fail-safe test | Ok, Faulty
71c93ee4-c284-55ce-99e2-9bd18f206e34 | textbox | Serviced by:
4fd502bb-1d32-589f-b31f-cc82df6a231d | note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
72ddc61e-0f65-4bf6-9189-82e06e3b95df | checkpoint | Completion
bb196e3b-d980-5044-b91f-ae492fc70d5c | textbox | Plumber Name:
95efd6be-f992-4951-998a-6f11a502d064 | signoff | Add Signature
c172e59f-1f3e-4155-85a2-67ce11e48127 | checklist | TMV Commissioning Log Sheet |  | TMV Commissioning Log Sheet
3a8f7da1-cd08-442d-8f22-d79942cb17cb | checkpoint | TMV Commissioning Log Sheet:
a7f1780b-e526-5801-8ad9-cf7e02ac62de | textbox | Building Name:
f686823c-37ac-51e1-af3d-df925d3ceb98 | textbox | Contact Person:
469ecfdf-d2ab-593c-8b5e-cef6c6304c79 | textbox | Address:
0e7f15d4-c9b9-5c50-a941-3629c3ad9939 | textbox | Lic:
ad0ec5b4-6021-528b-ba75-04014450cff6 | textbox | Registration number:
acb2a7fc-dd8e-5ba5-89b1-ee038f4a58a0 | textbox | Phone number:
d8023cac-ad80-50d3-8b7c-91d3a766c3e9 | textbox | Make of valve:
dbac7f81-14f6-5090-962c-ff7a8ebcdb45 | textbox | Model number:
914e3e10-aef8-549b-bbf2-b3162773ab65 | textbox | Valve location:
70360b95-af8a-5c5b-a32c-0f4e5c0bb8fd | textbox | Room name:
bf538b80-ecd4-533e-b6dd-9ee499c22c19 | textbox | Valve purchased from:
819a9194-2d27-51e8-8619-7c6c10435725 | textbox | Installation date:
d8aaee2f-79da-55e4-9361-276787eefa88 | textbox | Valve installed by:
f2bcebb1-d52f-50d8-b19d-1fa4ab811420 | textbox | Number of outlets served - Baths:
99dcfc0b-1fcd-50e3-a952-8347f147575d | textbox | Number of outlets served - Basins:
5be8bcd0-b396-5f65-ad32-0a939f99bd55 | textbox | Number of outlets served - Showers:
5197e1e5-46d7-5582-aa63-897cc313124a | textbox | Total number of mixing valves on site:
1ec204c6-df96-543b-846b-89eb372f7e18 | button | Does the installation comply with the manufacturer's/supplier's published installation instructions? | No,Yes
ef1890c3-e32f-5240-9c96-315e41ec88b0 | button | Does the installation comply with the current requirements of the local water supply authority? | No,Yes
f3826041-b533-5b31-840b-26f878c00f22 | textbox | Temperature of hot water supply? |  |  |  | °C
63d7eb22-4539-5837-8a8a-4b128ee35787 | textbox | Temperature of cold water supply? |  |  |  | °C
4bdb5d46-3515-5f8b-8ff8-4057639948c9 | textbox | Temperature of warm water delivery at outlet fitting? |  |  |  | °C
11253992-854c-59c1-9942-c9806f72e470 | textbox | Dynamic pressure of hot water: |  |  |  | kPa
14d7cc7a-7ca1-5f69-93cd-8aab24d280f1 | textbox | Dynamic pressure of cold water: |  |  |  | kPa
6ff263c3-7b28-434a-a7ff-9759090be136 | checkpoint | Check fail safe operation (hot water at least 20c above warm water)
b88b82cd-1935-4d5f-bc01-0d890d26dc73 | checkpoint | Commissioned by
137d3899-07eb-5b6f-ac0f-a6bf76abe4dc | textbox | Commissioned by:
6be2e4d6-6059-5941-997b-c3b9ee51ddf5 | textbox | Company name:
69abad20-73d5-4f04-8f22-fa3a4cc2ba2e | checklist | TMV Routine Service Log Sheet |  | TMV Routine Service Log Sheet
b4a97cec-2bea-4dae-8c43-a8733dc63fad | checkpoint | TMV Routine Service Log Sheet:
bd859591-e754-562f-8def-fecc80eba2b7 | textbox | Building name:
4db378b4-6a92-5449-a8fb-5f4907e9cc52 | textbox | Contact Person:
c910ec39-37ec-5f2d-adf9-96f4d19919eb | textbox | Address:
bae87bed-dfc2-5a74-be03-000fe1a1389e | textbox | Phone number:
28711558-3c87-500b-b9c2-f2e6c0291884 | textbox | Make of valve:
07a98b69-70b8-5240-977b-22455ca4e069 | textbox | Model number:
4459de76-405d-5fa3-b482-c7b5778d83bc | textbox | Valve location:
f7c3711e-8df7-5dab-b0ea-6e919be3bc4e | textbox | Room name:
bdf867d2-1f9b-5102-8232-c027a4c4d3e9 | textbox | Date of service:
8a1bd64e-08b7-5965-bd30-65851c1a95ef | textbox | Outlet water temperature:
49baa28b-5389-5b3d-ac5a-2a0ae72a42da | button | Outlets flushed for 15 seconds | Yes, No
d901eddf-ded4-575d-83c0-659e40637b69 | button | Shower heads disinfected | Yes, No
e05d5b34-ea89-55e7-bddc-66bb600b6dba | textbox | Serviced By:
02563599-1e76-447a-b18a-7255eb70147f | checkpoint | Recommended Service Periods
5cc01c45-c5e1-5aae-b359-85aaf59339a1 | note | Outlet water temperature = Fortnightly
cc9b5d05-c28b-57ad-a94c-9b296e579f4f | note | Flushing of outlets = Weekly
a124c23d-83a0-51db-bdb0-d9f11c27d0e8 | note | Disinfect shower heads = Monthly
76fdeb37-e507-4d7e-b607-4c962b81e18d | checkpoint | Completed by:
a1821c24-1bf3-5643-9fb4-3e74c3567fa5 | textbox | Plumber Name:
8b38cb2a-555c-4bad-b980-8a5766dcd1dd | signoff | Add Signature
71875d21-eaf8-49b7-9fda-5eafbb4736c1 | checklist | zSYS - TMV 12 Month Service Log (old version) |  | TMV 12 Month Service Log (use a separate checklist for each valve)
96a8d8ec-19e9-4379-a4e3-bf23c083b16f | checkpoint | TMV 12 Month Service Log
c5580b72-4e9f-53f7-a5a0-57f3d6e37eb6 | textbox | Building name:
8797805a-1931-55ff-84ba-63491146c0ae | textbox | Contact person:
1ee42004-8164-5d71-9d8c-7a7d4748fb25 | textbox | Address:
cdc6660a-affe-5c5f-b15e-1039e3ea69af | textbox | Phone number:
575c5f12-7ed0-5857-928c-2bbb9b482ddb | textbox | Make of valve:
76aaa9f9-64eb-53cd-8c87-a4e4c92dbf10 | textbox | Model number:
94f0ff36-7a67-5c0f-9c4e-a518cf38f616 | textbox | Valve location:
dd97fc3b-45ea-58d2-9721-2550a9240319 | textbox | Room name:
a532fa81-7a26-5bc3-9c05-7e993fc74b29 | textbox | Date of service:
54f77530-41d2-5976-a172-853ba675acfe | button | Element: | Ok, Faulty
0a7d10c8-2064-59f2-8c11-94a529481545 | button | O' rings: | Ok, U, S
865e93d0-95d4-52e9-9d19-d91a3c8a50a0 | button | Strainers: | Ok, Dirty
52bb1c3f-3294-532d-bec1-8536877eccc4 | button | Non-return Valves | Ok, Faulty
9f5fe5e0-281f-5de3-8bac-5e6175a9fc42 | button | Fail-safe test | Ok, Faulty
315f2929-ffd0-5c59-b839-19b3ddab4d58 | textbox | Serviced by:
0e0b1c30-0138-514a-a720-a38086340d2c | note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
929f73a0-bfd1-4a0f-aa35-41182b0f0722 | checkpoint | Completion
08744529-db22-5ef8-a517-bd437fc44e33 | textbox | Plumber Name:
0d2488a6-04d1-4b0f-b4c0-228eb2d0673b | signoff | Add Signature