## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | Fire Hydrant Systems Checklist |  | Fire Hydrant Systems
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f9517f0a-4948-48f4-a893-daa79dec70b3 | checkpoint | 1.1 Water supply stop valves and isolating valves
287ac7a3-2b31-5f55-a503-7c82412f0bd6 | tickbox | (a) CHECK all isolating valves including underground key-operated valves are in the correct operating position
70e247d6-a181-5570-ac93-e61f86b68934 | tickbox | (b) CHECK all above ground valves are secured or monitored.
3eb978e5-2026-4c18-ade9-5bf9949669ff | checkpoint | 1.3 Hydrant valves (below ground)
e2c9f8c0-1791-5696-8ff9-94c6b4d3b522 | note | CHECK all hydrant valves:
0ac08324-19c9-5ae8-bf1c-5ade2e5e8cb9 | tickbox | (a) Are accessible.
1ba9b5be-dc75-5292-a68b-bfe1d1f4de85 | tickbox | (b) Blanking caps, where fitted, are in good condition.
4f66cdfd-2a5c-53ac-bd63-06b5f053ea6b | tickbox | (c) Check cover plate for ease of opening.
c25324eb-544a-49c9-b9ea-1ac023ae0a36 | checkpoint | 1.4 Booster assembly
cbd395f2-7bdf-59f8-97fc-f16d2e1deb4a | note | CHECK all booster assemblies:
aee7f434-4a1c-54f4-82e0-0c4571621b0e | tickbox | (a) Are accessible.
bf9a126b-560d-5a87-9686-c24c707f9d8b | tickbox | (b) Hand-wheels are securely fitted.
d4ad7338-3f5b-55f1-aac4-db93b1a81563 | tickbox | (c) Pressure gauges and blanking caps, where fitted, are in good condition.
e50d9700-2632-5d34-96d5-2be0709b6a0a | tickbox | (d) For condition of washers on booster assembly connection inlets and replace if signs of deterioration.
882f3c5a-394d-5e60-9f54-c1de241907c5 | tickbox | (e) For legible labelling indicating maximum system working pressure.
266dbdd2-c285-418f-bc16-67b7accab580 | checkpoint | 1.5 Hydrant and booster connections Compatibility
9255a92d-613b-5712-906d-9b4435d71757 | tickbox | CHECK that all hydrant and booster connection points are compatible with local brigade requirements.
a2a57431-040a-4c53-af2e-9f85d73695e5 | checkpoint | 1.6 All valves
e3473c17-f805-5394-8c71-8b12b7929b79 | tickbox | CHECK all valves for leaks.
0ba5b2bd-aa4c-43a5-a1bd-60c768f59ae6 | checkpoint | 1.9 Cabinets
6dd4b736-453b-52a0-89f9-ec9f610e2b3d | tickbox | CHECK that all hydrant and booster cabinets are accessible, clear of extraneous materials, clearly and correctly marked and in good condition.
d2d9f8e0-df1b-4fc7-b72c-cac5b2ecb072 | checkpoint | 1.14 Block plan and pressure gauge
4935ed94-e59e-5d96-9165-a6a052935cef | tickbox | CHECK for legibility and appropriate location
| checklist | Fire Hose Reels Checklist |  | Fire Hose Reels
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6f7a1d01-22a4-4d31-a99c-f2669a5894c3 | checkpoint | 1.1 Accessibility
d4e161b5-6bfe-562e-9b32-b84610d8bc86 | tickbox | CHECK that the hose reel is readily accessible with no obstacles restricting its access.
7de34c7e-20aa-4e44-87ab-0c5c67ff87fd | checkpoint | 1.2 Signage
76232eb3-bc25-5fcc-9c69-26291f99136c | tickbox | Where a location sign is required by AS 2441, CHECK that it is correctly located and visible.
8d6d7b7a-c210-4b13-af1f-02b928d41d98 | checkpoint | 1.3 Operating instructions
2c8c995f-421a-530c-afb3-01e9dcb4b971 | tickbox | CHECK that the operating instructions are legible.
3f281de6-ce82-4225-b8fb-fff482fc07c5 | checkpoint | 1.4 Damage
8c1d5f7b-5ab5-5280-82fc-c30369caa544 | tickbox | CHECK for any damage or corrosion of components that could adversely affect the operation of the reel
01f5c70a-846b-4ba9-9033-d6923d0fe527 | checkpoint | 1.6 Cabinet
9b464f1a-b845-50c6-a8e8-50546061e77f | tickbox | CHECK that all hose reel cabinets are accessible, clear of extraneous materials,clearly and correctly marked and in goodrepair.
4846e065-fc23-4bc4-872b-a501a877152e | checkpoint | 2.3 Hose fittings
c98218a0-6b44-588e-b7e0-f465ede9894c | tickbox | DETERMINE that all hose fittings and connections are tight
fbc31c10-49c8-4846-ab72-e38b37bbe836 | checkpoint | 2.5 Swing arm
bc50aa2e-7fb8-5149-b6f2-89c3a7024ef6 | tickbox | Where fitted, TEST the swing arm to ensure it operates correctly and allows the hose to be run off in its intended direction
d09d4354-af03-4447-8a96-873cdbaf8c19 | checkpoint | 2.6 Unwind
d59949b4-c9c7-58d3-af5e-40b97cebdc3d | tickbox | With the nozzle closed and stop valve open, TEST that the hose reel can be unwound freely in its intended direction by unwinding at least 5 m of hose.
2e4ffa55-0def-4cad-b574-9d9d943563f4 | checkpoint | 2.7 Leakage
6ce30553-bc51-5796-be9d-cdef9df2b00f | tickbox | With the nozzle closed, pressurize the reel by opening the stop valve. DETERMINE if there are any leaks from the gland, nozzle, stop valve, hose or any fittings. NOTE: In order to check that there is no leakage of water from any part of the reel waterway, it is recommended that the hose be completely unwound off the reel, so that all parts of the waterway can be examined.
dad6044c-01a7-46a3-87d3-1d30dea38c8e | checkpoint | 2.8 Flow
edda791e-f810-5580-87eb-5d3a4daecccf | tickbox | TEST water to ensure it is able to flow through the reel by opening and closing the nozzle.