## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
9a549b4d-6d4b-59d4-9eb6-b80e61eefa4a | checklist | Cable Schedule |  | Cable Schedule
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
11bdd80d-da1b-5a32-94f4-5a8adff94dc7 | checkpoint | Attach cable schedule - Earthing Cable Schedule
5d4e06d0-3da2-5749-b5d3-d8d745b25a62 | checkpoint | Attach cable schedule - Busduct Schedule
d5c3e07c-d63a-5f1e-bf04-55cd0d6eeefc | checkpoint | Attach cable schedule - DH5A Branch TOB Cables
82f44c09-c71c-57a0-b483-9e6f3977b83c | checkpoint | Attach cable schedule - LV Cable Schedule
d646fc67-3d3d-506c-8129-6d1fc6a49989 | checkpoint | Attach cable schedule
27094fa3-0a24-5e96-8a8d-0c4a8e4ba343 | checklist | Commissioning Documentation |  | Commissioning Documentation
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
84d53554-a998-5fa7-b2cf-e24a0d397f33 | checkpoint | Attach relevant commissioning documentation
eda3bc88-e962-5f31-aa4c-deab5c3b19f2 | checklist | DC Supplies CxL2 |  | DC Supplies CxL2
0b4ad232-5674-51d3-9408-aef0b58a609d | section | Details:
5ae48345-4b4a-5412-bc90-b32aa84a3057 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
02471f87-eeae-5401-ad7c-4cb48bee4470 | textbox | From
c5611496-b45f-59af-a3a5-5220d41df01f | textbox | To
5dbcfc52-e41d-591c-9898-105a631b1219 | checkpoint | Installation Checks (Insulation damage, Correct Type of Termination, Correct colour code, Correct cable size and labelling, Correct cable routing and diverse path where required)
5adc9e12-877f-5557-bf6b-161cdb2bc001 | textbox | Insulation Resistance (+/-)
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
93a2fddc-c1f2-4601-964a-541e0a2b60ba | checklist | DC Supplies CxL2 Rev 2 |  | DC Supplies CxL2 Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
330f192e-e1b9-4863-a604-6c1348a36773 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
8e7eea34-57c4-56c5-afae-63cec6bcf0a8 | textbox | From
b4302ec6-540b-5bf7-a405-2791a08d0ca3 | textbox | To
b5a313dc-9979-4780-b875-8dbba6ad9b47 | signoff | Holdpoint / Sign Off
42a47d3e-7d91-4a01-91e4-7a8abe50c218 | checkpoint | Installation Checks (Insulation damage, Correct Type of Termination, Correct colour code, Correct cable size and labelling, Correct cable routing and diverse path where required)
ae256e73-13f6-5ed5-84f9-bbe0df2a3c63 | textbox | Insulation Resistance (+/-)
c3340473-2c5c-4be4-a349-d03fac022cf0 | signoff | Holdpoint / Sign Off
592f2e64-9148-489e-a121-ad68e82614c1 | checkpoint | Labelling Installed
71ec43be-6036-4e00-9f9a-1236318cf729 | signoff | Holdpoint / Sign Off
b26d032a-8129-41a7-8dee-fecda2c1366e | checkpoint | Cable Terminations to be checked (No loose terminations)
818bb181-c9b1-4a4b-86f8-3fc4444ecd2f | signoff | Holdpoint / Sign Off
ec450fac-fd12-42eb-a9ed-9fa52fe06904 | checkpoint | Switchgear to be cleaned
7ad2aa42-e032-492e-be51-b41f10064dc7 | signoff | Holdpoint / Sign Off
e73c7fb1-d6ec-4e06-b5c9-7ce722aa29fa | checkpoint | Photo of Subcircuit Installation works and termination points
2a6c46c2-af02-4b27-8c8d-ad8b77a72438 | signoff | Holdpoint / Sign Off
2b494ebd-7d89-4ffe-a202-5818ff084c32 | checkpoint | Final acceptance
b0890db0-bd33-47f1-b846-5a1728a54451 | signoff | Final acceptance
149e396c-5097-5319-85ae-ed3a491640c2 | checklist | DC Supplies CxL3 |  | DC Supplies CxL3
0b4ad232-5674-51d3-9408-aef0b58a609d | section | Details:
df940797-0036-5fe4-9fdf-1e94fc8d0ce5 | checkpoint | DC Supplies CxL2 completed
546bb586-f375-585c-b40e-b3afc8e5221f | textbox | From
f2e18fc0-ebcb-51df-9eed-077c4174d5c8 | textbox | To
9e45f3d9-eed8-50da-9da8-7ae4285c3a93 | textbox | Voltage (+/-) Note - 110VDC range 99V to 121V
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
9e7c0de0-38e3-4cf9-923b-3fc72a4b980c | checklist | DC Supplies CxL3 Rev 2 |  | DC Supplies CxL3 Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
25bae935-3615-41ce-bc4e-403c4d7255fb | checkpoint | DC Supplies CxL2 completed
102b09bb-2612-51fa-988e-a49d6fe0d031 | textbox | From
40f37eed-1683-53b7-918d-288abf229769 | textbox | To
53d35f57-5f8d-540e-b1e8-becb6774e045 | textbox | Voltage (+/-) Note - 110VDC range 99V to 121V
535b4988-8e79-49ab-a92c-0a0a780d2e7c | signoff | Holdpoint / Sign Off
df655286-05d7-4a98-879e-b16aba64c522 | checkpoint | Final acceptance
4c4ca28c-55fe-45c3-813a-e4ad808ec556 | signoff | Final acceptance
7b120390-f452-4ff8-a664-9028badbb55d | checklist | Dynamic Signage |  | Dynamic Signage
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
ad0a7f30-8eda-4c72-908e-66ac4f552bb8 | checkpoint-no-value | Fitting ID
3ee333c9-90e2-56a9-95a5-ec6059d0d70e | textbox | Fitting ID
50249307-f2f1-49ae-94bf-86d371349d57 | checkpoint | Installed to location as per drawing
b1526a1d-3086-472a-af68-a32d609fb476 | signoff | Holdpoint / Sign Off
767075ab-01cf-463d-afd6-4ff578a90d2c | checkpoint | Labelling applied
81d1b98c-8fe4-429c-9bd3-b436635b29a3 | signoff | Holdpoint / Sign Off
1b4386ac-59b2-4a8f-8eb2-78f00fbb97ae | checkpoint | Attach timestamp photo of Fire Event E/W Corridor
420acedd-ec0e-4487-baa7-e6274308f9c4 | signoff | Holdpoint / Sign Off
83466275-4ff5-435d-a4b5-eab3e83e0e1d | checkpoint | Attach timestamp photo of Fire Event N/S Corridor
4e984a0a-2264-4795-a9ad-cc32ea44cb36 | signoff | Holdpoint / Sign Off
ec223107-2d34-4c9a-af7b-cd233adac335 | checkpoint | Final acceptance
da4dbce8-2d4b-49bd-ad70-48f346725e07 | signoff | Final acceptance
97ef6877-7491-5c60-91e6-723ae02bf4dc | checklist | EL-0008-2-C-R[B] Low Voltage Cables |  | EL-0008-2-C-R[B] Low Voltage Cables
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
f746eb4d-e55e-5cc3-9e8b-3e06014d1f09 | checkpoint | EL-0008-2-P-R[B] Low Voltage Cables completed
2d25b0d5-da80-5546-b4a9-b915491c7448 | textbox | From
8b498cd2-793b-5340-88f5-7d671e482aff | textbox | To
a237a7f6-7a63-521c-92e3-e4c93ba8a048 | textbox | Voltage (+/-)
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
8819485a-6397-573f-981c-23df46b057e0 | checklist | EL-0008-2-P-R[B] Low Voltage Cables |  | EL-0008-2-P-R[B] Low Voltage Cables
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5ae48345-4b4a-5412-bc90-b32aa84a3057 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
d9f755a3-2e8f-5028-b151-cf9d569910df | textbox | From
1539d453-b416-5fbf-8573-0780e963d91d | textbox | To
ed38db4c-1f0e-5fe8-bade-90c011836b8b | checkpoint | Insulation damage
a9cc2e4c-f587-5914-968b-b5d08732c5e4 | checkpoint | Correct Type of Termination
9eb1e619-8fa1-5475-85f9-da954d66e0dd | checkpoint | Correct Colour Code, As per Low Voltage Cable Schedule
77d36f90-fdfb-51b8-8553-b45baa056bdf | checkpoint | Correct cable size, As per Low Voltage Cable Schedule
4f6a10a6-b4fc-5058-96cf-14852e868e0d | checkpoint | Correct cable routing and diverse path where required, As per layout drawings
85e11ff5-4ba8-5edd-9327-48fed078b79f | textbox | Insulation Resistance (+/-), A minimum resistance value of 1 Megaohm is required
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
6fdf474a-ba52-5545-8fff-e92fb40b579d | checklist | EL-0021-P-R[B] Extra Low Voltage Cables |  | EL-0021-P-R[B] Extra Low Voltage Cables
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a84b09fd-c3ad-5eec-82d8-c15f1dea7c05 | checkpoint | All prerequisite checks are completed
949d9c62-d1f2-5d3f-9312-fa4631f61afa | textbox | From
50770086-30c0-5231-a5c4-00b2a957e511 | textbox | To
a9d175a6-b689-5e87-bab0-ead1e4457821 | checkpoint | No Insulation Damage
a9cc2e4c-f587-5914-968b-b5d08732c5e4 | checkpoint | Correct Type of Termination
a93fdd6a-4c8a-517d-bbb6-dae13edefaae | checkpoint | Correct Cable Size
27f33352-48d8-5454-9281-629807594633 | checkpoint | Polarity Check
cf47b0bc-7b0f-5a4c-baad-29395f9a3745 | checkpoint | Continuity Test
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
e44b454b-6aba-44a9-8041-9ae6c997828e/1 | checklist | Fire Rating - Small Penetration - Basement |  | Fire Rating - Small Penetration - Basement
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
bb752492-05b0-4604-aa41-db0f666c0339 | checkpoint | Fire Stopping System No.
3ee17c71-4fd5-5b41-a8e3-5784be257584 | dropdown | Select System No. | FAS190236 RIR1.8 TBA Firefly, 27912900 RIR1.6 Hilti CP611A
c64d3a5a-420c-4fd3-b466-c7fc0f8f205e | checkpoint | Penetration Type
2aa42998-348c-5392-8746-f5e83118761d | dropdown | Select Type | Floor,Wall,Ceiling
3d445f7e-f8a5-46ee-8ac9-fde197d17440 | checkpoint | Location
0085fe17-041f-5c1d-a669-7f09baafeea6 | dropdown | Location: | Basement
4c188206-e221-473c-9a61-d5ab3b232141 | checkpoint | FRL
a87295f9-370b-5168-bb0a-1c71841f9efa | dropdown | Select FRL | ~ / 120 / 120, ~/ 60 / 60
844736c1-952e-4d90-a2f5-dc0df4572bc1 | checkpoint | Service Description
a1f89bd5-9745-5ab8-a44c-78721c198ff3 | dropdown | Select Description | Cables through Blockwork, Cables through plasterboard, Cables through concrete, Conduits throuh blockwork, Conduits through plasterboard, Conduits through concrete
d59113cd-d570-4556-87a1-c339e072564a | checkpoint | Photo of Fire Sealing & Label
dc2d85fe-7314-4c55-95d6-a2588f7004c7 | checkpoint | Details added to penetration register
de024118-c10e-4ad2-a4b3-dbe7f25ff2cf/3 | checklist | Fire Rating - Small Penetration - Level 1 |  | Fire Rating - Small Penetration - Level 1
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
988ac44c-25fb-49b2-a133-0611e19c363f | checkpoint | Fire Stopping System No.
fd64caed-0e92-50b5-83bd-7e428e019cd8 | dropdown | Select System No. | FAS190236 RIR1.8 TBA Firefly, 27912900 RIR1.6 Hilti CP611A
5437926a-61ad-4c7e-a0ee-306e5ac97ff3 | checkpoint | Penetration Type
f4d9152d-75a7-5c8e-8dd0-f69ff87e432d | dropdown | Select Type | Floor,Wall,Ceiling
9a73355a-6c84-437d-96a1-3698b50da4aa | checkpoint | Location
d9d4fc9e-dadc-58f8-b350-73f363282528 | dropdown | Location: | Level 1
5e1dc215-8051-4cd3-8ac6-269ac5f774d9 | checkpoint | FRL
693658d1-563f-591d-bc83-269b55397e9d | dropdown | Select FRL | ~ / 120 / 120, ~/ 60 / 60
ea6c066c-0ea7-43cb-816a-e0e917f3f6d7 | checkpoint | Service Description
1160eecd-ebfa-59a7-b27a-1d487a8cec70 | dropdown | Select Description | Cables through Blockwork, Cables through plasterboard, Cables through concrete, Conduits throuh blockwork, Conduits through plasterboard, Conduits through concrete
8aae5776-91fd-425e-b220-5590b35c4f87 | checkpoint | Photo of Fire Sealing & Label
a1cd8d82-bce2-4de4-97c4-02e131a329ac | checkpoint | Details added to penetration register
3a596a6b-4145-49e0-90eb-7b3f411366b6/1 | checklist | Fire Rating - Small Penetration - Level 2 |  | Fire Rating - Small Penetration - Level 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2f95fdd9-4708-4e7a-bc27-e9f28196ca64 | checkpoint | Fire Stopping System No.
acfb3d72-ff1f-5914-934f-84282e813af9 | dropdown | Select System No. | FAS190236 RIR1.8 TBA Firefly, 27912900 RIR1.6 Hilti CP611A
d686cf02-6c4a-4dbe-b791-4c0b5cb43523 | checkpoint | Penetration Type
504feb7c-b78c-521d-8505-f3111bb6e728 | dropdown | Select Type | Floor,Wall,Ceiling
1cb74c43-0f53-4239-bd3a-bd0127949074 | checkpoint | Location
1c42525c-57bc-59ca-a469-9cae89d23d28 | dropdown | Location: | Level 2
d932424a-9c3d-485b-b90c-23a6b8486340 | checkpoint | FRL
99bd33c7-1f5d-5ef8-911b-62222ee450ff | dropdown | Select FRL | ~ / 120 / 120, ~/ 60 / 60
4391e5da-523c-4545-85ab-4790e5a97394 | checkpoint | Service Description
367fa296-c082-5255-b396-c8565a21763a | dropdown | Select Description | Cables through Blockwork, Cables through plasterboard, Cables through concrete, Conduits throuh blockwork, Conduits through plasterboard, Conduits through concrete
331194ef-373b-424a-bfd9-0afd62bcc93c | checkpoint | Photo of Fire Sealing & Label
3a3accb0-8eb7-42b5-b141-c403cdd3d654 | checkpoint | Details added to penetration register
e0bba17e-0b3a-41c2-9237-ddf644dc89c4/1 | checklist | Fire Rating - Small Penetration - Level 3 |  | Fire Rating - Small Penetration - Level 3
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f5a33244-b9c1-416a-bd43-cecbf8b8e284 | checkpoint | Fire Stopping System No.
46043f49-eb9b-5e95-9b0f-07d845c9001d | dropdown | Select System No. | FAS190236 RIR1.8 TBA Firefly, 27912900 RIR1.6 Hilti CP611A
73a10296-0405-4e28-9ed4-cdd70645a929 | checkpoint | Penetration Type
18aa3dcc-d5bc-5995-a2c7-aee5ca83874c | dropdown | Select Type | Floor,Wall,Ceiling
ad72ff7e-468a-4655-920d-8ba2253563c1 | checkpoint | Location
921fa0f0-1bac-5c05-a0cd-023d45e36a39 | dropdown | Location: | Level 3
6c1b1fd0-f6a8-4f40-b06b-588ba3a1690f | checkpoint | FRL
126d6992-f573-5782-a3b9-99ff3edcc752 | dropdown | Select FRL | ~ / 120 / 120, ~/ 60 / 60
a6c77d6b-810a-4007-ad4f-e6ced8fa8d0a | checkpoint | Service Description
c334d8d9-cff5-554e-87f8-7a89d0f72e88 | dropdown | Select Description | Cables through Blockwork, Cables through plasterboard, Cables through concrete, Conduits throuh blockwork, Conduits through plasterboard, Conduits through concrete
3c1a20d4-0347-49ab-bdf5-dd08a8ccdfd8 | checkpoint | Photo of Fire Sealing & Label
ebbd9060-5fe6-496a-8c30-1f4b0e0d8b40 | checkpoint | Details added to penetration register
5d25868b-c2cb-413e-898c-641fd9a66b01/1 | checklist | Fire Rating - Small Penetration - Level 4 |  | Fire Rating - Small Penetration - Level 4
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
eabd7d08-d00a-4aea-906f-ff663ba6dc7b | checkpoint | Fire Stopping System No.
bc1938fb-3468-5af5-9780-0dc3e7ef39d8 | dropdown | Select System No. | FAS190236 RIR1.8 TBA Firefly, 27912900 RIR1.6 Hilti CP611A
4d367d21-4420-419f-9cb8-a2c0fec919ba | checkpoint | Penetration Type
3d08bfde-38f4-5f51-a3e1-b6e2c9e5d5e0 | dropdown | Select Type | Floor,Wall,Ceiling
481cf9cb-eaf9-4237-8a57-6310f6a068a7 | checkpoint | Location
bff363ce-877c-5c08-a581-ee5022e10d8b | dropdown | Location: | Level 4
b2739d7d-0fd7-4dcc-a91a-e2885bcf72a5 | checkpoint | FRL
51b23825-ecc5-5462-a214-b74eb19a4919 | dropdown | Select FRL | ~ / 120 / 120, ~/ 60 / 60
4dcd143f-4b06-4cd0-b0a0-eb4b86f3531a | checkpoint | Service Description
640bde1d-f2a5-5e9b-85bf-f823b7b46369 | dropdown | Select Description | Cables through Blockwork, Cables through plasterboard, Cables through concrete, Conduits throuh blockwork, Conduits through plasterboard, Conduits through concrete
43828904-e796-4fb7-9618-39b9ceed3f85 | checkpoint | Photo of Fire Sealing & Label
41adcd1a-f006-41ec-9f24-598d64223df6 | checkpoint | Details added to penetration register
104c5709-c841-4e5d-8136-d51019d83330/1 | checklist | Fire Rating - Small Penetration - Level 5 |  | Fire Rating - Small Penetration - Level 5
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
21529361-36e7-40a8-be29-0cd472d8b91b | checkpoint | Fire Stopping System No.
456b1731-79c5-543a-b42f-c4816c809d3c | dropdown | Select System No. | FAS190236 RIR1.8 TBA Firefly, 27912900 RIR1.6 Hilti CP611A
8f7b2e3d-80b9-4682-a351-219833f2d2a0 | checkpoint | Penetration Type
8176b488-a568-5b6c-8032-6b5e1e5487ee | dropdown | Select Type | Floor,Wall,Ceiling
b53fc70c-6c68-410d-957e-278d52dda7e8 | checkpoint | Location
d1e9ae70-5604-5090-a23d-4da503007378 | dropdown | Location: | Level 5
4e902279-12f8-4775-aa81-5846f5bb6fb8 | checkpoint | FRL
fbbaf5f4-61c6-5e42-a9ff-d5c92a6fcf12 | dropdown | Select FRL | ~ / 120 / 120, ~/ 60 / 60
a7622af9-e39d-43ab-a196-e692290643f0 | checkpoint | Service Description
2aa0c188-ab98-53f0-b081-3b08a68d5ac9 | dropdown | Select Description | Cables through Blockwork, Cables through plasterboard, Cables through concrete, Conduits throuh blockwork, Conduits through plasterboard, Conduits through concrete
e431e633-9324-4c33-82a2-9b36532d75df | checkpoint | Photo of Fire Sealing & Label
0c24df1f-bb23-4ce6-a3d9-15926ceab76b | checkpoint | Details added to penetration register
4e727b88-8dd6-48f2-b516-86b4ee5d9d3c/1 | checklist | Fire Rating - Small Penetration - Level 6 |  | Fire Rating - Small Penetration - Level 6
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d3b89eaa-e9cd-4d19-a9d5-aefa8d0973f2 | checkpoint | Fire Stopping System No.
920b4dda-a9c3-59c7-be51-97b5ca1e43ab | dropdown | Select System No. | FAS190236 RIR1.8 TBA Firefly, 27912900 RIR1.6 Hilti CP611A
50673667-4bad-4f0d-b500-6ef4be2cd330 | checkpoint | Penetration Type
5a4411b5-bcb2-5784-b153-d9c0edc33e45 | dropdown | Select Type | Floor,Wall,Ceiling
869d62aa-5f2e-4ea9-9812-549c8cc93d5e | checkpoint | Location
1ce82d2b-fee3-5777-b9a7-2cac25ca0544 | dropdown | Location: | Level 6
be7e8564-02e2-4697-ba3c-c361d1d0e6ac | checkpoint | FRL
a179cad5-744d-5e60-aa1f-a7fd9f47d648 | dropdown | Select FRL | ~ / 120 / 120, ~/ 60 / 60
a5f3a0c9-c5e4-4f9b-b499-d38a25099a3a | checkpoint | Service Description
80f46902-a1fe-5d43-9b31-efe6835872da | dropdown | Select Description | Cables through Blockwork, Cables through plasterboard, Cables through concrete, Conduits throuh blockwork, Conduits through plasterboard, Conduits through concrete
e7c0c8a4-cb91-467c-9868-a07922dfe306 | checkpoint | Photo of Fire Sealing & Label
bfa3a01b-7b15-4915-969a-4f918f021c46 | checkpoint | Details added to penetration register
43c40a07-69b9-41c9-9f9a-593461675348/1 | checklist | Fire Rating - Small Penetration - Level 7 |  | Fire Rating - Small Penetration - Level 7
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
947878e5-b061-45da-b289-0071b1e36f86 | checkpoint | Fire Stopping System No.
e9b27cc6-3f4a-5dd1-ba4d-9f71a4a7a3ad | dropdown | Select System No. | FAS190236 RIR1.8 TBA Firefly, 27912900 RIR1.6 Hilti CP611A
cb3660d9-e877-4331-8474-96a7a6ceecb7 | checkpoint | Penetration Type
e557d594-6d7e-5316-8407-7ed4488ced3d | dropdown | Select Type | Floor,Wall,Ceiling
29755c09-562e-45d3-bc61-f15b157fcf16 | checkpoint | Location
89913aaf-67c5-5fba-825e-fbde2129ffd0 | dropdown | Location: | Level 7
bbf37c5c-2406-4207-b31f-0805f6d7310e | checkpoint | FRL
b113e465-3379-54f3-8b9d-141f9be46ff0 | dropdown | Select FRL | ~ / 120 / 120, ~/ 60 / 60
b8fcc4bb-4f15-469e-b20a-4d8134d72a67 | checkpoint | Service Description
cb5d8b4b-f10c-5c63-a629-bfbc333c90cd | dropdown | Select Description | Cables through Blockwork, Cables through plasterboard, Cables through concrete, Conduits throuh blockwork, Conduits through plasterboard, Conduits through concrete
54f123c1-32d4-4582-8df1-951aa6febd84 | checkpoint | Photo of Fire Sealing & Label
625bd3db-cf5f-4b84-bdc1-9ba525b05514 | checkpoint | Details added to penetration register
3f39446f-7443-482e-a25c-b5650ef9969d/1 | checklist | Fire Rating - Small Penetration - Level 8 |  | Fire Rating - Small Penetration - Level 8
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
e12da315-58a1-4cee-a2a6-dd6b60cc0638 | checkpoint | Fire Stopping System No.
054cddb6-afbc-559b-ac1a-60c8f903c515 | dropdown | Select System No. | FAS190236 RIR1.8 TBA Firefly, 27912900 RIR1.6 Hilti CP611A
d2473116-0f47-4fce-ae6e-8aea403bfc8d | checkpoint | Penetration Type
76e51c9c-9a43-5d2e-bf0b-d3470b4bb842 | dropdown | Select Type | Floor,Wall,Ceiling
4b260d52-e35a-4958-847b-bb53ce27fb56 | checkpoint | Location
ddd0a8f9-6370-566c-927a-96f5ac8cea62 | dropdown | Location: | Level 8
72c1f381-1e70-4647-815a-d24f6f90641f | checkpoint | FRL
da6e01c9-82d2-5887-91ff-d1b2c0932432 | dropdown | Select FRL | ~ / 120 / 120, ~/ 60 / 60
edd4dd32-ed3d-42de-803a-e735e6bef361 | checkpoint | Service Description
3dbac083-aef7-5d09-bfe1-70ad42b0be98 | dropdown | Select Description | Cables through Blockwork, Cables through plasterboard, Cables through concrete, Conduits throuh blockwork, Conduits through plasterboard, Conduits through concrete
b80045a2-ce9b-4590-b880-0cc6578ef7d9 | checkpoint | Photo of Fire Sealing & Label
9d46dcf5-1e99-4f43-9bba-0a27732776d1 | checkpoint | Details added to penetration register
1772cae6-c6d4-4e43-84ec-2c82bdb61ae1/2 | checklist | Fire Rating - Small Penetration - Level Roof |  | Fire Rating - Small Penetration - Level Roof Plant
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2da135b2-d49e-4d36-a255-c01fc2162e89 | checkpoint | Fire Stopping System No.
a95310a7-2f05-59cf-9b04-2bc4a1003f2f | dropdown | Select System No. | FAS190236 RIR1.8 TBA Firefly, 27912900 RIR1.6 Hilti CP611A
1477d2ed-771f-405a-aced-b96f41d23521 | checkpoint | Penetration Type
621a4ab4-46ff-51f7-a183-6645ff2ba109 | dropdown | Select Type | Floor,Wall,Ceiling
19d494ff-4154-4b74-aea9-a81647f05618 | checkpoint | Location
de56d51b-4c8f-5d6d-a005-e41611ec00c1 | dropdown | Location: | Level 9
361091b8-d798-42f1-8ceb-3da2108742d4 | checkpoint | FRL
91c32751-b444-5e4b-9ba2-b032213d371f | dropdown | Select FRL | ~ / 120 / 120, ~/ 60 / 60
46ac8af1-2165-4d8a-9f15-241603da7d9b | checkpoint | Service Description
dcd733bb-c988-5359-9600-3d68416bff81 | dropdown | Select Description | Cables through Blockwork, Cables through plasterboard, Cables through concrete, Conduits throuh blockwork, Conduits through plasterboard, Conduits through concrete
0551d070-3498-4fd0-9d36-4f3b935db379 | checkpoint | Photo of Fire Sealing & Label
0d5b80ac-6cfa-4412-a1ad-8b5d974e0b40 | checkpoint | Details added to penetration register
b2d14cfb-f1e7-5064-abfa-1d1e22cf6e31 | checklist | Lighting Circuits CxL3 |  | Lighting Circuits CxL3
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
3e5cca90-6d01-5f3f-8bab-2ada1f84d79e | checkpoint | CxL2 Lighting Circuits completed
23ee8638-3496-5571-8722-acd9e7b64417 | textbox | Circuit Number
3eb88021-2bc3-5c41-9421-2a3212f766b3 | checkpoint | Polarity (No Transposition)
6916d52a-f665-5bb9-9997-59299c83290a | checkpoint | Polarity (Switch in Active)
dacf8478-85d1-55af-869b-7cea6e389fbf | textbox | RCD Tripping Test (Trip current)
e8c3ef1b-5044-520f-abd0-a20e87f6bac1 | textbox | RCD Tripping Test (Tripping time) as per AS/NZS 3017
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
5dc645ab-8b1e-4afa-8ef7-4d5100cb2879 | checklist | Lighting Circuits CxL3 Rev 2 |  | Lighting Circuits CxL3 Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
10728972-cfe2-4834-b5b8-9c1ef5edcaaf | checkpoint | Lighting CxL2 completed
1fbba4d3-673d-570c-882c-3721e8066492 | textbox | Circuit Number
d2ede9bc-d5af-42d9-84e9-b1872d5dc8b2 | signoff | Holdpoint / Sign Off
50ea68e1-c06a-4f7b-846c-7f5d5f4b8c81 | checkpoint | Polarity (No Transposition)
1a316042-e777-4add-9fb2-873c36f90575 | signoff | Holdpoint / Sign Off
fd0ec815-ceda-49fd-9c08-b536109a13ca | checkpoint | Polarity (Switch in Active)
f217d5d6-a8b2-59c6-9b52-798ea1fc93af | textbox | RCD Tripping Test (Trip current) (refer to Reference Table - RCD)
6d5034ea-4d65-566b-8b0e-e573dc205931 | textbox | RCD Tripping Test (Tripping time) as per AS/NZS 3017 (refer to Reference Table - RCD)
84d2e9eb-9bcf-4649-9fad-16618da214db | signoff | Holdpoint / Sign Off
20365446-6868-4ecd-968c-448586c4a8b3 | checkpoint | Final acceptance
c6407ddd-b138-4dc9-af41-66ab206c41d3 | signoff | Final acceptance
1537a3c1-d95b-5be0-af38-4e04c84bb3f8 | checklist | Lighting CxL2 |  | Lighting CxL2
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5ae48345-4b4a-5412-bc90-b32aa84a3057 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
051216f8-5a03-5501-9e55-b35956552010 | textbox | Circuit Number
84366f08-a768-509f-b537-ec887b9f3d2f | checkpoint | Installation Checks
a58c8ac0-06a8-59c2-a9f8-467e1cdc3d56 | textbox | Continuity Test (Resistance - Ohm)
8789d456-03e1-5c41-83fe-f6520309145a | textbox | Target (Resistance - Ohm), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1
1df0009a-54a5-530c-bde4-286d71cbed51 | textbox | Insulation Resistance (P-N)
6d9b07af-a1e4-5c15-ba6b-61f028ca8f85 | textbox | Insulation Resistance (P-E)
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
b40c105a-a8cb-4bca-9d10-db145c3b3b0d | checklist | Lighting CxL2 Rev 2 |  | Lighting CxL2 Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1440e9fa-f5b9-4d48-bb7a-1240eb5527db | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
bfa65b94-3d61-5c59-9aff-a4ff3d1b18ce | textbox | Circuit Number
8122479c-975a-4148-8198-850b9b225865 | signoff | Holdpoint / Sign Off
aaf3e78b-6d03-4b56-9170-9a47e57ad6b2 | checkpoint | Installation Checks (Insulation damage, Correct Type of Termination, Correct colour code, Correct cable size and labelling)
7042100d-89a5-55c2-afd5-699dbd7658e7 | textbox | Continuity Test (Resistance - Ohm)
1803e858-4c36-5adb-9eda-01bbf10de296 | textbox | Target (Resistance - Ohm), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1 (refer to Reference Tables - Resistance)
f4c267d2-0bec-5856-bd5a-854c81f332fa | textbox | Insulation Resistance (P-N)
04ff243c-a2c7-52c1-b596-468ad5d41556 | textbox | Insulation Resistance (P-E)
cc734045-b0a4-410a-a54a-cd287aa4dac9 | signoff | Holdpoint / Sign Off
8029e5c3-6916-4f14-a91e-c0fb195f8abc | checkpoint | Cable Terminations to be checked (No loose terminations)
21fb39b8-8d74-472c-936d-ec1c69759bd7 | signoff | Holdpoint / Sign Off
e3611a93-4d1f-48c5-8b0c-a544238af23d | checkpoint | Final acceptance
f647ca52-4e0e-46e0-8a36-54730e6497da | signoff | Final acceptance
2af9cad3-c1a7-5c2c-85fb-be686f0b3bc6 | checklist | Pictures |  | Pictures
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
8bb118c8-788c-52c3-8851-393a010a3137 | checkpoint | Attach any revelant pictures
0b2c632c-fde0-5a25-a448-4b506b51c38d | checklist | Power Outlets CxL2 |  | Power Outlets CxL2
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5ae48345-4b4a-5412-bc90-b32aa84a3057 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
728ff1f2-0b99-5b9f-99f4-558357401f31 | textbox | Circuit Number
84366f08-a768-509f-b537-ec887b9f3d2f | checkpoint | Installation Checks
1b8029e4-ac29-5f82-9d0b-3c9c84cef14c | textbox | Continuity Test (Resistance - Ohm)
e5a8f582-a991-5603-966d-12b7b74d82ca | textbox | Target (Resistance - Ohm), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1
6bc9ffa2-7bb4-556c-963f-39fb392cbce5 | textbox | Insulation Resistance (R-W)
791ecb3d-d1e9-5273-887e-15303d611704 | textbox | Insulation Resistance (R-B)
1d6a7ecc-0ab6-5cfd-a7fc-fd7632d5c57a | textbox | Insulation Resistance (W-B)
fe911e5f-5a61-5cb3-b334-7eaad7356d96 | textbox | Insulation Resistance (R-N)
f3bd0488-027f-5d12-9332-55ab3507fb8c | textbox | Insulation Resistance (W-N)
ceea6134-768e-53df-b736-6da998bdbe0f | textbox | Insulation Resistance (B-N)
71006c47-8879-50e5-9c17-9a289319a315 | textbox | Insulation Resistance (R-E)
5c2e1fcc-f57b-5c14-a427-bd4fb4a25072 | textbox | Insulation Resistance (W-E)
aad3969c-52fd-589e-8ae9-9f13295ec6d2 | textbox | Insulation Resistance (B-E)
4e66303a-a49c-5ae9-881b-683e7b643458 | textbox | Insulation Resistance (N-E)
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
fbb1eef6-74bb-4c0e-9584-8a3e30d63887 | checklist | Power Outlets CxL2 Rev 2 |  | Power Outlets CxL2 Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2e9a3695-0872-49b1-b0c1-0cf81ac4dd4c | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
c21b852e-4e3c-5c4b-be65-9b1b9c9438b6 | textbox | Circuit Number
68be8785-3844-4b73-a5c1-9e97904a9817 | signoff | Holdpoint / Sign Off
4dcb842c-71aa-4b08-8777-0bec9b5d8b35 | checkpoint | Installation Checks (Insulation damage, Correct Type of Termination, Correct colour code, Correct cable size and labelling)
45f47bb2-021a-5d37-a998-4a36cf1d09aa | textbox | Continuity Test (Resistance - Ohm)
0ed0db4e-708f-5c54-9c44-fb59e01ced08 | textbox | Target (Resistance - Ohm), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1 (refer to Reference Tables - Resistance)
91519b6e-5f26-57ab-a4c2-af1b2f1535f0 | textbox | Insulation Resistance (R-W)
de5cd627-1b5a-564c-b344-4a31036a3a3f | textbox | Insulation Resistance (R-B)
7c88d8d7-bc83-5fff-b8f4-73b044550824 | textbox | Insulation Resistance (W-B)
6eb88265-8c25-5485-b981-77d79f0e4ac6 | textbox | Insulation Resistance (R-N)
0a505a9e-2894-582f-b3e9-555189477464 | textbox | Insulation Resistance (W-N)
a0922a1c-349e-5baa-b372-ca9a0110a26a | textbox | Insulation Resistance (B-N)
ef7cd231-ebcf-5755-804e-b4ea192b4732 | textbox | Insulation Resistance (R-E)
59cde692-d504-51fc-810e-93b68f4cf168 | textbox | Insulation Resistance (W-E)
7e5b4393-6f19-581c-92d0-493e20bdc58f | textbox | Insulation Resistance (B-E)
2fbae03a-08c5-5e44-9a0f-fa95f5173f66 | textbox | Insulation Resistance (N-E)
4f86d47d-01d2-4a96-a7d5-b59ab6b721bc | signoff | Holdpoint / Sign Off
b1c09289-19c3-4f81-8538-ba7857fc5617 | checkpoint | Labelling Installed
d9a4577f-5301-4e64-a7b4-c05979950ee7 | signoff | Holdpoint / Sign Off
da2a4b9d-12ee-4a16-9587-9fdfb3fe4c82 | checkpoint | Cable Terminations to be checked (No loose terminations)
ed39caf0-dbe7-47eb-8ac7-2b9277d78b24 | signoff | Holdpoint / Sign Off
3fc08559-fcbb-4cd3-8723-43e9b779ebe2 | checkpoint | Final acceptance
ee5dc301-8e16-4bc9-95f5-ab1ab266592b | signoff | Final acceptance
42ed166a-46ce-5e95-844d-7cdb894c78c1 | checklist | Power Outlets CxL3 |  | Power Outlets CxL3
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
16565465-1cb5-5884-b8f0-45ed189e142d | checkpoint | CxL2] Power Outlets completed
0bf45d2d-292c-57e1-820a-3d98ad997736 | textbox | Circuit Number
3eb88021-2bc3-5c41-9421-2a3212f766b3 | checkpoint | Polarity (No Transposition)
6916d52a-f665-5bb9-9997-59299c83290a | checkpoint | Polarity (Switch in Active)
074555f3-d486-5b8b-9341-aa9ad60459e2 | textbox | Voltage Check (R-W)
d2b00f1f-9691-526a-99f9-653df766382a | textbox | Voltage Check (R-B)
8e247239-9b01-5cf4-ae9e-f76f61d15e87 | textbox | Voltage Check (W-B)
56efaf13-2c41-5745-b611-026af4b5bee2 | textbox | Voltage Check (R-N)
c43a23cf-d94d-554e-85fb-72d7eb249929 | textbox | Voltage Check (W-N)
455a2797-a88f-57fc-882b-66804d6fda44 | textbox | Voltage Check (B-N)
9f653092-71f1-517d-a290-aa8fe4e20f63 | textbox | Voltage Check (R-E)
5b26eff5-7d01-5276-8b1d-903d4f86c9e5 | textbox | Voltage Check (W-E)
032ceb5d-ab99-5e39-bffe-3a1f1c52c158 | textbox | Voltage Check (B-E)
cb6ade76-c49d-5fca-ad18-c86f800a5ab4 | textbox | Earth Fault Loop Impedance Test (Impedance - Ohm)
27d505be-845e-561c-b622-b4fafed90f2c | textbox | Target (Impedance - Ohm) as per AS/NZS 3017
31db0018-06ae-518c-8c17-ef6e3e7361f2 | textbox | RCD Tripping Test (Trip current)
d3289be8-e96f-5a72-9b0d-8056c49dc11b | textbox | RCD Tripping Test (Tripping time) as per AS/NZS 3017
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
192d00e2-d323-4d46-adc4-2a1f0e938745 | checklist | Power Outlets CxL3 Rev 2 |  | Power Outlets CxL3 Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
ee4b5d9f-2afc-46c0-9c07-f72fa0cb64f4 | checkpoint | Power Outlets CxL2 completed
a05c5efd-f506-5bf1-9965-73501bf3a8e6 | textbox | Circuit Number
3fa959dd-c5fe-4a5d-8ea5-593b20c52c8f | signoff | Holdpoint / Sign Off
d1f04bf8-2bab-48e1-9f31-cebb8f2cd1ef | checkpoint | Polarity (No Transposition)
e6dbae66-5aa7-42a4-858b-1dea192fb21d | signoff | Holdpoint / Sign Off
86f41ac3-6353-4984-95ce-bf80f51838e7 | checkpoint | Polarity (Switch in Active)
819e7b3f-939b-5128-9988-6d0c27dda482 | textbox | Voltage Check (R-W)
585ac085-d92d-5b54-9698-3a705df520dc | textbox | Voltage Check (R-B)
26539206-062a-5deb-8579-7502eda46fde | textbox | Voltage Check (W-B)
bc4b18c4-3c85-5d8d-9e29-4f2d472c279f | textbox | Voltage Check (R-N)
8adca789-14d2-535a-92e0-9f13738024f6 | textbox | Voltage Check (W-N)
2c55446c-c288-55ab-a24f-15bdf2ac7436 | textbox | Voltage Check (B-N)
e1595367-a95f-5947-818c-1e4e6ad0179c | textbox | Voltage Check (R-E)
9f856e21-05c4-5633-8bad-7a9b02cb8cf0 | textbox | Voltage Check (W-E)
119818a2-daf9-51a9-b652-e24af240297b | textbox | Voltage Check (B-E)
f77bf68f-99e3-5c92-b53d-7df48a4fab69 | textbox | Earth Fault Loop Impedance Test (Impedance - Ohm) (refer to Reference Tables - Fault Loop)
4ce8e6b5-07f1-51e5-a23c-de278ce2829d | textbox | Target (Impedance - Ohm) as per AS/NZS 3017 (refer to Reference Tables - Fault Loop)
a5c1abcf-7c0a-5295-a1ce-8833c7f8d1e6 | textbox | RCD Tripping Test (Trip current) (refer to Reference Tables - RCD)
ade2e239-cc16-5665-9d41-86e359ebba6a | textbox | RCD Tripping Test (Tripping time) as per AS/NZS 3017 (refer to Reference Tables - RCD)
827f8e4d-acd6-4dac-b69d-4b96a79727d4 | signoff | Holdpoint / Sign Off
54ab85f6-d54a-425f-ae0b-52dcb677c861 | checkpoint | Final acceptance
739cfb47-8c95-4fca-847e-9ba97c65e591 | signoff | Final acceptance
a19cd1f3-e1e5-59e6-82d4-2403b9d60f8b | checklist | Reference Documents |  | Reference Documents
0b4ad232-5674-51d3-9408-aef0b58a609d | section | Details:
636ba2bb-ace4-5606-a006-e3d9e04ed6d5 | checkpoint | Reference Documents added here.
8a25f6a4-8a6f-530d-91ab-7856b8ac0e9f | checklist | S3-EL-01-ITC-HD5-0001[0] - Cable Tray |  | S3-EL-01-ITC-HD5-0001[0] - Cable Tray
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
c41c831c-ace5-5f7e-bfd9-6418f95611b9 | checkpoint | Correct Location/Area to Drawing
f525af4f-d880-52ed-954b-5493f92dc366 | checkpoint | Correct Size, Type and Spare Capacity
152a21f2-b231-5d6d-9ea9-61afd3dfbc9f | checkpoint | Galvanised / Painted
3dcbb2cf-b675-5763-b930-0d5f0693ccce | checkpoint | Correct Spacing
27e84154-e41a-51ee-8c0b-ed3abf7ce3f1 | checkpoint | Correct Alignment
6d3ac7f9-e503-5085-b2b2-7e27d8dea235 | checkpoint | Correct Brackets and Safe Fixing
266f2897-de20-55df-b28d-e6b59f1d14ee | checkpoint | Clear to Other Services
e7d7f74f-0ec2-539b-8262-0206042415bc | checkpoint | Seismic Supports installed to drawing
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
be5591d6-89e4-42b9-ba65-85060dd3e453 | checklist | S3-EL-01-ITC-HD5-0001[0] - Cable Tray Rev 2 |  | S3-EL-01-ITC-HD5-0001[0] - Cable Tray Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a1b5eee9-ce48-47e0-8fd4-3971f354ec0e | checkpoint | Correct Location/Area to Drawing
8ac54212-bc34-4210-b5f7-3800639acaf6 | signoff | Holdpoint / Sign Off
a9a813bc-f58c-449b-a71c-7b3c4e835b2b | checkpoint | Correct Size, Type and Spare Capacity
e59148d1-f9c7-42e7-94b0-89424d6a9ab0 | signoff | Holdpoint / Sign Off
f56f23f7-9bb8-4a4e-8f03-d00078f2e57e | checkpoint | Galvanised / Painted
b4b3c54e-9435-4a0a-90e4-ef6ffe3a7473 | signoff | Holdpoint / Sign Off
12a3f3ad-b827-4a12-944d-738b227b3f19 | checkpoint | Correct Spacing
f29cb133-607e-4ab3-a1c7-9bd24cb860eb | signoff | Holdpoint / Sign Off
817b9bbf-ea25-444d-a61f-91efab367415 | checkpoint | Correct Alignment
e715e677-1121-46f7-ba8c-3b50f685e1f3 | signoff | Holdpoint / Sign Off
dc69f829-4af9-4fe2-81f8-3e50ae6c6055 | checkpoint | Correct Brackets and Safe Fixing
76deb369-5695-4dae-b9ca-8664e3ac31ae | signoff | Holdpoint / Sign Off
f309ca9f-ae15-4756-bfb4-6b5630f48670 | checkpoint | Clear to Other Services
6323f091-f65a-4658-935f-57f11c38ca81 | signoff | Holdpoint / Sign Off
2d10f24f-e6f9-47b7-95a2-6dc9ba571781 | checkpoint | All Supports, Joints and Bolts tightened
0849f921-8fed-4eac-b031-00da9c58173d | signoff | Holdpoint / Sign Off
e3b2ab51-48b8-41fb-bdb7-4c3f5f0ccb8b | checkpoint | Seismic Supports installed to drawing
72346f95-0c55-42ea-96c1-cb710de089a5 | signoff | Holdpoint / Sign Off
cbac5333-5d98-431b-ae7b-e3c6dc6c82fe | checkpoint | Photo of Cable Tray Installation works
06ad6f67-a0ff-4634-aa66-2ec5e7302260 | signoff | Holdpoint / Sign Off
d0426bcd-ad12-4a49-a6ef-8684ac0726eb | checkpoint | Final acceptance
50ce39de-4f16-4551-8256-bbf2bcce4353 | signoff | Final acceptance
e91a16e7-4d95-5a58-9e3a-61e10c0e878b | checklist | S3-EL-01-ITC-HD5-0012[01] Lighting Control |  | S3-EL-01-ITC-HD5-0012[01] Lighting Control
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5ae48345-4b4a-5412-bc90-b32aa84a3057 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
e9faf6f3-b572-5ad5-af57-d5a11a7fdb0e | textbox | Circuit Number
bf56fa1e-d7bc-52e8-9049-6cd280069783 | checkpoint | Correct Location
89109ce2-b90c-5cf1-ad72-7fc566a6f0b9 | checkpoint | Construction and Finish
8232c6e2-9ec7-5249-9e2f-6ec0bf3d7db2 | checkpoint | Level and Alignment
143b30ef-4fec-5f00-9bf5-18fb7ab1ff50 | checkpoint | Access Provisions
6d0aef00-b661-50a6-b4c8-fc568edda9c1 | checkpoint | Earth Connection
2db307c6-6580-53f4-b085-a8834e9ecc40 | checkpoint | Labelling
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
5d2ce5e8-7ab8-4b9d-bd23-8bd92df81ed6 | checklist | S3-EL-01-ITC-HD5-0012[01] Lighting Control Rev 2 |  | S3-EL-01-ITC-HD5-0012[01] Lighting Control Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
075c40ac-5a97-4a41-8ff0-e3197c9d69a7 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
19eb9fa4-fe0f-5723-a4a3-16a6bca17c7d | textbox | Circuit Number
30184f2d-3fbe-4160-959f-f1c93b316b71 | signoff | Holdpoint / Sign Off
b3acd434-fc54-4655-9b82-9a6c2c62babd | checkpoint | Correct Location
e9b2105c-3cf5-4ac5-8dce-08783d370e3e | signoff | Holdpoint / Sign Off
6d8cb0ec-41fd-4ed0-8279-6ea615580eec | checkpoint | Construction and Finish
ba04001f-3f16-47df-aab2-eac7c5f0bdda | signoff | Holdpoint / Sign Off
25b3991b-8c17-4b1d-b210-aa30a2c64b2a | checkpoint | Level and Alignment
98fc782e-ea53-44ac-85c5-e62b7332c445 | signoff | Holdpoint / Sign Off
ffca3b68-7bce-4fc8-9cfa-8fa64c89b581 | checkpoint | Access Provisions
4034d9dd-6d30-4db4-81f9-d5c17d052c6c | signoff | Holdpoint / Sign Off
e66cdc15-0f78-43da-961b-f08339f1b18f | checkpoint | Earth Connection
e201c006-96be-41ef-8e99-75d163f5d4d9 | signoff | Holdpoint / Sign Off
34dcd4b5-7d88-4011-9600-92e5c2a2084e | checkpoint | Labelling Installed
e1d57d93-f3b2-4330-b174-c0bdd7796ea1 | signoff | Holdpoint / Sign Off
fd2aebd2-b5ca-461e-9dde-2936bfed2c2d | checkpoint | Lighting control panel equipment Installed correctly
9a3b41d0-b477-40a1-a7d5-1a4d61d70dc6 | signoff | Holdpoint / Sign Off
c284956b-8bb6-4544-b848-71bc06e3a1c7 | checkpoint | Cable Terminations to be checked (No loose terminations)
ecb9debc-6a52-4b0c-92ef-6bbab5894443 | signoff | Holdpoint / Sign Off
31276f3d-bae4-4ee9-9d2e-99eae105aae2 | checkpoint | Photo of Lighting control panel equipment Installation works and termination points
25bf4568-ad9f-4bdf-83f1-b84fc44e21d6 | signoff | Holdpoint / Sign Off
bb5f3a5d-22db-484e-a5df-36c023d9bce5 | checkpoint | Final acceptance
1be252ed-1bd4-4581-97e4-7ef831e250c9 | signoff | Final acceptance
c9bad9a0-99f3-5fd9-b1d9-cfddad9a91e4 | checklist | S3-EL-01-ITC-HD5-0036[01] - Control Cable |  | S3-EL-01-ITC-HD5-0036[01] - Control Cable
0b4ad232-5674-51d3-9408-aef0b58a609d | section | Details:
a84b09fd-c3ad-5eec-82d8-c15f1dea7c05 | checkpoint | All prerequisite checks are completed
1e2b73e3-365a-57e6-850d-112b2f0157ef | textbox | From
f6a51651-faec-5937-b1fd-8bbc37f3cdca | textbox | To
8d8d02a1-c1c9-5b57-a87f-765084c892ef | checkpoint | Installation Checks (Insulation damage, Correct Type of Termination, Correct colour code, Correct cable size and labelling)
cf47b0bc-7b0f-5a4c-baad-29395f9a3745 | checkpoint | Continuity Test
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
19e8e2fa-560d-4a7a-b38d-d86d76be85f4 | checklist | S3-EL-01-ITC-HD5-0036[01] - Control Cable Rev 2 |  | S3-EL-01-ITC-HD5-0036[01] - Control Cable Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
529cc883-e139-46da-904c-3a86914e8b21 | checkpoint | All prerequisite checks are completed
2104d942-7a0c-5c04-9bf4-f1efcb578bd1 | textbox | From
fd927e7e-d1df-57d6-ab54-0d7282ad394c | textbox | To
dab53407-ed19-4833-8552-83170ab8e9f1 | signoff | Holdpoint / Sign Off
70e21ff2-d750-4461-9389-359d8f1aba12 | checkpoint | Installation Checks (Insulation damage, Correct Type of Termination, Correct colour code, Correct cable size and labelling)
7777a02a-6f27-4dcc-a147-4bda2fe1ec55 | signoff | Holdpoint / Sign Off
701037d6-008b-461c-b836-59c106f20531 | checkpoint | Continuity Test
97413051-6455-4dc2-97a2-f3c39278da94 | signoff | Holdpoint / Sign Off
f5c5fab3-f9a3-43ce-8ecd-f4708de48935 | checkpoint | Labelling Installed
688b0382-5ab1-4606-91e4-5e62d903d4dc | checkpoint | Cable Terminations to be checked (No loose terminations)
3e255cce-c4ac-4f99-85a2-5f942bbdf0cc | checkpoint | Final acceptance
a8c2e969-41e9-4458-b1f3-267b0d323491 | signoff | Final acceptance
a07bb0c7-ae3a-59cf-8c66-46af034a9481 | checklist | S3-EL-01-ITC-HD5-L2-BUSDUCT |  | S3-EL-01-ITC-HD5-L2-BUSDUCT
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
6276b8c9-ed36-5f90-aac9-feedb88e65d3 | checkpoint | Installation Check
18f0045b-e7f5-53de-89c8-ec4f55f4891d | textbox | From
fc36f5d9-1817-5b15-afd8-1dce7ad9fc9e | textbox | To
6d3ac7f9-e503-5085-b2b2-7e27d8dea235 | checkpoint | Correct Brackets and Safe Fixing
e7d7f74f-0ec2-539b-8262-0206042415bc | checkpoint | Seismic Supports installed to drawing
db3c9d9d-36fb-58b9-b052-45db836e3b1a | textbox | Insulation Resistance (R-W)
1b774c9c-d9b1-5e15-9ab7-e20a33b80077 | textbox | Insulation Resistance (R-B)
e9eaeca0-8107-541f-89f8-5bcfc7c63782 | textbox | Insulation Resistance (W-B)
24a9a568-6af1-5d07-bc69-81190810c9f1 | textbox | Insulation Resistance (R-N)
1355eef9-e8b6-55a0-b1de-98eb09e1c112 | textbox | Insulation Resistance (W-N)
2a788fdb-402b-5223-b01c-ad1bb9c04863 | textbox | Insulation Resistance (B-N)
82ccd3a0-c0f8-57be-a20a-96a952ebded6 | textbox | Insulation Resistance (R-E)
32f2ec99-d338-5772-8dcb-ebe4f6371e9c | textbox | Insulation Resistance (W-E)
2d2986c4-1bce-5439-af25-fd391720aeb4 | textbox | Insulation Resistance (B-E)
183305d0-595d-5e01-944d-0986a4380a69 | textbox | Insulation Resistance (N-E)
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
4e703e7b-6b87-55a3-ad78-f36f42593db3 | checklist | S3-EL-01-ITC-HD5-L2-BUSDUCT ORB |  | S3-EL-01-ITC-HD5-L2-BUSDUCT ORB
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
6276b8c9-ed36-5f90-aac9-feedb88e65d3 | checkpoint | Installation Check
2071ce26-04c4-5347-8a97-5aac1cc9a5b9 | textbox | From
dfe78711-d5f2-5cca-89e7-5b1b5b945a1e | textbox | To
6d3ac7f9-e503-5085-b2b2-7e27d8dea235 | checkpoint | Correct Brackets and Safe Fixing
e7d7f74f-0ec2-539b-8262-0206042415bc | checkpoint | Seismic Supports installed to drawing
c61e1515-0a4f-5b63-bb86-8a33ce0e5f0a | textbox | Insulation Resistance (R-W)
8bfabc2c-fbd9-5fd2-9ba6-2a2618675266 | textbox | Insulation Resistance (R-B)
a9d1d761-0bf9-5f8e-b938-370048c40416 | textbox | Insulation Resistance (W-B)
8c89764f-62ad-51c5-8619-7947d7a6c80b | textbox | Insulation Resistance (R-N)
503d3af7-77f6-5f99-b682-531cc1c1318d | textbox | Insulation Resistance (W-N)
cc9b265f-0b82-5c27-bcc5-b2647bb85033 | textbox | Insulation Resistance (B-N)
d46f7737-dafb-53bb-aab0-5dad4701dd15 | textbox | Insulation Resistance (R-E)
86d8d4db-bbd7-5e03-978e-d37fc5fb7799 | textbox | Insulation Resistance (W-E)
226c403c-292f-54be-a22a-1896b465b03a | textbox | Insulation Resistance (B-E)
efd4152a-1f90-5e34-81f6-da9fb0b8426d | textbox | Insulation Resistance (N-E)
2d933b61-93ce-54c4-8b48-7ef699528243 | textbox | Continuity Testing (A)
21895711-12c2-57e7-8345-01f7af4e2030 | textbox | Continuity Testing (B)
293907be-4174-5b71-98ce-9558f74298a1 | textbox | Continuity Testing (C)
2760778d-cb7e-538a-a742-61b455af2c47 | textbox | Continuity Testing (N)
58324ecf-2868-5cdc-94e6-c959d8943011 | textbox | Continuity Testing (E)
f4a15069-6146-5e19-8aec-450a8c9615a3 | textbox | Target Resistance (Based on 0.1285mΩ / meter)
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
9e93e566-1f46-48db-a910-ae54d6ee572b | checklist | S3-EL-01-ITC-HD5-L2-BUSDUCT ORB Rev 2 |  | S3-EL-01-ITC-HD5-L2-BUSDUCT ORB Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
17ee8afd-ffdc-4801-b983-c218bb447e58 | checkpoint | Installation Check (Supports Installed, Covers Installed)
7a2e87bd-4f0e-5cd9-bd89-d65256ce2e3a | textbox | From
a4a41a9a-b7f7-50ae-acd6-13227f18596b | textbox | To
cf450bd6-0e8c-4d1c-8b90-0742c9844147 | signoff | Holdpoint / Sign Off
d5a9cd56-38b2-488b-8b2f-013f2f74583f | checkpoint | Correct Brackets and Safe Fixing
ae3a2649-7ea0-4450-86bb-3fb0f6f2a11e | signoff | Holdpoint / Sign Off
83c03ba4-86ff-4079-aebe-419f2a9b21a7 | checkpoint | Seismic Supports installed to drawing
3d7ad689-456a-5576-ba67-2e7edaf83dc2 | textbox | Insulation Resistance (R-W)
e147f4b1-c7ca-5cb0-b208-817f143f14b6 | textbox | Insulation Resistance (R-B)
2e1062e3-6b77-5fa3-9e54-b41dce77d027 | textbox | Insulation Resistance (W-B)
5bc37f2f-7d2a-5e62-b23d-803c6d1767f0 | textbox | Insulation Resistance (R-N)
a3998246-0cc4-5f89-b8d5-aff7bd5d3308 | textbox | Insulation Resistance (W-N)
1dca54c8-2428-54f9-8e62-abc1506dca37 | textbox | Insulation Resistance (B-N)
b1886687-a615-5f9f-84d3-14ef700d46f5 | textbox | Insulation Resistance (R-E)
8600a08e-87a5-5ea4-932d-aef24be11cca | textbox | Insulation Resistance (W-E)
7d157673-f2ca-5dce-84f7-e0d11db4a902 | textbox | Insulation Resistance (B-E)
4e4abdce-310b-5dc2-bc8d-cc6e4b3b107e | textbox | Insulation Resistance (N-E)
072e9a16-1bde-5248-a95b-4467ab63e3ca | textbox | Continuity Testing (A)
f754ce3e-9b28-5fc7-925e-3097c4b31298 | textbox | Continuity Testing (B)
449492ee-d4b4-539b-8c70-c648fcdf2d04 | textbox | Continuity Testing (C)
e76e400c-15c1-59e5-bb6f-44b7cbf529e2 | textbox | Continuity Testing (N)
7f9cd2d1-37d7-5266-8738-3285375e6b22 | textbox | Continuity Testing (E)
22fb4917-4175-5833-890e-3d0ffc5b2142 | textbox | Target Resistance Note - Value to be based on 0.1285mΩ / meter
2cc564ca-88a0-4abd-adcc-fc68cd527e49 | signoff | Holdpoint / Sign Off
5749e419-f28a-403a-aad9-123401512b97 | checkpoint | Photo of Busduct Installation works
2b55f640-1170-4aaa-a109-0585564f00ed | signoff | Holdpoint / Sign Off
53d8577e-d5f0-4497-b382-fceec822a261 | checkpoint | Final acceptance
40521928-1fc7-486a-a1f5-c9a04263f25d | signoff | Final acceptance
703c42aa-d2db-478f-b5ae-c5b136bf1843 | checklist | S3-EL-01-ITC-HD5-L2-BUSDUCT Rev 2 |  | S3-EL-01-ITC-HD5-L2-BUSDUCT Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
c17e8888-be7c-4d0a-89b2-732d8af3c79c | checkpoint | Installation Check (Bolts Torqued, Supports Installed, Covers Installed)
431ec692-7d42-5cc2-b081-4b543c14f1fc | textbox | From
7f144e13-1c21-545d-b5de-cd7bc2617ef4 | textbox | To
0a2962ec-f52f-4fa3-8742-42dcff08d21b | signoff | Holdpoint / Sign Off
dce82cb1-1b6e-40c4-bfa7-535383600c68 | checkpoint | Busduct Torqued and marked at termination points
c04fcb44-70b4-4d12-895e-58477d2e6b1c | signoff | Holdpoint / Sign Off
0e509237-6bcf-4424-9971-a021a3bdada8 | checkpoint | Correct Brackets and Safe Fixing
5cf174e8-5d48-4ca8-a027-24ecb8feb88e | signoff | Holdpoint / Sign Off
a74692c1-d8b0-4234-b30f-de244580e191 | checkpoint | Seismic Supports installed to drawing
e5372c80-474c-5d1c-bffc-66d7d0966445 | textbox | Insulation Resistance (R-W)
7345d062-a599-5361-aa97-8cd2e4c993e3 | textbox | Insulation Resistance (R-B)
f6dc1bd1-8a1c-5231-8d98-c6d6b8533d1b | textbox | Insulation Resistance (W-B)
d55b1486-a430-5d4e-aa47-62dbe251422c | textbox | Insulation Resistance (R-N)
fac0032f-13f3-546c-9747-337f037ed43e | textbox | Insulation Resistance (W-N)
ce0cd6ac-5ace-5da4-8f2e-d0e3d4d6f48b | textbox | Insulation Resistance (B-N)
4e0b5471-21cf-55ce-a3fd-c38a8aa3c381 | textbox | Insulation Resistance (R-E)
7f1adcff-9ad0-5dc0-937f-7ce847493ba5 | textbox | Insulation Resistance (W-E)
37b310d3-b850-5791-8a8b-d30b5819e0c9 | textbox | Insulation Resistance (B-E)
63013f2b-6f85-5604-9d89-cab8e7a9b7a2 | textbox | Insulation Resistance (N-E)
efa71535-434e-5050-90de-5aca5bedebbc | textbox | Ductor Test Results to be attached
e42ce36f-7b2b-4cc2-bae7-98f156d56bae | signoff | Holdpoint / Sign Off
d9f5a3c1-a9d6-492c-b341-c4403bc224b7 | checkpoint | Photo of Busduct Installation works and Termination points
45eca633-7b0c-4fa0-b798-9841cb9e1cca | signoff | Holdpoint / Sign Off
f3d9234b-9fd5-4d31-9aee-5842724cbf4a | checkpoint | Final acceptance
9eb71a85-3a7e-489c-875d-10732dbea3fb | signoff | Final acceptance
7bef294a-07d3-5e85-bd8b-3a36835ef630 | checklist | S3-EL-01-ITC-HD5-L2-EARTHING |  | S3-EL-01-ITC-HD5-L2-EARTHING
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a84b09fd-c3ad-5eec-82d8-c15f1dea7c05 | checkpoint | All prerequisite checks are completed
391cf018-94d9-5811-8a68-4874d32e695d | textbox | From
98baed7c-c663-575c-9c44-edf533cb6a49 | textbox | To
a3c0cc8f-0c4e-5fae-9d7f-3a45ae97b007 | checkpoint | Visual Checks
99732e99-d047-5937-a853-0a34f52f8e18 | checkpoint | Continuity Test, Continuity test is to ensure continuity of the earthing conductor with the earthing system
b545b635-b3fd-5c32-a59e-8261ef9d12bd | textbox | Continuity Test (Resistance - Ohm), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
e14a7577-94a2-4a05-a123-2a637e68af54 | checklist | S3-EL-01-ITC-HD5-L2-EARTHING Rev 2 |  | S3-EL-01-ITC-HD5-L2-EARTHING Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
57c3ba4c-fcfd-4e79-bb9a-83823f608c21 | checkpoint | All prerequisite checks are completed
8a11ce34-377f-59f4-a73d-f006434ae6ba | textbox | From
0ac0f297-373b-5c64-8287-059b0c35ac2c | textbox | To
5a25bdf7-77d3-4184-86bb-0991d6a4cacf | signoff | Holdpoint / Sign Off
f45f129c-859f-4234-9f47-3d5d7853562f | checkpoint | Installation Checks (Insulation damage, Correct Type of Termination, Correct colour code, Correct cable size and labelling, Correct cable routing and diverse path where required)
96931907-2f0b-4d33-b6b8-4794912889f8 | signoff | Holdpoint / Sign Off
673e6e19-9acb-4f70-8eb5-c4541186c8a0 | checkpoint | Continuity Test, Continuity test is to ensure continuity of the earthing conductor with the earthing system
a1b8641d-4a28-56b1-8c5e-a3b71825eeb4 | textbox | Continuity Test (Resistance - Ohm), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1 (refer to Reference Table - Resistance)
43896808-628f-5b07-ab10-c58cc73886b7 | textbox | Target (Resistance - Ohm), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1 (refer to Reference Table - Resistance)
828febd0-45b6-49fc-9375-d472365386c7 | signoff | Holdpoint / Sign Off
1f2736b2-b955-409c-b780-692c7cd8f7f7 | checkpoint | Labelling Installed
5c903758-924b-4d68-a575-3ada1abdcc97 | signoff | Holdpoint / Sign Off
590ac73e-4d29-4e27-83db-8792925457ed | checkpoint | Cable Terminations to be torqued and marked
713129c1-1cc4-403a-bc96-240140bb66f1 | signoff | Holdpoint / Sign Off
1fc7e50d-6fc5-4e8b-b27c-a80558d8d0d7 | checkpoint | Switchgear to be cleaned
b94d4479-3060-40bb-8a5d-1470b1fa6acc | signoff | Holdpoint / Sign Off
80d2d020-a914-46ca-9f89-61d70ceb583b | checkpoint | Photo of Earthing Installation works and termination points
8a0a1db8-a832-4153-9eb0-ceea089e5330 | signoff | Holdpoint / Sign Off
7718d4a5-3722-46c4-8052-b6b97189bacf | checkpoint | Final acceptance
3b5e1003-1f82-469f-a2e5-a9aa64d43da8 | signoff | Final acceptance
53ec6695-1d96-52bc-9129-b3c0097d22d8 | checklist | S3-EL-01-ITC-HD5-L2-EMLIGHTING |  | S3-EL-01-ITC-HD5-L2-EMLIGHTING
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5ae48345-4b4a-5412-bc90-b32aa84a3057 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
8171b770-64c8-5c4a-8f6b-585a3db2a3de | textbox | Circuit Number
bf56fa1e-d7bc-52e8-9049-6cd280069783 | checkpoint | Correct Location
89109ce2-b90c-5cf1-ad72-7fc566a6f0b9 | checkpoint | Construction and Finish
8232c6e2-9ec7-5249-9e2f-6ec0bf3d7db2 | checkpoint | Level and Alignment
143b30ef-4fec-5f00-9bf5-18fb7ab1ff50 | checkpoint | Access Provisions
6d0aef00-b661-50a6-b4c8-fc568edda9c1 | checkpoint | Earth Connection
2db307c6-6580-53f4-b085-a8834e9ecc40 | checkpoint | Labelling
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
bfa7fabe-e99c-45bb-9332-6e66008defff | checklist | S3-EL-01-ITC-HD5-L2-EMLIGHTING Rev 2 |  | S3-EL-01-ITC-HD5-L2-EMLIGHTING Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
aacad64a-2eb2-4767-86ec-e48999cfbc17 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
9c5a2ee0-6921-54b5-aaff-4910a75ab20b | textbox | Circuit Number
4973f3ea-95a2-434c-8db6-d4a76bf0a586 | signoff | Holdpoint / Sign Off
1baa0341-5a36-4ccb-932d-760f568638fa | checkpoint | Correct Location
882a4421-997a-462c-bdbd-01f6b2de2d23 | signoff | Holdpoint / Sign Off
a97563cf-84ba-4209-8fbb-4111ad0e076d | checkpoint | Construction and Finish
7556973d-fbd1-4b20-b420-9837fe1b9ff8 | signoff | Holdpoint / Sign Off
7e28a914-6ee1-438a-9f03-31865dd9b018 | checkpoint | Level and Alignment
4878b76f-793b-4706-93b1-a276277bfb13 | signoff | Holdpoint / Sign Off
41d9e034-3eca-42e5-ace0-4ec8fc27d7d9 | checkpoint | Access Provisions
f1734eef-f691-48a3-9018-bdc134bf0bad | signoff | Holdpoint / Sign Off
adbdb461-7c48-44c1-87c4-a7200343c66b | checkpoint | Earth Connection
13293e66-2330-4f01-b06b-2b292ed41a5e | signoff | Holdpoint / Sign Off
f158d2b9-5968-4f98-b5c0-65b2837df880 | checkpoint | Labelling Installed
96d754fc-df9a-4c8b-82f0-076c9e5c85b8 | signoff | Holdpoint / Sign Off
a71b1463-01ba-44c1-8133-186df63766fe | checkpoint | Emergency Lighting control panel equipment Installed correctly
26ce2abe-a875-4017-b491-df3f8d00fbad | signoff | Holdpoint / Sign Off
67094ea3-f021-4833-8f3f-091533b4bf6a | checkpoint | Cable Terminations to be checked (No loose terminations)
d346ceb3-e04d-454e-81aa-9eb0bc80e260 | signoff | Holdpoint / Sign Off
ce3876ce-193c-4f4a-a0bf-10d7de4ac606 | checkpoint | Photo of Emergency Lighting control panel equipment Installation works and termination points
094c82a9-00bf-4d67-b583-eeb8cc30b1bf | signoff | Holdpoint / Sign Off
aeb1b1fb-6790-4c07-af74-f04565518552 | checkpoint | Final acceptance
29825b84-f137-49b0-b0e5-7708c0b3c70f | signoff | Final acceptance
229fba82-4ed5-52ce-afbb-596fa44557d3 | checklist | S3-EL-01-ITC-HD5-L2-LVCABLE |  | S3-EL-01-ITC-HD5-L2-LVCABLE
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5ae48345-4b4a-5412-bc90-b32aa84a3057 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
00c8a887-df1c-5fb0-a9fe-c5ad1527852d | textbox | From
0757a4f2-8915-5375-bdc2-fbdc52b04ea9 | textbox | To
ed38db4c-1f0e-5fe8-bade-90c011836b8b | checkpoint | Insulation damage
a9cc2e4c-f587-5914-968b-b5d08732c5e4 | checkpoint | Correct Type of Termination
990338ba-59f3-51ca-8ffd-2f2ae1bc501e | checkpoint | Correct colour code, As per Low Voltage Cable Schedule
29f0cc53-8632-5eeb-b46d-e4d5e8d768c0 | checkpoint | Correct cable size and labelling, As per Low Voltage Cable Schedule
4f6a10a6-b4fc-5058-96cf-14852e868e0d | checkpoint | Correct cable routing and diverse path where required, As per layout drawings
7309e322-910b-58e7-8ff4-c5ca18f8e146 | textbox | Insulation Resistance (R-W), A minimum resistance value of 1 Megaohm is required
4b3535ba-e4ce-570b-930f-e8d3fb32e5c9 | textbox | Insulation Resistance (R-B), A minimum resistance value of 1 Megaohm is required
18cc107b-9976-515f-a2cd-ada545bdc115 | textbox | Insulation Resistance (W-B), A minimum resistance value of 1 Megaohm is required
c8f75e3b-e679-5fbf-8908-1d9e8d840eee | textbox | Insulation Resistance (R-N), A minimum resistance value of 1 Megaohm is required
78187705-34f0-58ce-871d-8717133f14d2 | textbox | Insulation Resistance (W-N), A minimum resistance value of 1 Megaohm is required
d075135e-311b-5eaa-8707-743ceca8ef5a | textbox | Insulation Resistance (B-N), A minimum resistance value of 1 Megaohm is required
133c0c90-df8b-57dc-b0c0-25fbba466f9b | textbox | Insulation Resistance (R-E), A minimum resistance value of 1 Megaohm is required
efc33263-c472-5524-a36b-58fbf746f1f3 | textbox | Insulation Resistance (W-E), A minimum resistance value of 1 Megaohm is required
3aee0a21-5007-5e60-adfb-122ff7f2dce0 | textbox | Insulation Resistance (B-E), A minimum resistance value of 1 Megaohm is required
8490e555-304d-5c91-a2eb-b0e888b0aa4f | textbox | Insulation Resistance (N-E), A minimum resistance value of 1 Megaohm is required
58be4899-6aba-5252-beac-7fd4a58a4a31 | textbox | Continuity Test (A), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1
fbe676cb-176e-50e8-8ba2-c94970a4034a | textbox | Continuity Test (B), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1
a586194e-f81e-51f3-a254-2042869fcfda | textbox | Continuity Test (C), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1
3e6166bc-ed75-5816-a2ad-0bb15fc59411 | textbox | Continuity Test (N), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1
621e3846-6a48-58bd-a212-3da5fdc74ffe | textbox | Continuity Test (E), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
ee7ba9c3-d392-4f54-a70a-235196fabe52 | checklist | S3-EL-01-ITC-HD5-L2-LVCABLE Rev 2 |  | S3-EL-01-ITC-HD5-L2-LVCABLE Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1ef9ea67-d920-42a8-947e-308097b015c5 | checkpoint | All prerequisite checks are completed, Installation of upstream and downstream switchboard/equipment is completed
e6b187f3-0676-5fb5-ab4b-b8e939dc3989 | textbox | From
9414926f-6ccc-5d8a-993c-33c1b84983e6 | textbox | To
17449a3d-7f63-45fb-a48c-b731b4c739a3 | signoff | Holdpoint / Sign Off
17f6f348-a9a4-4370-a7da-60c0e8f9a02c | checkpoint | Installation Checks (Insulation damage, Correct Type of Termination, Correct colour code, Correct cable size and labelling, Correct cable routing and diverse path where required)
6abb2e22-b12b-5a7a-9e42-67eb19d5567c | textbox | Insulation Resistance (R-W), A minimum resistance value of 1 Megaohm is required. Test shall be conducted at 1000V
b4ae2ecc-615c-5b17-9833-8317b210decc | textbox | Insulation Resistance (R-B), A minimum resistance value of 1 Megaohm is required. Test shall be conducted at 1000V
99428ece-6a6b-5bbe-87f2-abce6db5655b | textbox | Insulation Resistance (W-B), A minimum resistance value of 1 Megaohm is required. Test shall be conducted at 1000V
06cf6d5f-d8a0-5a3f-851a-bbaf5abb84ca | textbox | Insulation Resistance (R-N), A minimum resistance value of 1 Megaohm is required. Test shall be conducted at 1000V
5c8f8885-105b-5051-ac0b-63731c06e3af | textbox | Insulation Resistance (W-N), A minimum resistance value of 1 Megaohm is required. Test shall be conducted at 1000V
14347326-e18a-5a2d-b0a4-c3a1d33c6da7 | textbox | Insulation Resistance (B-N), A minimum resistance value of 1 Megaohm is required. Test shall be conducted at 1000V
77d07e81-ab1d-5f6b-87e7-536f9dda0ccf | textbox | Insulation Resistance (R-E), A minimum resistance value of 1 Megaohm is required. Test shall be conducted at 1000V
355ef9b0-e7b7-5065-b362-935f469b4458 | textbox | Insulation Resistance (W-E), A minimum resistance value of 1 Megaohm is required. Test shall be conducted at 1000V
797fa8cc-1875-5ec9-929a-c7fa6d2ae871 | textbox | Insulation Resistance (B-E), A minimum resistance value of 1 Megaohm is required. Test shall be conducted at 1000V
9b3b457c-0b20-592f-adcc-09907c17e11b | textbox | Insulation Resistance (N-E), A minimum resistance value of 1 Megaohm is required. Test shall be conducted at 1000V
d4cea94b-dbfa-5bce-8cd4-8d550f85217f | textbox | Continuity Test (A), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1 (refer to Reference Tables - Resistance)
79878987-9403-54d0-b885-0986d5ecee0f | textbox | Continuity Test (B), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1 (refer to Reference Tables - Resistance)
d031f99e-6dfe-5f31-bb30-b12aa145c377 | textbox | Continuity Test (C), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1 (refer to Reference Tables - Resistance)
1fda102c-fef0-56d0-b855-8e0b2c19f99f | textbox | Continuity Test (N), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1 (refer to Reference Tables - Resistance)
d71e7672-ef10-5f56-800e-da60fe78f67f | textbox | Continuity Test (E), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1 (refer to Reference Tables - Resistance)
76681a6d-e3ed-5fde-879c-17411a909a87 | textbox | Target (Resistance - Ohm), Values of resistance shall be in accordance with Table 1 from AS/NZS 3008 1.1 (refer to Reference Tables - Resistance)
07c62b32-6eb7-460b-bae5-05c1005caed8 | signoff | Holdpoint / Sign Off
c36b77e9-0dc8-4fc8-b220-0f9581e4f82d | checkpoint | Labelling Installed
7d382b0e-3171-4110-be6e-fa4ff1c32792 | signoff | Holdpoint / Sign Off
aab2a500-1ea1-4a6e-bb62-b3cc3d646cb5 | checkpoint | Cable Terminations to be torqued and marked
ad8fbbf3-51f5-4f3f-86c8-cbe7c40e83c2 | signoff | Holdpoint / Sign Off
b2c02df3-da25-4d36-b117-7933d079661c | checkpoint | Switchgear to be cleaned
93e593c9-8b5d-460f-a675-2adc180bd6cd | signoff | Holdpoint / Sign Off
faa24ff8-c7dd-43af-a9e1-c3c9b659c6eb | checkpoint | Photo of Submain Installation works and termination points
17c4c019-7d37-4e2e-8d7a-93734ec548d6 | signoff | Holdpoint / Sign Off
47ea652f-3b5e-4b27-8df7-a8eb851e4ea6 | checkpoint | Final acceptance
40734fcb-c0c0-4bd1-9b59-139ecee92c15 | signoff | Final acceptance
4c2b3127-547c-5e63-9744-46d9e7131485 | checklist | S3-EL-01-ITC-HD5-L2-LVDB |  | S3-EL-01-ITC-HD5-L2-LVDB
0b4ad232-5674-51d3-9408-aef0b58a609d | section | Details:
a84b09fd-c3ad-5eec-82d8-c15f1dea7c05 | checkpoint | All prerequisite checks are completed
cc286d66-1c3c-5d3c-8649-9f446239f365 | textbox | Distribution Board Name
8d8d02a1-c1c9-5b57-a87f-765084c892ef | checkpoint | Installation Checks (Insulation damage, Correct Type of Termination, Correct colour code, Correct cable size and labelling)
63853d11-9dca-5600-bc1d-74642e5448ba | checkpoint | GENERAL: External Paint colour & finish (visual inspection) as per drawing
5d4ad826-fd10-5ee4-81bc-bc14726f2b44 | checkpoint | GENERAL: Internal Paint colour & finish (visual inspection) as per drawing
f3207d03-e3e0-59a3-aaf7-cb22c3b699be | checkpoint | GENERAL: Method of construction matches IP rating on drawing:
6e2d49e2-93e9-5bf6-b606-85981645b9b4 | checkpoint | GENERAL: Equipment fitted square & neatly
57c92516-3c2d-5258-9bfc-cba588876d90 | checkpoint | GENERAL: Doors open & close satisfactory, latches close satisfactory
4572660c-d49c-5332-b43b-65bf1219690f | checkpoint | GENERAL: Door Lock / latch Keys supplied (if applicable)
d2a0dd3d-2312-567d-9f1d-80f6e6b7bb40 | checkpoint | GENERAL: Correct Gland plate material used as per drawing.
b7786953-a932-506b-9975-3b056ef9cf12 | checkpoint | GENERAL: Schedule Holder fitted (if applicable)
20f25061-e2d0-5bd0-b859-0575f88ec895 | checkpoint | GENERAL: Connection Q.A stickers fitted in each compartment
01c4f881-0ea4-5445-99e2-e8db5f424cb9 | checkpoint | LABELLING: Wording checked against drawing
9a02e075-cbb9-53be-9779-63b18acc3fb6 | checkpoint | LABELLING: All standard labels fitted e.g. Control fuses behind etc
e6fedff3-7838-5fab-86b1-42956b4072b7 | checkpoint | LABELLING: SMBQ AS/NZS61439 rating plate label fitted
4f5d2471-6d0f-5a0f-b896-4a901d390428 | checkpoint | LABELLING: All Warning labels fitted including discrimination label
8bef0351-53b2-5d89-969b-c5abc8770283 | checkpoint | LABELLING: Label fixing: nylon pins or self adhesive tape
9d7706e8-0aea-517d-b5d1-c5f99e820b79 | checkpoint | LABELLING: All internal labels fitted neatly & straight.
628332c9-d7f0-5407-8166-22a0451570c5 | checkpoint | LABELLING: "Authorised Access" & "Danger 415V" stickers fitted
eea5d6f4-b661-511e-8dad-9302bb4b86b0 | checkpoint | LABELLING: "Alternate Supplies" warning label fitted where applicable
8974f73a-6ccb-5020-90d9-5053f17b3347 | checkpoint | LABELLING: Labelling complete
b6a8bfe7-e8f0-5a42-8b16-e00a660c745b | checkpoint | SWITCHGEAR: Switchgear Ratings checked & Quantities checked against drawing
c06b6f2e-bd1a-510b-be65-519eeec4d7e4 | checkpoint | SWITCHGEAR: Switchgear Trip Units set as per discrimination study
ce71389d-dda3-5877-a116-a1d5a5ea3484 | checkpoint | SWITCHGEAR: Contactors & overloads ratings checked against drawing
b5d57178-88d5-5058-b9d3-33558de9b0f1 | checkpoint | SWITCHGEAR: Mechanical interlocks fitted & operated correctly
df630f75-f64b-5acc-8059-8eb7b11ab5a2 | checkpoint | SWITCHGEAR: Fuse links continuity check
a24d3b1c-ac4d-535a-b81d-e5ea296e0a22 | checkpoint | BUSBARS: Busbar sizes checked against drawing
06ed662c-0e22-5071-9ae5-f7e481179ea4 | checkpoint | BUSBARS: Minimum Clearance (19mm phase to phase & 16mm phase to Earth)
8439454b-7625-52e4-8cef-52aa7dae846c | checkpoint | BUSBARS: Busbar supports/cleats in correct locations
d54be04b-5007-594e-93a5-914867bb9bb9 | checkpoint | BUSBARS: Bolted phase connections torque tightened and check marked on nuts
d66d586a-41b6-5e94-a350-f0c3f4a5bafc | checkpoint | BUSBARS: Bolted Neutral connections torque tightened & check marked on nuts
9b4bed4a-a1e9-51d8-80b0-1ef2bb10a439 | checkpoint | BUSBARS: Bolted Earth connections torque tightened & check marked on nuts
90dfb812-f918-57d8-8904-9c80cfb409d8 | checkpoint | BUSBARS: Earth connections bolts stamped
a8e918b8-67de-54c0-af51-c06cee726106 | checkpoint | BUSBARS: Neutral connections bolts stamped
004dfd64-0c15-5cff-9927-2dd06e83ec7c | checkpoint | BUSBARS: Hardware 8.8 high tensile bolts used on joints (Torque settings: M8 = 30Nm M10 = 40Nm M12 = 60Nm)
fbe6f861-beb2-5691-aed2-f0b65257a554 | checkpoint | BUSBARS: Phase colour coding correct and checked against drawing
d726ddac-b07f-51b2-a817-485bb8115eee | checkpoint | BUSBARS: Covering - i.e. PVC dipping, PVC sleeving, heat shrink or NIL
7268a2f7-00f0-5ef2-a665-ebeb489fdf97 | checkpoint | BUSBARS: Busbar joints wrapped satisfactory
34693fc9-a06c-5c2a-aed0-9e3c8d1898aa | checkpoint | BUSBARS: Busbar flags for Submains suitable for cables
d12a5199-5019-53da-845e-3cbda4943a25 | checkpoint | BUSBARS: Bolts suitable type and length for cables
7c685e49-fcd8-559c-96fc-04521338ab09 | checkpoint | WIRING: Colour coding on power cable lugs represents correct phasing
dde0a6fe-779e-5f0d-abbd-408e9189bfe6 | checkpoint | WIRING: Correct Colour colouring on control wiring used for each applicable voltage.
71fff98b-9a2a-5bb1-adc9-1996640a3d22 | checkpoint | WIRING: Terminal connections tight & correctly fitted.
45512d1d-4d6e-562a-9d69-d5fb28a0556b | checkpoint | WIRING: Slotted cable duct adequately sized as per drawings.
d7856700-e229-5bc7-919e-adfe296d2ab7 | checkpoint | WIRING: Cable sizes correct and sized as per drawing.
e771714a-a92b-5a58-8f29-a1cf926c6788 | checkpoint | WIRING: Wire numbers fitted
b6feedc9-4d72-58a7-87e3-03c6f8c151dd | checkpoint | WIRING: Terminal numbers fitted where specified
22b97f0b-1404-570d-bfa6-d174410dcd77 | checkpoint | WIRING: Control Circuit functionality
4320fce9-c02e-5e51-b75c-b38c98b69fbc | checkpoint | WIRING: Point to point check control wiring as per drawings
f1da2577-e379-5adc-967d-bb5c053e3177 | checkpoint | MISCELLANEOUS ITEMS: 2 x Spare Keys for 1/4 Turn locks supplied secured inside board.
1fa3c171-2443-5a71-ac2d-b86929dc5fd5 | checkpoint | MISCELLANEOUS ITEMS: Keys for Selector switches supplied secured inside board.
241de48b-8209-53f4-b739-d41778c3fadc | checkpoint | MISCELLANEOUS ITEMS: Earth continuity between framework of shipping sections (Acceptance Criteria = equal or less than 0.5Ω)
c89686b4-a549-5a22-b20b-bb2cb5c86ea5 | checkpoint | MISCELLANEOUS ITEMS: Earth continuity between earth bar & frame (Acceptance Criteria = equal or less than 0.5Ω)
59bb467a-1ff2-5c3b-b971-ee89c47fcef2 | checkpoint | MISCELLANEOUS ITEMS: Earth continuity between earth bar & doors (Acceptance Criteria = equal or less than 0.5Ω)
814bd629-03fd-5ccd-9600-c7dc3b6a8501 | checkpoint | MISCELLANEOUS ITEMS: Operating instructions for Time switch / Time delays etc. supplied with switchboard
ff52c175-2d1d-5e7f-87b3-59e0b6d2beb0 | checkpoint | MISCELLANEOUS ITEMS: Heatshrink has been supplied for cable terminations
fccfca79-5b3e-5a3c-b496-685160052a02 | textbox | Insulation Resistance (R-W), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
79ef3a95-34e4-55ea-81d0-876495559237 | textbox | Insulation Resistance (R-B), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
8f96fe7b-9b14-5385-bd0d-7863e79ced20 | textbox | Insulation Resistance (W-B), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
6a5755d1-1a58-59eb-a668-b416c9306e7f | textbox | Insulation Resistance (R-N), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
7da0a28e-1d5b-5816-a85b-064c0e5ae3d8 | textbox | Insulation Resistance (W-N), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
0f3a3cd1-faa2-57f5-9390-b2e48f237b4e | textbox | Insulation Resistance (B-N), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
416bd39e-14cc-5116-ac4d-e688944845cd | textbox | Insulation Resistance (R-E), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
1746239c-1e88-5b9d-8cba-e8db859b0c51 | textbox | Insulation Resistance (W-E), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
68458ef3-669b-51ac-93ac-847ce56c8e36 | textbox | Insulation Resistance (B-E), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
fc7b123e-dc84-5974-ab21-07cb2d17c9de | textbox | Insulation Resistance (N-E), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
184c2cc0-1628-528b-890a-a0011b84ba3b | textbox | Ductor Test R
612cff15-aa16-554f-8c08-735713823ba6 | textbox | Ductor Test W
edb4795e-9af2-5717-b964-786fa79ec508 | textbox | Ductor Test B
5c685e2a-5273-5164-a098-1b3cbccbf965 | checkpoint | FUNCTIONAL CHECK: ACB/MCCB Settings Check:
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
5bb25843-49ab-432d-a1a4-dbae41956644 | checklist | S3-EL-01-ITC-HD5-L2-LVDB Rev 2 |  | S3-EL-01-ITC-HD5-L2-LVDB Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
83d8d2cb-b3ee-4f1b-a6b3-66c3ea0ff736 | checkpoint | All prerequisite checks are completed
48538f28-ec0d-50ab-947f-e5debfbe38fc | textbox | Distribution Board Name
d53217a3-dfb5-4dd5-897c-c5e3e3062da3 | signoff | Holdpoint / Sign Off
feaf2641-d757-4dea-a8eb-81574f39c481 | checkpoint | Installation Checks (Insulation damage, Correct Type of Termination, Correct colour code, Correct cable size and labelling)
795a3022-6db4-4340-87c1-1c9c3bbc949c | signoff | Holdpoint / Sign Off
6c0e1694-756e-4cf9-8f23-3933a81ef17b | checkpoint | GENERAL: External Paint colour & finish (visual inspection) as per drawing
69bc5e58-0921-4645-8283-227b8a3c0df9 | signoff | Holdpoint / Sign Off
b396275e-ae56-4f3a-b662-dd4c50a6a303 | checkpoint | GENERAL: Internal Paint colour & finish (visual inspection) as per drawing
d8a15b5a-fe49-4571-8601-f24343f7317c | signoff | Holdpoint / Sign Off
0627f2c5-88de-4da8-81df-77a0d3e550ba | checkpoint | GENERAL: Method of construction matches IP rating on drawing:
9648b4ba-cf09-4059-81db-72f671106619 | signoff | Holdpoint / Sign Off
119dadb8-d1e5-4c2c-a0f8-7ccc0810fafb | checkpoint | GENERAL: Equipment fitted square & neatly
4a2301c8-443b-4882-afa4-273385842eca | signoff | Holdpoint / Sign Off
2570b7d5-ef58-431f-9073-d44731984393 | checkpoint | GENERAL: Doors open & close satisfactory, latches close satisfactory
18d2374e-9372-462c-b67d-4ef055ef8b2d | signoff | Holdpoint / Sign Off
8a75c148-0b33-49d9-9f42-940d0a4a5bed | checkpoint | GENERAL: Door Lock / latch Keys supplied (if applicable)
987bdb4e-503c-45c1-9afc-7be0b7bc583f | signoff | Holdpoint / Sign Off
6f7e608e-fe4c-4222-b9cc-e6f1583a1342 | checkpoint | GENERAL: Correct Gland plate material used as per drawing.
899508d3-010c-4891-8bb8-72fce376111e | signoff | Holdpoint / Sign Off
3784ef9b-392b-4d6d-b773-2e197c575658 | checkpoint | GENERAL: Schedule Holder fitted (if applicable)
e4588acc-028f-4a87-81a8-5de30470d2bb | signoff | Holdpoint / Sign Off
eaf289fa-ae0a-422c-aa38-84f914338730 | checkpoint | GENERAL: Connection Q.A stickers fitted in each compartment
c838f8d8-4120-4d9e-8816-b0ed7ee894a1 | signoff | Holdpoint / Sign Off
909b4d91-a2d6-4221-8a3e-66e820659406 | checkpoint | LABELLING: Wording checked against drawing
776fadd1-8365-47dc-8423-3bd1b5901dba | signoff | Holdpoint / Sign Off
456744f8-e180-4a05-b277-aec037e375cc | checkpoint | LABELLING: All standard labels fitted e.g. Control fuses behind etc
90295bf3-fe92-459a-b712-9e207ea11a07 | signoff | Holdpoint / Sign Off
833f341d-3f7c-4ab2-868a-a6548fa5cc42 | checkpoint | LABELLING: SMBQ AS/NZS61439 rating plate label fitted
dec85546-3ab0-437e-b719-e25dbea62c3f | signoff | Holdpoint / Sign Off
f0e206e0-1767-4803-a8bd-fc832a56d5fd | checkpoint | LABELLING: All Warning labels fitted including discrimination label
292fff99-902a-4d1a-a571-ce08ca19d7ed | signoff | Holdpoint / Sign Off
29b76ca1-235f-45bd-b163-20cefc969ec0 | checkpoint | LABELLING: Label fixing: nylon pins or self adhesive tape
d7692e41-1d45-4337-bcd4-590521ce8fc5 | signoff | Holdpoint / Sign Off
67aa13e9-6511-4579-97e4-87b4a7184dad | checkpoint | LABELLING: All internal labels fitted neatly & straight.
0cbbfc28-5bbd-461d-bf9d-90d1f9a6405f | signoff | Holdpoint / Sign Off
7414a5d1-abd0-4f03-a069-286b56acf4d7 | checkpoint | LABELLING: "Authorised Access" & "Danger 415V" stickers fitted
557a18e1-0054-4a9e-b163-d9456837b7eb | signoff | Holdpoint / Sign Off
93ee3766-3009-40a5-a6a5-d8bce7892ef6 | checkpoint | LABELLING: "Alternate Supplies" warning label fitted where applicable
8d3ec77f-ba2a-49fa-bd74-fd26d10a14ad | signoff | Holdpoint / Sign Off
786d4939-8bfb-4ca6-83cb-a154fbe74e1a | checkpoint | LABELLING: Labelling complete
830c490b-a129-4c84-b6c0-85c86b2420bb | signoff | Holdpoint / Sign Off
cc5521cd-1217-4bf1-8065-dafc57df4ad9 | checkpoint | SWITCHGEAR: Switchgear Ratings checked & Quantities checked against drawing
1dae7a99-676c-4d52-8891-255f69daa20f | signoff | Holdpoint / Sign Off
e9080325-24da-4607-974f-8f79b44da331 | checkpoint | SWITCHGEAR: Switchgear Trip Units set as per discrimination study
88474f93-9650-4899-b513-bb4a6de45416 | signoff | Holdpoint / Sign Off
d802626a-3b4a-4dc2-8b57-1c2ec6a3e717 | checkpoint | SWITCHGEAR: Contactors & overloads ratings checked against drawing
2ea51015-889a-44f4-a94b-107773721aa4 | signoff | Holdpoint / Sign Off
ab6bf224-787d-464f-bdcd-96529e718eec | checkpoint | SWITCHGEAR: Mechanical interlocks fitted & operated correctly
4058b529-2215-425b-8cce-b31daf1bec86 | signoff | Holdpoint / Sign Off
15840426-493d-4f6a-b1c8-aa7a2d146652 | checkpoint | SWITCHGEAR: Fuse links continuity check
04b3ac94-e7a4-4445-ba06-9996b3b0cb10 | signoff | Holdpoint / Sign Off
be5efec4-64c3-4578-ab57-f3ec87109d16 | checkpoint | BUSBARS: Busbar sizes checked against drawing
89f192bd-c813-4803-ae49-a7f1adc0666d | signoff | Holdpoint / Sign Off
cc5c87ac-7fa8-4e05-b35d-e1ffbcd33fda | checkpoint | BUSBARS: Minimum Clearance (19mm phase to phase & 16mm phase to Earth)
1a33adc5-8e13-4220-813d-aeb7d629f0d6 | signoff | Holdpoint / Sign Off
57bca797-6584-4d40-a3b6-3f8aa83b7180 | checkpoint | BUSBARS: Busbar supports/cleats in correct locations
536e8815-8b8b-4f69-a84d-08c498440009 | signoff | Holdpoint / Sign Off
f9ba04f6-aa13-464d-9018-8f46945696ed | checkpoint | BUSBARS: Bolted phase connections torque tightened and check marked on nuts
762da078-db31-424e-a0ca-8d8332ce2fe4 | signoff | Holdpoint / Sign Off
32d42445-af59-4aa4-b0dc-a5999a8a408e | checkpoint | BUSBARS: Bolted Neutral connections torque tightened & check marked on nuts
2c28fd10-c7c7-41a8-8720-9a7121b2d980 | signoff | Holdpoint / Sign Off
1a3cc46f-b4f5-4f16-8311-db99b72aaf9a | checkpoint | BUSBARS: Bolted Earth connections torque tightened & check marked on nuts
c67eab0a-e0bf-462f-9b16-2053ced3dba1 | signoff | Holdpoint / Sign Off
54eb859d-af39-4347-a92b-250d791c483a | checkpoint | BUSBARS: Earth connections bolts stamped
92601426-2627-44b9-be89-f15e617e147f | signoff | Holdpoint / Sign Off
af3f31af-4cea-441f-961a-39d27de69a4c | checkpoint | BUSBARS: Neutral connections bolts stamped
153987af-f807-4771-bf23-4460dcf8e72b | signoff | Holdpoint / Sign Off
8192ff74-9386-42f8-ae3a-052c828a49a0 | checkpoint | BUSBARS: Hardware 8.8 high tensile bolts used on joints (Torque settings: M8 = 30Nm M10 = 40Nm M12 = 60Nm)
203d6118-f255-4b1f-b0c6-3050d0ca5b7d | signoff | Holdpoint / Sign Off
40fea796-69a5-4442-bc1a-6b2b1794bd5e | checkpoint | BUSBARS: Phase colour coding correct and checked against drawing
8b1ebc21-3c13-417c-ad4f-260d1f4948d4 | signoff | Holdpoint / Sign Off
e383bdb8-53c0-4154-b3fc-e642ca9280a7 | checkpoint | BUSBARS: Covering - i.e. PVC dipping, PVC sleeving, heat shrink or NIL
0211fee7-5b44-4578-8c38-15f3cebffa30 | signoff | Holdpoint / Sign Off
6ce54e6a-03e3-42d5-92db-eaa13015795c | checkpoint | BUSBARS: Busbar joints wrapped satisfactory
ac6050d2-2d33-405f-92c0-65737a7af3c5 | signoff | Holdpoint / Sign Off
7e86fc82-8952-4a61-9934-2ad0952aac0e | checkpoint | BUSBARS: Busbar flags for Submains suitable for cables
78eaf2bd-6be4-40d5-aa11-e7eff610274e | signoff | Holdpoint / Sign Off
072771fa-b177-4f91-be1e-f70393a56659 | checkpoint | BUSBARS: Bolts suitable type and length for cables
4bdb8e71-6f0f-4a79-8955-f8c44266bba6 | signoff | Holdpoint / Sign Off
769de0ef-a4a7-4101-9b2f-0bc6bc110526 | checkpoint | WIRING: Colour coding on power cable lugs represents correct phasing
d687d918-917f-4d61-81d1-57db7924676f | signoff | Holdpoint / Sign Off
b9100647-b172-4698-89f5-97c967b68746 | checkpoint | WIRING: Correct Colour colouring on control wiring used for each applicable voltage.
2170eed1-f34b-4fad-890e-7d2a27b6f883 | signoff | Holdpoint / Sign Off
330e6c45-5c76-402d-aee0-206b9fca9282 | checkpoint | WIRING: Terminal connections tight & correctly fitted.
14f0d333-7e5c-49fa-b992-f4081587600a | signoff | Holdpoint / Sign Off
88cc5245-0aab-4f3e-b15d-f203f484d106 | checkpoint | WIRING: Slotted cable duct adequately sized as per drawings.
6a075fda-42b2-428b-9570-91868267b264 | signoff | Holdpoint / Sign Off
750568e9-e584-442c-a407-cf4d74233689 | checkpoint | WIRING: Cable sizes correct and sized as per drawing.
b1450100-faec-4a80-bd79-e08e59478f70 | signoff | Holdpoint / Sign Off
86217f85-821d-4f5c-9463-503932be27a0 | checkpoint | WIRING: Wire numbers fitted
066d7fb5-8afb-4945-b33e-d9cb6bcc8b08 | signoff | Holdpoint / Sign Off
7a30c21a-5833-4691-8f31-c175cfe5c1d5 | checkpoint | WIRING: Terminal numbers fitted where specified
c76f7b8b-9646-4e95-8074-f9c13a12a83b | signoff | Holdpoint / Sign Off
c9466a26-e759-4b05-8ec4-37ee6a609f5a | checkpoint | WIRING: Control Circuit functionality
87ce2fab-fb49-4b77-a0b2-7b04d441bea0 | signoff | Holdpoint / Sign Off
84ac29ec-5d9b-41a3-b8c0-db5c75d55a6f | checkpoint | WIRING: Point to point check control wiring as per drawings
c36dc060-502d-496f-9e36-44941de6a850 | signoff | Holdpoint / Sign Off
ff754ea8-bf0f-4f9b-af82-cac2d99d8f3f | checkpoint | MISCELLANEOUS ITEMS: 2 x Spare Keys for 1/4 Turn locks supplied secured inside board.
d7ec8cf0-6cec-4213-b2da-7b90588f46a3 | signoff | Holdpoint / Sign Off
cb3fc29f-3ea2-4ef8-98e5-a4f19ee830ec | checkpoint | MISCELLANEOUS ITEMS: Keys for Selector switches supplied secured inside board.
834a28d2-819f-4135-907d-1e6b3b35766d | signoff | Holdpoint / Sign Off
9de32b6c-a805-47a7-a21f-4d217c4b9ff3 | checkpoint | MISCELLANEOUS ITEMS: Earth continuity between framework of shipping sections (Acceptance Criteria = equal or less than 0.5Ω)
234adc4b-46f9-4fad-85e1-1dcddec96a53 | signoff | Holdpoint / Sign Off
b96549e5-cfda-4a3a-af4a-a27e14888728 | checkpoint | MISCELLANEOUS ITEMS: Earth continuity between earth bar & frame (Acceptance Criteria = equal or less than 0.5Ω)
10280919-8afa-48af-b70d-9a4203a98e1e | signoff | Holdpoint / Sign Off
c88c0dc7-099e-4dc6-9bea-3156c758f9d8 | checkpoint | MISCELLANEOUS ITEMS: Earth continuity between earth bar & doors (Acceptance Criteria = equal or less than 0.5Ω)
a57b7c8b-ec87-49a8-8011-ba43f477a4e3 | signoff | Holdpoint / Sign Off
e2d22ab7-c325-4c97-a424-396219c9c276 | checkpoint | MISCELLANEOUS ITEMS: Operating instructions for Time switch / Time delays etc. supplied with switchboard
8c3e8840-4b76-4719-a441-f2ad88b17468 | signoff | Holdpoint / Sign Off
0ed1eca8-d274-4c5c-9e27-1bfd4f7b56b8 | checkpoint | MISCELLANEOUS ITEMS: Heatshrink has been supplied for cable terminations
485b7c09-f7dd-5f9f-a54c-2b0189ee97b6 | textbox | Insulation Resistance (R-W), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
315ebe35-cc4d-5832-b1e6-40fb278b1798 | textbox | Insulation Resistance (R-B), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
bf5f6588-fdc1-5774-a432-9a6ee99aca66 | textbox | Insulation Resistance (W-B), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
06a6e792-d96f-5c13-98a2-d108ebc60fd8 | textbox | Insulation Resistance (R-N), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
040bffb2-81fc-5616-abf7-fbb5876a70dd | textbox | Insulation Resistance (W-N), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
36775197-501e-5978-83d4-4ce07753eeef | textbox | Insulation Resistance (B-N), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
6c9611a6-bf82-519e-b801-7e460c61db87 | textbox | Insulation Resistance (R-E), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
9e94fe64-fc0e-511b-955e-eeefba740842 | textbox | Insulation Resistance (W-E), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
11a0e528-3387-5110-b96d-0b03c6c52b48 | textbox | Insulation Resistance (B-E), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
691360fc-40e7-5d7c-8623-d8efc3ef3a9f | textbox | Insulation Resistance (N-E), A minimum resistance value of 2 Megaohm is required. Test shall be conducted at 1000V
09c453a4-40bb-5b19-8059-0ba9ee48a983 | textbox | Ductor Test R
a338a1c0-9ccd-57e8-9c31-8e0a36bfa643 | textbox | Ductor Test W
2dca8f5e-8502-510f-9e75-afef00c4acfc | textbox | Ductor Test B
0031bbf4-8dc9-4d73-8948-769ac2a20666 | signoff | Holdpoint / Sign Off
21cfaf34-0013-44fc-8848-e19f7675e474 | checkpoint | FUNCTIONAL CHECK: ACB/MCCB Protection Settings Check:
104c298c-86d2-4b35-938b-49b8e5014427 | signoff | Holdpoint / Sign Off
49bd1305-8f05-42dd-8af4-5eab9620c082 | checkpoint | Cable Terminations to be torqued and marked
5b4b983e-fdc4-47f8-92a9-05e2a65b0e51 | signoff | Holdpoint / Sign Off
26b3dcce-a8cf-4e18-9138-b2f411f00ceb | checkpoint | Switchgear to be cleaned
1b413f4f-b9eb-4787-a35e-8565bd25df67 | signoff | Holdpoint / Sign Off
80478c08-06b8-4863-9cca-f5d1a2f8327a | checkpoint | Photo of LVDB Installation works and termination points
1907a19e-5822-4298-be0f-27e93317fae6 | signoff | Holdpoint / Sign Off
7596f092-e864-4a48-bb44-ed3de7d5c7b0 | checkpoint | Final acceptance
aa713dc6-1f9a-4711-bd86-79ef6b53cce6 | signoff | Final acceptance
35fc45f5-4659-4b98-b5d6-3b741b5ecfc1 | checklist | S3-EL-01-ITC-HD5-L2-RACB |  | S3-EL-01-ITC-HD5-L2-RACB
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
0d9a8d6a-a842-4213-a01e-d18ade37b6b6 | checkpoint | Installation Check (Bolts Torqued, Supports Installed, Covers Installed)
be648256-aa93-5d08-b969-9b21ec79ae9e | textbox | RACB Label
2b8d1de7-17b2-4ab2-bc5b-d2fec8a2c0d7 | signoff | Holdpoint / Sign Off
6e5eabbf-bb5f-4582-907b-390d7e2d2311 | checkpoint | Correct Labelling
5a3a2504-8c61-41c8-8dff-3bdf6fcbd1ac | signoff | Holdpoint / Sign Off
bc360715-8c87-4400-96a5-6238d4fd4907 | checkpoint | Insulation Resistance
ce33041f-78d7-52cd-951b-841543dd88b3 | textbox | Insulation Resistance (R-W)
a0f4e22b-6738-5034-98c9-daefda860e72 | textbox | Insulation Resistance (R-B)
af38ff16-1b9b-551e-b0b6-1f5198ac851f | textbox | Insulation Resistance (W-B)
f1926cac-693f-51c1-a334-0a8b97e93ef2 | textbox | Insulation Resistance (R-N)
c1c17612-b986-5043-be0b-e59be658bf95 | textbox | Insulation Resistance (W-N)
f9e6a2c1-5b60-550b-8f23-1fa803b4afc7 | textbox | Insulation Resistance (B-N)
1e1e5326-7cee-5727-8b7a-7cf4d9b327c3 | textbox | Insulation Resistance (R-E)
6eab0d3a-08ec-5fc6-aaf6-7ba9ce1e5c53 | textbox | Insulation Resistance (W-E)
235cf653-127f-5348-b798-e36e61b1a73d | textbox | Insulation Resistance (B-E)
8e9f3f36-4e62-5be4-b482-64af9f7b72cf | textbox | Insulation Resistance (N-E)
1320c15e-d5fe-4fb5-84f1-f8c5b77dd5bd | signoff | Holdpoint / Sign Off
fb587319-b098-45aa-a099-63730e18802e | checkpoint | Continuity Testing
6ff2746a-74b7-59c4-b29f-eef2da3442a6 | textbox | Continuity Testing (R)
2132dd9b-d3f7-505b-817e-685ba7b6b6f8 | textbox | Continuity Testing (W)
56726007-f5cd-5394-9210-e79f400bf3ad | textbox | Continuity Testing (B)
078e2bcf-1c51-5ff5-a305-339d22eff487 | textbox | Continuity Testing (N)
172255ae-f947-519f-ab1b-b85df1e03da0 | textbox | Continuity Testing (E)
89e2d953-fd72-459f-9c42-dabc67784865 | signoff | Holdpoint / Sign Off
b229d471-a29e-4681-9e6a-6a7098f04bb5 | checkpoint | Photo of RACB Installation works
88d433d4-201b-4922-8095-ae97b16499a3 | signoff | Holdpoint / Sign Off
5f79a63c-8d1b-432f-bfbe-47707a6d4560 | checkpoint | Final acceptance
03ad6823-f716-4cc0-80e3-b15a0bfb99cb | signoff | Final acceptance
1d3cc53b-f405-497d-a5e3-f445dd0abc21 | checklist | S3-EL-01-ITC-HD5-L2-RISO |  | S3-EL-01-ITC-HD5-L2-RISO
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f725271d-a550-4c0e-b015-967ec6b3affe | checkpoint | Installation Check (Bolts Torqued, Supports Installed, Covers Installed)
e710cc0d-d5ad-542d-91bc-fbee3c564681 | textbox | RISO Label
ee67799d-8c13-40cc-b3c3-61adeff30ec1 | signoff | Holdpoint / Sign Off
35963dd1-9039-4381-a01d-677835666dae | checkpoint | Correct Labelling
6b23f5df-aaa0-433f-a432-7bfba3c6a129 | signoff | Holdpoint / Sign Off
343bd582-1f50-48ef-963e-32ee2415af61 | checkpoint | Castell Lock installed
06acd738-5e53-4b7c-8226-900713985f0c | signoff | Holdpoint / Sign Off
c7b9f1c7-7cef-491e-8158-04bd88a37e17 | checkpoint | Insulation Resistance
077d540b-52b0-501e-b669-d4ccd3628fec | textbox | Insulation Resistance (R-W)
60a09e71-2d76-57d0-a785-a207a555f075 | textbox | Insulation Resistance (R-B)
6ffeb002-2e17-55c2-8d7f-4328b4d03d1f | textbox | Insulation Resistance (W-B)
23068591-963b-5edf-8f4d-964e2affd639 | textbox | Insulation Resistance (R-N)
4857b0f6-b588-519e-9409-f33bff00c1dd | textbox | Insulation Resistance (W-N)
b403e707-0ad3-5b36-82f2-6c2372bf0837 | textbox | Insulation Resistance (B-N)
4cdcdf72-8659-57ed-aa2f-d4ca722abfda | textbox | Insulation Resistance (R-E)
9af460e1-fa29-5369-9d94-643b21bcc1aa | textbox | Insulation Resistance (W-E)
ceff8160-1a1a-5ae8-911e-781aa05138ca | textbox | Insulation Resistance (B-E)
76098335-073f-5f47-a245-a0a5b5f4637e | textbox | Insulation Resistance (N-E)
91cb576a-885a-4179-baa3-d2c3868d8403 | signoff | Holdpoint / Sign Off
3828cb05-6cda-4482-952e-470b600dc395 | checkpoint | Photo of RISO Installation works
7fa4a1bb-b266-4b6e-9940-712ceef65573 | signoff | Holdpoint / Sign Off
5de07253-d7e8-468a-a862-351356d00102 | checkpoint | Final acceptance
d59ee766-076a-4456-b7a7-84b690f2c2fc | signoff | Final acceptance
2ff14cec-63f0-504f-b59e-ebc88d383bd2 | checklist | S3-EL-01-ITC-HD5-L3-BUSDUCT |  | S3-EL-01-ITC-HD5-L3-BUSDUCT
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
9159729e-a93f-51a4-8691-6192a4a9ca13 | checkpoint | CxL2 Busduct (ITC:0019) Busduct completed
eb3e4d38-7c23-52a3-b4b6-150909cd5a5e | textbox | From
6c0ba737-e6c4-59e6-9137-d2a448c65b7a | textbox | To
36fa5a49-548b-5a2a-98df-d62e7808fb58 | textbox | Phase rotation
ae2d73d6-7a8e-5ef3-b5b3-e8af2aecdc65 | textbox | Voltage (R-W)
170cda6b-4ea7-58c4-90eb-3183ed2a12f4 | textbox | Voltage (R-B)
83097336-a2b0-5b7f-a3e7-d2003360d9af | textbox | Voltage (W-B)
d808092b-d499-56ed-8cfa-3a9006ad153b | textbox | Voltage (R-N)
d53b84af-5656-5f1d-8378-b211e0d6f1a8 | textbox | Voltage (W-N)
15fffcf2-ea4d-5e32-b0d2-3757ef05eeac | textbox | Voltage (B-N)
f538946b-c955-5e9d-8e75-82f24482e500 | textbox | Voltage (R-E)
f282069a-73cc-5588-8efd-532f55b55bf0 | textbox | Voltage (W-E)
3dd2a2d3-74c6-53d4-b271-6bac01c4ae96 | textbox | Voltage (B-E)
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
6c9a996f-ad9e-4026-bccd-abee664d0b86 | checklist | S3-EL-01-ITC-HD5-L3-BUSDUCT_ Rev 2 |  | S3-EL-01-ITC-HD5-L3-BUSDUCT_ Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
868d1a6c-deed-4605-b33b-da82a8db2a86 | checkpoint | S3-EL-01-ITC-HD5-L2-BUSDUCT completed
f815ebce-8b82-514f-bd33-5b4d9f733261 | textbox | From
c6df1569-b2ec-5129-b59e-92c9303839f0 | textbox | To
711ef02f-fb56-50c7-8a98-e463b2c96201 | textbox | Phase rotation
1a425642-2d8e-59db-9d8d-32cb9e76406d | textbox | Voltage (R-W)
edb3e28d-c954-57d5-a6ca-7a9a35c0cd7b | textbox | Voltage (R-B)
978b21c6-c0ee-5866-83b3-a13d4ef57d25 | textbox | Voltage (W-B)
8fe2a306-a23c-56e7-ad88-6666e0d11fe9 | textbox | Voltage (R-N)
906241f7-cf60-5a6b-a628-e1191d3254cc | textbox | Voltage (W-N)
a55dff39-b826-5b9f-bb8a-0f3209b27987 | textbox | Voltage (B-N)
1daf0c93-8b24-5553-8dfd-2b85d2d1bc01 | textbox | Voltage (R-E)
2d6ffbc7-0321-59f2-b828-59b3c0f35308 | textbox | Voltage (W-E)
13c257f9-0480-5eea-b7c8-d1f279d77952 | textbox | Voltage (B-E)
297240a1-c470-4665-ba48-7f0a5ace8bbb | signoff | Holdpoint / Sign Off
1cf6e4f4-200b-470a-ab8d-74970a880deb | checkpoint | Final acceptance
937b3914-9bf9-4092-8570-91c9bafb9036 | signoff | Final acceptance
375fcde7-9e52-546f-b271-15a1a5700859 | checklist | S3-EL-01-ITC-HD5-L3-LVCABLE |  | S3-EL-01-ITC-HD5-L3-LVCABLE
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5577872f-d041-5651-aaa0-75cac97c3fc4 | checkpoint | EL-0008-1-P-R[B] Low Voltage Cables completed
a5f0a5b8-213a-5fb4-8497-a2f6e5e5f9f3 | textbox | From
6a4f5639-1edf-57c6-aed7-f27a536f74a5 | textbox | To
6d0e7912-f9e7-5c31-a450-7a7ca6dfd54c | textbox | Phase rotation
b9827cbd-77b5-5bee-9ff7-d8b0f70e93f3 | textbox | Voltage (R-W)
a21f7864-6ee8-532c-826e-89fe29467ba2 | textbox | Voltage (R-B)
766282a9-64bf-5a27-bd98-4aa2a7055c6c | textbox | Voltage (W-B)
a21606d4-91fe-5725-af9d-b69f7e5317b7 | textbox | Voltage (R-N)
f8192b60-9389-562e-bbbf-d8fcb90c2588 | textbox | Voltage (W-N)
20fda18e-7e0c-5ebe-a81c-facf3a989603 | textbox | Voltage (B-N)
3311b612-0e88-50e2-b5c8-c881030dff1b | textbox | Voltage (R-E)
b9fc9ede-a32e-5005-b472-ed2bf9764dda | textbox | Voltage (W-E)
2f66f9f4-55b6-57ef-a037-58ba8d8637f6 | textbox | Voltage (B-E)
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
ecad313b-d564-4601-a8bb-8be7ae9274e9 | checklist | S3-EL-01-ITC-HD5-L3-LVCABLE Rev 2 |  | S3-EL-01-ITC-HD5-L3-LVCABLE Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
16325d30-5ba3-41ca-8510-13b7ce4c7163 | checkpoint | S3-EL-01-ITC-HD5-L2-LVCABLE completed
58d64e24-1351-5f3f-8988-34500bc0f044 | textbox | From
bebba55e-a045-54c9-872a-d8e45154fd1c | textbox | To
6e0fcb4e-8205-5673-90d5-dbf410ec6bb7 | textbox | Phase rotation Note - Clockwise is required
5de03167-7805-535a-82f1-00f480b4f99e | textbox | Voltage Source (R-W) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
1084b4f5-5147-51a8-8e91-26f80085dc12 | textbox | Voltage Source (R-B) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
67aa5be7-1a98-5f4f-a2ff-0f24baabfcb3 | textbox | Voltage Source (W-B) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
b0f09632-c399-567a-ba18-fdc3b8bb01bf | textbox | Voltage Source (R-N) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
efa813dd-d93b-5524-aa8d-6b8623a41f2f | textbox | Voltage Source (W-N) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
8642c56a-5fa6-5e30-a8e1-dbce433d0383 | textbox | Voltage Source (B-N) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
6c8aac44-71fa-5505-849f-66f4d301c9d6 | textbox | Voltage Source (R-E) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
9496e39e-9a3b-57e6-abf7-b23c878c3227 | textbox | Voltage Source (W-E) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
55e7460f-95ae-52d2-a174-3922ee8cb458 | textbox | Voltage Source (B-E) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
cc362166-c6fe-531a-bc7e-309da12e10df | textbox | Voltage Destination (R-W) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
c9821806-0251-5e5b-a5f7-156aa347f85d | textbox | Voltage Destination (R-B) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
9f74db26-794b-5f74-8133-75fbc82a120d | textbox | Voltage Destination (W-B) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
d44b4fbb-46ce-5cb4-93e0-403228ee6e05 | textbox | Voltage Destination (R-N) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
e6fc02e2-72c4-537d-8470-bc4e1a4cdb17 | textbox | Voltage Destination (W-N) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
d8e79de0-2f09-5a0a-9aea-39432efd9dd5 | textbox | Voltage Destination (B-N) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
da00a3b5-b331-5401-8d0f-efef1622a32a | textbox | Voltage Destination (R-E) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
29bf7ece-4c8f-53bc-859f-c9eea5aa062c | textbox | Voltage Destination (W-E) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
d983cc43-de43-5a4d-baa8-623d79de3a40 | textbox | Voltage Destination (B-E) Note - P-P 690V range 649V to 759V, P-N 415V range 216V to 253V
c9a21897-6a53-4a5c-a593-09cbca188dcc | signoff | Holdpoint / Sign Off
37ffd560-a236-46a4-a5a1-4c02da114476 | checkpoint | Final acceptance
e7f00725-2785-4126-a9be-3bd2026297f1 | signoff | Final acceptance
b00a94f7-36c3-5933-9bd0-08707246eb9a | checklist | S3-EL-01-ITC-HD5-L3-LVDB |  | S3-EL-01-ITC-HD5-L3-LVDB
0b4ad232-5674-51d3-9408-aef0b58a609d | section | Details:
a01814ad-feaf-5871-9611-969c36794d85 | checkpoint | S3-EL-01-ITC-HD5-L2-LVBOARD completed
43e51c05-be06-5798-a920-4506a72ba606 | textbox | Distribution Board Name
ad10de0b-be85-5b5e-a30c-b3bff15c3d88 | checkpoint | Type of Power Monitor Fitted and location within Board as per drawing
0c4cd3f6-13ef-5a0f-8167-7eaa9103e20e | checkpoint | CT ratio set up within power monitor
c0203a66-102b-516a-8bb3-4d36ccb96cbb | textbox | CT Ratio
92394634-160b-53c1-9d84-c85aad4d3ff6 | checkpoint | Correct Ct's fitted in board & ratio checked against drawing
34461c98-e098-553e-a05f-48c96db380f8 | checkpoint | CT polarity fitted correctly in board (P1 towards incoming)
169f1ccd-34b0-5a2c-b24f-c6a5e30c11fc | checkpoint | Wiring correct from CT's shorting links
681282b0-1242-588c-bf84-75ebc7019870 | checkpoint | Wiring correct from shorting links to power monitors
aead17d1-7eb1-58fb-b7a0-6694115bfd64 | checkpoint | Point to Point comms interface
29a5c76e-4903-517e-a3b0-68005ea149aa | checkpoint | Final acceptance
c58fc97d-6802-559c-8980-aa54624b8c95 | signoff | Final acceptance
955e49b2-eee4-4c2e-a5ea-2b6238c2b4e1 | checklist | S3-EL-01-ITC-HD5-L3-LVDB Rev 2 |  | S3-EL-01-ITC-HD5-L3-LVDB Rev 2
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
faca9e20-5bfb-4352-9aaf-0d10bc27b088 | checkpoint | S3-EL-01-ITC-HD5-L2-LVBOARD completed
486a0fbf-2b75-5cf7-a020-6c9d78dbd2c4 | textbox | Distribution Board Name
b2e46e57-854b-4fcf-bea8-36a5cb4c147a | signoff | Holdpoint / Sign Off
3315b8e2-816a-46da-90a2-1de755234eff | checkpoint | Type of Power Monitor Fitted and location within Board as per drawing
51b6b7b7-b674-4be8-a095-d88860819198 | signoff | Holdpoint / Sign Off
f6f1f317-c503-4bf7-b947-10164ef73d31 | checkpoint | CT ratio set up within power monitor
4029813b-4a92-5b75-bde6-fffce97264ed | textbox | CT Ratio
e2ccf838-cbd3-4f5a-80b4-e24424853bb6 | signoff | Holdpoint / Sign Off
abe50b14-eaf9-4bdf-b8a4-df01271afaf5 | checkpoint | Correct Ct's fitted in board & ratio checked against drawing
c414c69a-d749-4b61-80fd-4d5d34ecf5d9 | signoff | Holdpoint / Sign Off
5d0ca41a-c4a8-43a0-8b13-8dbfdccb304a | checkpoint | CT polarity fitted correctly in board (P1 towards incoming)
e5db741c-1576-4dc8-92eb-e9d503c9d740 | signoff | Holdpoint / Sign Off
d028871a-f3ae-4f21-97e6-b43df6fb70d2 | checkpoint | Wiring correct from CT's shorting links
09b64cfa-2194-4efb-b271-9301927113c5 | signoff | Holdpoint / Sign Off
4213006a-c940-4509-baa2-57e67c14fdb3 | checkpoint | Wiring correct from shorting links to power monitors
fa288f18-c1cf-4e1a-9292-b8fba280ca17 | signoff | Holdpoint / Sign Off
951e9e76-1f7f-4e9e-a92c-49a4fd132a11 | checkpoint | Comms interface installed
e494b361-d152-457a-a702-10c12aed2c2c | signoff | Holdpoint / Sign Off
64535154-a005-44cf-9868-1010c1d759c3 | checkpoint | Final acceptance
f08ef3d6-9f22-40f5-93b8-8f35a8627614 | signoff | Final acceptance
580a407b-71a3-4e22-b238-e2e3895eb098 | checklist | S3-EL-01-ITC-HD5-L3-RISO |  | S3-EL-01-ITC-HD5-L3-RISO
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
c1366ce8-ece4-4953-a3ca-c636e714d57c | checkpoint | S3-EL-01-ITC-HD5-L2-BUSDUCT completed
33221bb8-8d8f-54d7-bf29-792b5fc8ec04 | textbox | RISO Label
5d9ea636-0341-4f1a-a619-8d22ef2f2c34 | signoff | Holdpoint / Sign Off
a2b79a02-4069-4bf0-8b6b-be349d066296 | checkpoint | RISO Isolator Operational Check (Open/Close)
ab30dada-0d31-452b-a1f6-fbdb0e67ddbc | signoff | Holdpoint / Sign Off
acf16dbd-f49a-4c84-959c-d6881df1105b | checkpoint | RISO Isolator Operational Check CSMS Verification (Open/Close)
6da95c40-12d3-4490-bef5-667ad6bc7532 | signoff | Holdpoint / Sign Off
85ca04be-9f57-4e22-b644-de81ea4c0615 | checkpoint | Final acceptance
10f83c2c-5651-44bf-a5ca-5c73b12ee400 | signoff | Final acceptance
e5cc35b5-99e5-423a-b3b6-35e9d7f523fc | checklist | Seismic Bracing |  | Seismic Bracing
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6a0eb252-25a6-48be-967f-4c6b19582b81 | checkpoint-no-value | Seismic Bracing Type
ebea1036-80fa-5b9a-86e6-e45dd4c4eb45 | dropdown | Select System No. | C3 FM2073, J2 SP80-2072 SP80 Strut, K1 SUPA50, P1, P3, P4, P9, C2 Post
166c103b-16c1-46c2-b4ab-093ba4bdf8dd | checkpoint | Seismic Supports installed as per drawing
00ac4b0c-8a63-49d0-af05-6828e5a27371 | checkpoint | All Supports, Joints and Bolts tightened
f634a81e-0cb2-4b3f-ae8d-15148ce6cee7 | checkpoint-no-value | Location
6e132de5-2b40-5def-b0a6-b1568c1db04e | dropdown | Location: | Corridor, Switch room, Data Hall, Riser, Other
0ed481c4-3f3c-4ea6-b73a-899b73f3a22a | checkpoint | Photo of Seismic Installation
b31f5b75-c238-481b-a644-ef4bd1a274fc | checkpoint | Final acceptance
ced3d872-0ad2-49ea-8925-014cac93faf3 | signoff | Final acceptance