## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Metal Cladding |  |  |  |  | Yes | Metal Cladding | 005d7064-fdf7-4a85-9690-c4d0e36d2d14
checkpoint-status |  |  | checkpoint | Using approved cladding materials
checkpoint-status |  |  | checkpoint | Pipework less than 150mm outside diameter over insulation-Aluminium or galv 0.5mm Thick
checkpoint-status |  |  | checkpoint | Pipework 150mm to 450mm outside diameter over insulation -Aluminium 0.7mm thick or Galv. 0.6mm thick.
checkpoint-status |  |  | checkpoint | Pipework/ Vessels / Evaporators over 450mm outside diameter over insulation -Aluminium 1.0 mm thicker Galv. 0.9mm thick.
checkpoint-status |  |  | checkpoint | Minimum 40mm overlapping circumferential joints.
checkpoint-status |  |  | checkpoint | Longitudinal joints faced away from view
checkpoint-status |  |  | checkpoint | Fixed with straps (same materials) for chilled water pipework or refrigerant pipework. Do not violate vapour barrier.
checkpoint-status |  |  | checkpoint | Used lobster back segments for curved surfaces. Seal all holes
checkpoint-status |  |  | checkpoint | Seal up all penetrations for gauges , instruments drains and vents.
checkpoint-status |  |  | checkpoint | Using Suitcase clips for all Readily removable at evaporator heads, strainers, and similar areas where removal for maintenance is anticipated.
checklist-flat |  |  | checklist | Duct / Equipment Cleaning |  |  |  |  | Yes | Duct / Equipment Cleaning | 00dadbfe-1715-4793-bddb-692bccbfdd7f
checkpoint-status |  |  | checkpoint | Specialized Cleaning contractor to clean Outdoor / Supply and Return air Ducting and equipment in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
checkpoint-status |  |  | checkpoint | Verification of ductwork cleanliness shall be by vacuum test ( gravimetric analysis ) in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
checkpoint-status |  |  | checkpoint | Undertake a second vacuum test immediately prior to handover.
checklist-flat |  |  | checklist | Preworks Inspection QA |  |  |  |  | Yes | V1 HBH - Preworks Inspection QA | 059194ae-cf56-488c-9693-44ac3b332208
checkpoint-status |  |  | checkpoint | Drawings at construction issue
text | 9366e722-7f41-53b4-b4cc-901e6092a866 |  | textbox | Revision #
checkpoint-status |  |  | checkpoint | Equipment ordered and ready to be delivered
checkpoint-status |  |  | checkpoint | Floor clear and access suitable, please attach photos
checkpoint-status |  |  | checkpoint | High level services / trades completed their applicable works
checklist-sectioned |  |  | checklist | Pipework Insulation |  |  |  |  | Yes | V1 HBH - Pipework Insulation | 08c9963d-ebc8-47fd-a216-a11fc34e7615
checkpoint-group |  |  | section | Chilled & Hot Water Pipework Insulation
checkpoint-status |  |  | checkpoint | Using Approved Insulation Materials and Thickness: (Thermobreak)
checkpoint-status |  |  | checkpoint | Install as per Manufacturer's Standards: (Nexus Foam-Thermobreak CHW)
checkpoint-status |  |  | checkpoint | Ensure the pipe remains tightly butted against clamps blocks supports.
checkpoint-status |  |  | checkpoint | Adhere the insulation to the pipe with a 50mm band of adhesive applied to the bore of both ends of each section to form a vapour barrier.
checkpoint-status |  |  | checkpoint | Apply adhesive for all Longitudinal and Circumferential joints.
checkpoint-status |  |  | checkpoint | 50mm minimum width pressure sensitive self adhered reinforced aluminium foil tape firmly applied to the facing .
checkpoint-status |  |  | checkpoint | Use mitre cut elbow for all the bends.
checkpoint-status |  |  | checkpoint | Install as per Manufacturer's Standards: (Nexus Foam-Thermobreak HHW)
checkpoint-status |  |  | checkpoint | Use mitre cut elbow for all the bends.
checkpoint-status |  |  | checkpoint | 50mm minimum width pressure sensitive self adhered reinforced aluminium foil tape firmly applied to the facing .
checkpoint-status |  |  | checkpoint | Apply Reinforced aluminium tape for all Longitudinal and Circumferential joints.
checkpoint-group |  |  | section | Metal Cladding
checkpoint-status |  |  | checkpoint | Using Approved Cladding Materials :
checkpoint-status |  |  | checkpoint | Pipework less than 150mm outside diameter over insulation -Aluminium or Galv. 0.5mm thick
checkpoint-status |  |  | checkpoint | Pipework 150mm to 450mm outside diameter over insulation -Aluminium 0.7mm thick or Galv. 0.6mm thick.
checkpoint-status |  |  | checkpoint | Pipework/ Vessels / Evaporators over 450mm outside diameter over insulation -Aluminium 1.0 mm thicker Galv. 0.9mm thick.
checkpoint-status |  |  | checkpoint | Minimum 40mm overlapping circumferential joints.
checkpoint-status |  |  | checkpoint | Longitudinal joints faced away from view.
checkpoint-status |  |  | checkpoint | Fixed with straps (same materials) for chilled water pipework or refrigerant pipework. Do not violate vapour barrier.
checkpoint-status |  |  | checkpoint | Used lobster back segments for curved surfaces. Seal all holes
checkpoint-status |  |  | checkpoint | Seal up all penetrations for gauges , instruments drains and vents.
checkpoint-status |  |  | checkpoint | Using Suitcase clips for all Readily removable at evaporator heads, strainers, and similar areas where removal for maintenance is anticipated.
checklist-flat |  |  | checklist | Ducting Fit-Off |  |  |  |  | Yes | V1 HBH - Ducting Fit-Off | 0d30636d-d935-4c30-b7bd-0c294c886fa0
checkpoint-status |  |  | checkpoint | Flexible Ducting installed w/c Brackets
checkpoint-status |  |  | checkpoint | Correct grills and diffuser installed
checkpoint-status |  |  | checkpoint | Grills as per drawing, relocated or removed
checklist-sectioned |  |  | checklist | Electrical QA |  |  |  |  | Yes | Electrical QA | 13d1b2e8-06a8-4941-bd67-83fae804ece8
checkpoint-group |  |  | section | QA - First Fix
checkpoint-status |  |  | checkpoint | Switch Board Mounted in correct position and level
checkpoint-status |  |  | checkpoint | Switch Board terminations complete
checkpoint-status |  |  | checkpoint | Board Tested
checkpoint-status |  |  | checkpoint | COC's Complete
checkpoint-status |  |  | checkpoint | BMS controllers and associated modules installed, wired correctly
checkpoint-group |  |  | section | QA - Second Fix
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checkpoint-status |  |  | checkpoint | BMS controllers and associated modules installed wired correctly
checkpoint-status |  |  | checkpoint | BMS Modules installed / Wired correctly
checkpoint-status |  |  | checkpoint | All IOs are labeled and wired correctly as per BMS contractors instructions
checklist-flat |  |  | checklist | Fire Damper # |  |  |  |  | Yes | V1 HBH - Fire Damper # | 150d734e-7aa8-4fb8-891d-ed3d545e0bd4
checkpoint-status |  |  | checkpoint | Fire damper reference
text | e2a7319b-74ff-5b08-b082-f9ad4af67bce |  | textbox | Manufacturer:
text | 7674e965-af84-534b-ae43-591449a69005 |  | textbox | Model No.
text | fa05c6ee-7356-5fa5-8f5d-3e6dd8c7d365 |  | textbox | Wall thickness
text | 9b9801c9-df64-5948-b204-e68dc731fe53 |  | textbox | Duct Width/Dia
text | db5d0382-1863-51dc-b508-aa906f417579 |  | textbox | Duct height
label | 44ffdeb7-4c89-5c11-b74d-6049950e79aa |  | note | Access
boolean | cf77f871-e522-5214-9ce6-ae0eb6ed66a5 |  | tickbox | Air On
boolean | 72991ab8-e65a-53a3-879e-0715385b7ed5 |  | tickbox | Air Off
text | 6b00d130-5618-50b2-a016-443f8ac95143 |  | textbox | Fire Damper FRL
checkpoint-status |  |  | checkpoint | F/D label in accordance with 1682.1 is fitted
checkpoint-status |  |  | checkpoint | F/D construction and installation is in accordance with the certified and tested method
checkpoint-status |  |  | checkpoint | F/D orientation is installed as per the label
checkpoint-status |  |  | checkpoint | F/D is fully open and the fusible link is installed
checkpoint-status |  |  | checkpoint | F/D is installed with respect to the direction of the airflow marked on the label
checkpoint-status |  |  | checkpoint | F/D wall clearances are achieved (Reference 1682.2)
checkpoint-status |  |  | checkpoint | F/D operation (closure) is not impeded
checkpoint-status |  |  | checkpoint | F/D assumes a fully closed position in fire mode
checklist-sectioned |  |  | checklist | Condensate Pipe Work |  |  |  |  | Yes | Condensate Pipe Work | 15709c09-4128-465b-8cce-a4da6cdf5295
checkpoint-group |  |  | section | QA - First Fix
checkpoint-status |  |  | checkpoint | Correct pipe routing as per shop drawings
checkpoint-status |  |  | checkpoint | Proper Pipe size, length, material used
checkpoint-group |  |  | section | QA - Second Fix
checkpoint-status |  |  | checkpoint | Pipe joints, connections, Tees all tested for leaks
checkpoint-status |  |  | checkpoint | Correct pipe routing as per shop drawings
checkpoint-status |  |  | checkpoint | Proper pipe routes to drain pipes
checklist-flat |  |  | checklist | Heater Banks |  |  |  |  | Yes | Heater Banks | 165d6755-3513-414f-a7e5-3fa0127f621b
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Mountings / springs installed
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of Equipment heights correct as per Workshop Drawings.
checkpoint-status |  |  | checkpoint | Fire rated insulation installed as per spec
checkpoint-status |  |  | checkpoint | All E4M wirings are installed and tested
checklist-flat |  |  | checklist | CHW & HHW Insulation |  |  |  |  | Yes | CHW & HHW Insulation | 19725688-0075-47df-a1a1-1153b071533d
checkpoint-status |  |  | checkpoint | Approved material thickness has been used (Thermobreak®).
checkpoint-status |  |  | checkpoint | Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specification
checkpoint-status |  |  | checkpoint | Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
checkpoint-status |  |  | checkpoint | Insulation is glued to the pipe with a 50mm wide band of adhesive (Ados F2®) at both ends of section to form the vapour barrier
checkpoint-status |  |  | checkpoint | Adhesive is applied along all longitudinal and circumferential joints
checkpoint-status |  |  | checkpoint | A 50mm wide strip of pressure sensitive tape reinforced aluminium tape is applied to the insulation facing, along and around all joints
checkpoint-status |  |  | checkpoint | Mitre cut elbows have been used on all bends.
checkpoint-status |  |  | checkpoint | Apply reinforced aluminium tape for all longitudinal and circumferential joints.
checklist-flat |  |  | checklist | External Duct Work Insulation QA |  |  |  |  | Yes | External Duct Work Insulation QA | 1df8daea-c6b6-433b-8768-ce316beab512
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Ductwrap materials - Multitel 18kg Density foiled 1-side 25mm thick
checkpoint-status |  |  | checkpoint | Cover entire surface with insulation including all flanges,stiffeners and support angles.
checkpoint-status |  |  | checkpoint | Provide 50mm over lapping at all joints.
checkpoint-status |  |  | checkpoint | Tape all joints with 75mm width (72mm on the Market) Aluminium foiled tape.
checkpoint-status |  |  | checkpoint | Fixing for all Duct size 375mm to 750mm steel weld pins on centreline at 400mm spacing bottom surface only.
checkpoint-status |  |  | checkpoint | Fixing for all Duct size 750mm and greater steel weld pins at 400mm spacing maximum.
checkpoint-status |  |  | checkpoint | Fixing for all Duct riser steel weld pins at 400mm spacing maximum.
checkpoint-status |  |  | checkpoint | Using additional polypropylene fixing Bands 600mm centres.
checkpoint-status |  |  | checkpoint | Provide an overlap of at least 300mm where insulation changes from the inside of the duct to the outside.
checklist-flat |  |  | checklist | Radiant Heaters |  |  |  |  | Yes | Radiant Heaters | 2290d66c-4d9a-45da-8724-1a2a9b6645dc
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Mountings / springs installed
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of Equipment heights correct as per Workshop Drawings.
checkpoint-status |  |  | checkpoint | All E4M wirings are installed and tested
checklist-flat |  |  | checklist | E4MQA - Second Fix |  |  |  |  | Yes | E4MQA - Second Fix | 27015f9d-e70d-460a-a154-b7a84fb02ad5
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators, VSDs installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temperature, pressure sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | Roof Ductwork |  |  |  |  | Yes | V1 HBH - Roof Ductwork | 2be65920-aaf0-4015-8b0b-c2f9e8bc4dab
checkpoint-status |  |  | checkpoint | Ductwork installed correctly
checkpoint-status |  |  | checkpoint | Flange Capping installed
checkpoint-status |  |  | checkpoint | Seismic braces installed correctly
checkpoint-status |  |  | checkpoint | Dampers installed correctly
checkpoint-status |  |  | checkpoint | Insulation installed correctly
checkpoint-status |  |  | checkpoint | Sign off AE Smith
checkpoint-status |  |  | checkpoint | Sign off DHB
checkpoint-status |  |  | checkpoint | Sign off Hawkins
checklist-sectioned |  |  | checklist | Mechanical Duct |  |  |  |  | Yes | Mechanical Duct | 2f70f0c2-e892-45ef-b31c-82b90d71bcda
checkpoint-group |  |  | section | QA - First Fix
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | Ducting / equipment connections including flexibles, nuts, bolts and washers correct and tight.
checkpoint-status |  |  | checkpoint | U/S of duct heights correct as per Workshop Drawings.
checkpoint-status |  |  | checkpoint | Ducts to be removed relocated / relocated as per drawings
checkpoint-status |  |  | checkpoint | All volume dampers set fully open
checkpoint-status |  |  | checkpoint | Duct Hangers (is spacing correct, installed level etc)
checkpoint-status |  |  | checkpoint | Duct jointing (Joints sealed, cleats fitted etc)
checkpoint-status |  |  | checkpoint | Fire Dampers installed in open position c/w access panel.
checkpoint-status |  |  | checkpoint | Sound attenuators installed
checkpoint-status |  |  | checkpoint | Transfer ducts installed
checkpoint-group |  |  | section | QA - Second Fix
checkpoint-status |  |  | checkpoint | Motorized dampers orientation to be installed correct way for sealing purpose
checkpoint-status |  |  | checkpoint | Access Panels to be installed as per drawing
checkpoint-status |  |  | checkpoint | Butterfly and outlet dampers installed as per drawing and in open position.
checkpoint-status |  |  | checkpoint | Seismic bracing installed as per Drawing
checkpoint-status |  |  | checkpoint | Flexible ducting installed c/w supports.
checkpoint-status |  |  | checkpoint | Grille location as per updated drawings
checkpoint-status |  |  | checkpoint | Correct Equipment / Correct Grills / Diffuser Installed
checklist-flat |  |  | checklist | Fire Rated Duct Insulation |  |  |  |  | Yes | Fire Rated Duct Insulation | 2f9c3121-4e18-4814-a2ba-daf7e982e216
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Fire rated Ductwrap materials - 38mm thick Fyrewrap Elite 1.5 (FRL 120/120/120)
checkpoint-status |  |  | checkpoint | Install as per Manufacturer's Standards: (Trafalgar-Fyrewrap)
checkpoint-status |  |  | checkpoint | Fyrewrap duct wrap must completely covered the duct and there must not be any exposed sections or gaps.
checkpoint-status |  |  | checkpoint | A 100mm minimum overlap must be used on all joints. Only the Three specified methods (telescope, checkerboard and butt splice methods.) of overlap may be used when adjoining Fyrewrap duct wraps.
checkpoint-status |  |  | checkpoint | Cut edges must be completely sealed with the specified pressure-sensitive aluminium foiled tape.
checkpoint-status |  |  | checkpoint | ≤600 x600 duct size Steel banding only spacing 40mm from edges over the overlap and one additional between overlaps.
checkpoint-status |  |  | checkpoint | ≤1200 x1200 duct size Steel banding and pins bottoms only spacing 40mm from edges over the overlap and one additional between overlaps. Pre-welded Pins grid 200mm centres.
checkpoint-status |  |  | checkpoint | ≥1200 x1200 duct size pins only all sides of duct pre-welded Pins grid 200mm centres.
checkpoint-status |  |  | checkpoint | Wall penetrations up to 1600mm duct size 75mm x 75mm x1.6mm steel angle 100mm width x 60mm thick maxilite board.
checkpoint-status |  |  | checkpoint | Length of second layer from the fire barrier FRL 60/60/60
checkpoint-status |  |  | checkpoint | Duct size 600mm x 600mm or less -second layer 1350mm
checkpoint-status |  |  | checkpoint | Duct size 600mm x 1200mm or less -second layer 1600mm
checkpoint-status |  |  | checkpoint | Duct size 600mm x 600mm -second layer 1900mm
checkpoint-status |  |  | checkpoint | Duct size 200mm x 2400mm -second layer 2500mm
checkpoint-status |  |  | checkpoint | Duct size 2400mm x 3600mm -second layer 2700mm
checkpoint-status |  |  | checkpoint | Used only Trafalgar Access Panels -must be fitting directly over the existing duct access panels fixed with rivets and fyreflex fire rated sealant, with a second local layer of Fyrewrap.
checklist-flat |  |  | checklist | CHW & HHW Piping (VICTAULIC) |  |  |  |  | Yes | CHW & HHW Piping (VICTAULIC) | 37f3fb3d-1dd8-4b92-b986-0f8c10fa47da
checkpoint-status |  |  | checkpoint | Pipework installed as per Drawing
checkpoint-status |  |  | checkpoint | All fabricators/welders are qualified and have current tickets
checkpoint-status |  |  | checkpoint | Pipe sizing is correct and valving in correct location
checkpoint-status |  |  | checkpoint | Valve arrangement installed as per Detail specified drawing ie Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Expansion tank / Dosing Pod
checkpoint-status |  |  | checkpoint | Insulation blocks installed where required
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | Isolating and Control valve installed correctly
checkpoint-status |  |  | checkpoint | Hose piping installed
checkpoint-status |  |  | checkpoint | Air vents installed at all high points
checkpoint-status |  |  | checkpoint | All materials are in accordance with applicable AS/NZ standard
checkpoint-status |  |  | checkpoint | The pipe OD and groove dimensions are within tolerance range as per victaulic specification
checkpoint-status |  |  | checkpoint | The correct coupling has been used for the correct joint i.e flexible or rigid
checkpoint-status |  |  | checkpoint | All fitting are victaulic approved
checkpoint-status |  |  | checkpoint | Victaulic grease has been applied to the gasket and OD of pipe
checkpoint-status |  |  | checkpoint | Couplings are tightened by alternating sides equally
checkpoint-status |  |  | checkpoint | Bolt pads have firm metal to metal contact
checkpoint-status |  |  | checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
checklist-flat |  |  | checklist | Fans |  |  |  |  | Yes | Fans | 3b3dceb5-fdac-4d52-b89d-1055c03d3758
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Mountings / springs installed
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of Fan heights correct as per Workshop Drawings.
checkpoint-status |  |  | checkpoint | Confirm Model number
checkpoint-status |  |  | checkpoint | Labelling
checkpoint-status |  |  | checkpoint | Upstand height 200mm minimum high side
checkpoint-status |  |  | checkpoint | underflashing / Waterproofing completed
checkpoint-status |  |  | checkpoint | Check for damage
checklist-flat |  |  | checklist | External Acoustic Insulation (FCU's) |  |  |  |  | Yes | External Acoustic Insulation (FCU's) | 43041aed-4b4b-41d5-9855-bbd8b891e2e4
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Acoustic wrap materials - 50mm Polyester sheet cover with 5kg wave bar
checkpoint-status |  |  | checkpoint | Cover all surface of the FCU units with insulation excluding the Vents and pipe outlet area.
checkpoint-status |  |  | checkpoint | fixing using self adhesive pins and polypropylene Bands with with buckles .
checkpoint-status |  |  | checkpoint | Tape all joints with 50mm width reinforced Aluminium foiled tape.
checklist-sectioned |  |  | checklist | Plant Room # |  |  |  |  | Yes | V1 HBH - Plant Room # | 46b20d64-3ed5-4ec0-8804-14784197901a
checkpoint-group |  |  | section | Pre install checks
checkpoint-status |  |  | checkpoint | Updated drawing used
label | 760d1818-2b63-5e15-9f1b-ad7536c1d8ca |  | note | Please note the revision number in the comments box
checkpoint-status |  |  | checkpoint | All drawings correctly locate with respect to approved workshop drawings
checkpoint-status |  |  | checkpoint | All pipework and ductwork checked (refer to and use appropriate pipework and ductwork check sheets), utilize schematics
checkpoint-status |  |  | checkpoint | All specified anti vibration mounts (springs, air bags, inertia bases etc.) installed correctly
checkpoint-status |  |  | checkpoint | Equipment relevant to project from list below checked as being installed correctly and for the specific items listed.
checkpoint-group |  |  | section | Air handling units and fan coil units
checkpoint-status |  |  | checkpoint | Correctly supported
checkpoint-status |  |  | checkpoint | Trays and drains complete and correct, correct for trapped drains
checkpoint-status |  |  | checkpoint | Filters installed as specified, check access for cleaning
checkpoint-status |  |  | checkpoint | Belts, pulleys and guards installed and complete
checkpoint-status |  |  | checkpoint | Flexible/duct connections installed and complete
checkpoint-group |  |  | section | Air compressors
checkpoint-status |  |  | checkpoint | Installed as per manufacturer's instructions
checkpoint-group |  |  | section | Water treatment
checkpoint-status |  |  | checkpoint | Installed as per manufacturer's data
checkpoint-group |  |  | section | Volume control dampers manual & motorised
checkpoint-status |  |  | checkpoint | Installed in correct position
checkpoint-status |  |  | checkpoint | Full and correct movement available
checkpoint-status |  |  | checkpoint | Motors installed correctly and bracketed to prevent flexing
checkpoint-group |  |  | section | Valves and Pipe fittings
checkpoint-status |  |  | checkpoint | Installed as per Schematics and Piping layouts
checkpoint-status |  |  | checkpoint | Installed to allow proper clearances for access
checkpoint-status |  |  | checkpoint | No access to be installed anywhere near switchboards or electrical gear
checklist-sectioned |  |  | checklist | AHU |  |  |  |  | Yes | AHU | 5152c8a8-5e44-46ab-a040-7f316cb8b09b
checkpoint-group |  |  | section | QA - First Fix
checkpoint-status |  |  | checkpoint | Check if plinth site is correct
checkpoint-status |  |  | checkpoint | Correct Unit Installed as scheduled
checkpoint-status |  |  | checkpoint | Setting out point correct
checkpoint-status |  |  | checkpoint | Anti Vibration pads to be installed
checkpoint-status |  |  | checkpoint | Condensate Piping installed
checkpoint-status |  |  | checkpoint | Tundish installed by others and connected up
checkpoint-status |  |  | checkpoint | Insulation Complete for Piping and Condensate lines
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
checkpoint-status |  |  | checkpoint | Pipework and coils installed
checkpoint-group |  |  | section | QA - Second Fix
checkpoint-status |  |  | checkpoint | Filters Installed
checkpoint-status |  |  | checkpoint | Return air fan installed correctly
checkpoint-status |  |  | checkpoint | All Manual and motorized dampers installed
checkpoint-status |  |  | checkpoint | Heating and chilled valves installed
checkpoint-status |  |  | checkpoint | Ductwork installed correctly
checkpoint-status |  |  | checkpoint | Flange capping installed correctly
checkpoint-status |  |  | checkpoint | Insulation installed correctly
checkpoint-status |  |  | checkpoint | Sign off AE Smith
checkpoint-status |  |  | checkpoint | Commissioning complete
checklist-flat |  |  | checklist | Chillers / Buffer Tank / Dosing Pod / Pumps |  |  |  |  | Yes | Chillers / Buffer Tank / Dosing Pod / Pumps | 5259d3ad-7d97-498f-acc1-a4366e8c7c46
checkpoint-status |  |  | checkpoint | Check if plinth site is correct
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | Setting out point correct
checkpoint-status |  |  | checkpoint | Anti Vibration pads to be installed if required
checkpoint-status |  |  | checkpoint | Correct Springs installed ( If required )
checkpoint-status |  |  | checkpoint | Condensate Piping installed ( If required )
checkpoint-status |  |  | checkpoint | Tundish installed by others and connected up ( If required )
checkpoint-status |  |  | checkpoint | Correct pumps installed as scheduled
checkpoint-status |  |  | checkpoint | All installs as per drawing - Drawing reference
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
checklist-flat |  |  | checklist | Final Sign Off |  |  |  |  | Yes | V1 HBH - Final Sign Off | 5526f901-bcda-4f92-b1a2-5bc2daa74faf
checkpoint-status |  |  | checkpoint | AES
text | c3fba4f6-944e-5a92-bb68-7cd7e59d68da |  | textbox | Name:
checkpoint-status |  |  | checkpoint | Consultant
text | 8587b427-3bad-595e-b77d-8a294689ebd8 |  | textbox | Name:
checkpoint-status |  |  | checkpoint | DHB Representative
text | e81a70c3-f86a-5ede-97ec-b4d956bba8fe |  | textbox | Name:
checkpoint-status |  |  | checkpoint | Commissioning Agent
checklist-flat |  |  | checklist | Pre-Energisation Inspection and Commissioning Test Sheet |  |  |  |  | Yes | V1 HBH - Pre-Energisation Inspection and Commissioning Test Sheet | 5d2d75cf-568d-4521-897f-fd6fb26956bc
checkpoint-status |  |  | checkpoint | Completed and signed sheet attached
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Cable Ladder/Duct/Wire Installation Checklist |  |  |  |  | Yes | V1 HBH - Cable Ladder/Duct/Wire Installation Checklist | 5f38d8f2-aa95-4d8b-80ec-e05543194442
checkpoint-status |  |  | checkpoint | Document Reference
label | d692df4b-c786-5fc6-b13a-b6fdd3ca870f |  | note | AES-CL-QUA-ITC-002
label | fa73a672-65e7-5751-923f-c21e05a900c0 |  | note | Issue Date – May 2018
select | 55f2bc18-30e1-5405-8280-edfce40010c6 |  | dropdown | Type of ladder | LT1,LT3,Perforated,Others
checkpoint-status |  |  | checkpoint | Support brackets / method adequate for cables above 120mm
checkpoint-status |  |  | checkpoint | Support spacing visually been inspected
checkpoint-status |  |  | checkpoint | System installed level
checkpoint-status |  |  | checkpoint | All cut edges are without snag or catch points to cause cable damage
checkpoint-status |  |  | checkpoint | External is without protrusions to cause harm to personnel
checkpoint-status |  |  | checkpoint | Cable ducting visually been inspected
checkpoint-status |  |  | checkpoint | Divider strip installed where required for segregation
checkpoint-status |  |  | checkpoint | Earth bond applicable. (Ducts)
checkpoint-status |  |  | checkpoint | Sun cover provided where required
checkpoint-status |  |  | checkpoint | Conduits attached with correct saddles and knock ins
checkpoint-status |  |  | checkpoint | Correct Cable Spacing
checkpoint-status |  |  | checkpoint | Seismic restraints are installed as required.
checkpoint-status |  |  | checkpoint | Report for completed works sent
checklist-flat |  |  | checklist | 2nd Fix - Medical Gas |  |  |  |  | Yes | V1 HBH - 2nd Fix - Medical Gas | 677b228d-23c8-4ea1-96eb-2878ac0f0b94
checkpoint-status |  |  | checkpoint | Outlet Pipework installed with correct separation and labelling
checkpoint-status |  |  | checkpoint | AE Smith Sign off
checklist-flat |  |  | checklist | AHU |  |  |  |  | Yes | V1 HBH - AHU | 68132d0e-bdaf-40a2-9a30-52c74364408b
checkpoint-status |  |  | checkpoint | AHU Unit installed and fixed correctly
checkpoint-status |  |  | checkpoint | Return Air Fan installed correctly
checkpoint-status |  |  | checkpoint | Dampers installed correctly
checkpoint-status |  |  | checkpoint | Heating and chilled valves installed
checkpoint-status |  |  | checkpoint | Duct work installed correctly
checkpoint-status |  |  | checkpoint | Flange capping installed correctly
checkpoint-status |  |  | checkpoint | Insulation installed correctly
checkpoint-status |  |  | checkpoint | Sign off AE Smith
checkpoint-status |  |  | checkpoint | Sign off DHB
checkpoint-status |  |  | checkpoint | Sign off Hawkins
checklist-flat |  |  | checklist | Energisation Checklist |  |  |  |  | Yes | V1 HBH - Energisation Checklist | 72c652b3-61fc-4ee1-a7db-268f679c18f7
checkpoint-status |  |  | checkpoint | Document Reference
label | 5fb8c35c-dfea-5558-8b1f-78f6a7079976 |  | note | AES-PRE-ENERG-QUA-ITC-002 Rev 1
label | f06c7ea2-89cf-5565-99b1-4344167710fb |  | note | Issue Date – May 2018
checkpoint-status |  |  | checkpoint | Has your supervisor been contacted/notified?
checkpoint-status |  |  | checkpoint | Can the electrical equipment be safely Energised?
checkpoint-status |  |  | checkpoint | Have all permits, SWMS been completed, and signed by work party In consultation with client to ensure all permits have been completed correctly
checkpoint-status |  |  | checkpoint | Has equipment, switchboard or sub circuit to be worked on been clearly identified and confirmed via drawings, schedules etc?
checkpoint-status |  |  | checkpoint | Are the supply cables/circuits terminated & checked ?
checkpoint-status |  |  | checkpoint | Has the switchboard been vacuumed & cleaned?
checkpoint-status |  |  | checkpoint | Correct overload setting checked and recorded ?
label | 6c315348-19b6-59ee-a073-0bd586ed939c |  | note | (Refer to Energising/De-Energising Procedure)
checkpoint-status |  |  | checkpoint | Are all circuits labels correct & Installed?
checkpoint-status |  |  | checkpoint | Has the Switchboard Schedule been completed and installed ?
checkpoint-status |  |  | checkpoint | Are all covers in place / tools accounted for?
checkpoint-status |  |  | checkpoint | Have all work parties and people in close vicinity been made aware of proposed energisation ?
checkpoint-status |  |  | checkpoint | Has the completed permits been returned to the client to confirm energisation is completed ?
checkpoint-status |  |  | checkpoint | Have S/B been fire sealed?
checkpoint-status |  |  | checkpoint | Fire relay installed and commissioned by fire contractor ?
checkpoint-status |  |  | checkpoint | Energisation Permit Completed
checklist-sectioned |  |  | checklist | Fire Dampers |  |  |  |  | Yes | Fire Dampers | 739555c1-7e6a-4709-8439-113b22b875e9
checkpoint-group |  |  | section | QA - First Fix
checkpoint-status |  |  | checkpoint | Correct FD Installed
checkpoint-status |  |  | checkpoint | Access Panel installed
checkpoint-group |  |  | section | QA - Second Fix
checkpoint-status |  |  | checkpoint | Drop Tested
checkpoint-status |  |  | checkpoint | Track is Clear
checkpoint-status |  |  | checkpoint | Builder to Fire Sealed
checklist-flat |  |  | checklist | B2 - Cross connection test |  |  |  |  | Yes | V1 HBH - B2 - Cross connection test | 7455226d-b5b5-4b6c-a422-0389b2852f62
checkpoint-status |  |  | checkpoint | B2 Leakage Test Complete
text | 8c4e75ce-7ad1-5324-8601-ea8d42a2168b |  | textbox | Test by
text | 781032c2-4275-52c7-83cd-7466443a2af2 |  | textbox | Test date
text | 6f6a7343-80cb-5c39-b8af-e6e4c141ebf5 |  | textbox | Revision
checkpoint-status |  |  | checkpoint | This is to certify that a Cross-Connection test in accordance with HTM 02-01, paragraphs 15.52–15.55
boolean | 6e943896-21f4-54aa-83c6-1626f81e1334 |  | tickbox | Cross Connections between these systems were found If yes, detail findings above
text | 6756e5e8-2f2f-5538-9911-2615faf32fca |  | textbox | Status
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 8f1ad016-acda-5c01-847d-fff41b3cf68c |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | dc8a1eb6-8d74-5e15-8577-efcdc49674f0 |  | textbox | Consultant Name
checklist-flat |  |  | checklist | Commissioning |  |  |  |  | Yes | V1 HBH - Commissioning | 7ef4bc0e-7416-4052-8488-ad1462ae7935
checkpoint-status |  |  | checkpoint | Commissioning
checkpoint-status |  |  | checkpoint | Summary of tests - associated Plant items
checkpoint-status |  |  | checkpoint | All plant items, installed as per drawings
checkpoint-status |  |  | checkpoint | Commissioning Engineers comments
checkpoint-status |  |  | checkpoint | Commissioning Agent Sign Off
holdpoint |  |  | signoff | Sign Off
checkpoint-status |  |  | checkpoint | AE Smith Sign off
holdpoint |  |  | signoff | Sign Off
checkpoint-status |  |  | checkpoint | Witness Sign off
holdpoint |  |  | signoff | Sign Off
checkpoint-status |  |  | checkpoint | Consultant Sign off
holdpoint |  |  | signoff | Sign Off
checklist-flat |  |  | checklist | B3 - Leakage test report |  |  |  |  | Yes | V1 HBH - B3 - Leakage test report | 82b5a736-f11c-4cd4-88ec-366bbe93aaee
checkpoint-status |  |  | checkpoint | B3 Leakage Test Complete
text | 04f0fba0-551b-519c-b509-8ffeef9e5901 |  | textbox | Plant ref
text | 4b0ad8ed-2b11-548b-97df-43013fd56e47 |  | textbox | Test by
text | 71806a8e-8a5c-5d89-952c-d0fe75d8f6f9 |  | textbox | Test date
text | 3ddffb9c-6ddc-550e-be9f-05872603bdcf |  | textbox | Revision
checkpoint-status |  |  | checkpoint | This is to certify that a LEAKAGE test in accordance with HTM 02-01, paragraphs 15.59–15.60 was carried out on the piped system on this scheme and that during the test, a pressure as shown in column 2 below was held for the recorded duration. A certified pressure gauge was used for this work.
text | f562bcc6-adbb-5e22-969c-b16e9357ad8f |  | textbox | Certified pressure gauge reference number:
text | d2b22571-720c-5d3d-ad21-9a90a857aefc |  | textbox | Sections Tested
text | 210065ee-b3c4-58b3-8971-3c08a83d5efc |  | textbox | Test Pressure (kPa)
text | 8c0c03af-5b04-5957-8777-32aa0c4113de |  | textbox | Hours on test
text | 91e958c6-e13d-5006-8c93-0eb58d860c5a |  | textbox | Pressure drop (kPa)
text | 9fb3ca28-ef6b-5917-a505-dbde763884d0 |  | textbox | Pressure loss (kPa/hour)
text | 53415559-5e41-5588-9776-7d2bece6d306 |  | textbox | Pass/fail
label | 883c65a4-1470-59c4-ae3c-82966cec7562 |  | note | Pass / Fail requirements: < 0.2 kPa / 2h (400 kPa systems); < 0.5 kPa / 2h (700 kPa systems)
text | 1a63cb88-2bb2-50ee-993b-90a2dacfb5c6 |  | textbox | Contractors representative:
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 201a1379-1080-5388-94a7-65cf8fcb840f |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 0f57a196-3d8e-5692-929b-0457e360b81c |  | textbox | Consultant Name
checklist-flat |  |  | checklist | Energisation Inspection & Commissioning Test Sheet |  |  |  |  | Yes | V1 HBH - Energisation Inspection & Commissioning Test Sheet | 82ca1078-72c2-489c-a054-c0d16ddbfef0
checkpoint-status |  |  | checkpoint | Completed and signed sheet attached
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Ductwork First Fix |  |  |  |  | Yes | V1 HBH - Ductwork First Fix | 8b74bef6-0dd8-4fe4-b1d1-3036235a4bb0
checkpoint-status |  |  | checkpoint | Check-off shop drawings. Is it all installed correctly: i.e. each run complete
checkpoint-status |  |  | checkpoint | U/S of duct heights correct as per workshop drawings
checkpoint-status |  |  | checkpoint | All volume dampers set fully open
checkpoint-status |  |  | checkpoint | F/D access panel installed
checkpoint-status |  |  | checkpoint | Fire dampers
checkpoint-status |  |  | checkpoint | Duct hangers (Is spacing correct, is it level, are locknuts fitted)
checkpoint-status |  |  | checkpoint | Duct jointing (Are cleats fitted)
checkpoint-status |  |  | checkpoint | Flexible duct and supports (1m spacing)
checkpoint-status |  |  | checkpoint | Butterfly and outlet dampers open
checkpoint-status |  |  | checkpoint | Equipment / plant installed (FCU's, Chill beams, etc..)
checkpoint-status |  |  | checkpoint | Mounting and springs installed
checkpoint-status |  |  | checkpoint | Duct / equipment connections including flexibles, nuts, bolts and washers correct and tight
checkpoint-status |  |  | checkpoint | Approval
checklist-flat |  |  | checklist | Switchboard Installation Checklist |  |  |  |  | Yes | V1 HBH - Switchboard Installation Checklist | 9c5ddea3-6c4d-4bec-bdb7-13de0bd65df2
checkpoint-status |  |  | checkpoint | Document Reference
label | 515200ec-ed83-5cd3-a153-102d71159c56 |  | note | AES-MSSB-QUA-ITC-002
label | 28c29e95-8b13-5424-8279-2de9ae30294b |  | note | Issue Date – May 2018
checkpoint-status |  |  | checkpoint | Level, correct installation & mounting secure.
checkpoint-status |  |  | checkpoint | Doors & Escutcheons secure
checkpoint-status |  |  | checkpoint | Minimum clearance achieved
label | 8bd28908-ea27-5fd4-90c5-044f5621863b |  | note | Minimum required clearance off the front of any switchboard with an opening door be inserted 600mm clear from the door open at 90 deg.
checkpoint-status |  |  | checkpoint | Cable access / protection adequate.
checkpoint-status |  |  | checkpoint | Visible damage internal / external, loose items.
checkpoint-status |  |  | checkpoint | Signage on doors and covers
checkpoint-status |  |  | checkpoint | Labels Installed on Circuit Breakers
checkpoint-status |  |  | checkpoint | Electrical works complete.
checkpoint-status |  |  | checkpoint | Cleanliness. E.g.: vacuum of swarf
checkpoint-status |  |  | checkpoint | Report for completed works sent
checklist-sectioned |  |  | checklist | Pipework QA |  |  |  |  | Yes | V1 HBH - Pipework QA | 9e6bf9bf-862c-4284-8a29-9fc67b96f61e
checkpoint-group |  |  | section | Pipe Inspection
checkpoint-status |  |  | checkpoint | Equipment installed as per drawing
checkpoint-status |  |  | checkpoint | Pipework installed as per drawing
checkpoint-status |  |  | checkpoint | Condensate drains from units - Sufficient fall, track, vent if required
checkpoint-status |  |  | checkpoint | Size of pipework is correct as per drawing
checkpoint-status |  |  | checkpoint | Pipe penetrations are acoustically sealed where required
checkpoint-status |  |  | checkpoint | Access service details as advised via Drawing
checkpoint-status |  |  | checkpoint | Insulation blocks installed where required
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | Isolating and control valve installed correctly (IE: Orientation)
checkpoint-status |  |  | checkpoint | Drain-down facilities installed
checkpoint-status |  |  | checkpoint | Air vents/ bottles at top of risers and all high points
checkpoint-status |  |  | checkpoint | Pipe testing (Refer to separate sheet)
checkpoint-status |  |  | checkpoint | Approval
checkpoint-group |  |  | section | Pipe test
checkpoint-status |  |  | checkpoint | Test info
text | a4385aa0-b27b-5a92-8316-026f8d907f2c |  | textbox | System
text | 668abe44-f090-59f4-8a79-ee0acfb66677 |  | textbox | Drawing Number
text | 142fd9dc-cdff-57a6-9277-a5b9b3d349c5 |  | textbox | Location
text | b02b2345-3c6b-5d17-81ac-dbe3e88443fd |  | textbox | Revision number
text | 0411376d-cd14-51a5-9830-2d7fae593ac5 |  | textbox | Test pressure
text | e435a81f-bb27-50bb-97f7-b1568a852824 |  | textbox | Drop in pressure allowable
text | d1fa8a46-6c6b-51cc-8975-a05e336d261a |  | textbox | Time of test
text | f9d92fa9-3952-574c-bf8a-90d5611fe853 |  | textbox | Initial system pressure
text | 3e44bbdd-1430-50bf-9045-2690256573d2 |  | textbox | Final systems pressure
checklist-flat |  |  | checklist | B1 - Leakage test labelling marking sleeving supports |  |  |  |  | Yes | V1 HBH - B1 - Leakage test labelling marking sleeving supports | 9fc585aa-5022-44a2-af3a-be49000f6671
checkpoint-status |  |  | checkpoint | B1 Leakage Test Complete
text | be972ba9-f449-5a70-8513-2edbff60c485 |  | textbox | Hospital
text | 986cd3d8-29e5-56a9-8f03-93679b35d740 |  | textbox | Location or area
text | 07671adb-3d59-54fe-9db7-8c6e6e185d2d |  | textbox | Plant ref
text | 2b710c81-ea9a-58a0-88d4-8d905cd43a14 |  | textbox | Test by
text | 7b9faa5c-a109-5e0f-bc0d-ac83b03efe34 |  | textbox | Test date
text | 4b45d3a9-e868-51e6-9ccd-df62d9b21199 |  | textbox | Revision
checkpoint-status |  |  | checkpoint | Labelling and marking, sleeving and supports The following checks are to be carried out after the pipeline carcass installation is complete and prior to
boolean | 6f92902f-c5d1-5acb-b8d3-2af195176842 |  | tickbox | Visual check of pipeline labelling & marking
boolean | 8888de9c-e529-584c-991f-e9ad6c89d4f0 |  | tickbox | Visual check of pipeline sleeving & supports
checkpoint-status |  |  | checkpoint | Leakage Test details captured and recorded
label | a28b057f-5bcf-5827-b690-0d2f20afba16 |  | note | Leakage test - This is to certify that a LEAKAGE test in accordance with HTM 02-01, paragraphs 15.49–15.51 was carried out on the piped system on this scheme and that during the test, a pressure as shown in column 2 below was held for the recorded duration. A certified pressure gauge was used for this work.
text | 9a1335f2-798f-5c8d-8ca0-71d86cdfe617 |  | textbox | Certified pressure gauge reference number:
text | 980e5faa-9847-564c-8cd3-e995fd4d2e1d |  | textbox | Sections Tested
text | e05528cd-d17c-5aa6-88a7-f5e1330e4013 |  | textbox | Test Pressure (kPa)
text | 7e579fd5-6a9f-5b08-b72f-0057990c30d0 |  | textbox | Hours on test
text | b34b5ebf-7a94-5404-8c68-bd8f9e79dc08 |  | textbox | Pressure drop (kPa)
text | 62d1c22c-587e-5dc5-9196-0611dfc578c3 |  | textbox | Pressure loss (kPa/hour)
checkpoint-status |  |  | checkpoint | Pass/Fail Requirements Complete
label | 52a1aa3b-dd69-579c-95c7-905085ba8acc |  | note | Pass / Fail requirements: < 0.2 kPa / 2h (400 kPa systems); < 0.5 kPa / 2h (700 kPa systems)
text | b4060039-0bcb-5014-bbb5-1b18b119cb3c |  | textbox | For the purpose of carrying out this test, the following links have been made
checkpoint-status |  |  | checkpoint | This is to certify that above tests have been carried out and the following links have been removed:
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 7e7fb9f3-f8c6-59dd-a139-f47870712887 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 6f1f77df-f014-57ba-8d50-792ac411ed43 |  | textbox | Consultant Name
checklist-sectioned |  |  | checklist | Medical Gas QA |  |  |  |  | Yes | Medical Gas QA | a34a1e70-3360-48ca-9cdf-a1f9cf4c25cd
checkpoint-group |  |  | section | QA - First Fix
checkpoint-status |  |  | checkpoint | Pipework Installed as per drawing eg:( CO2 , O2 , MA4 , N2O , VAC, AGSS )
checkpoint-status |  |  | checkpoint | Pipework Labelled properly
checkpoint-status |  |  | checkpoint | Pipe elbows and Brackets installed
checkpoint-status |  |  | checkpoint | Pipe sizing is correct as per drawing / schematic
checkpoint-group |  |  | section | QA - Second Fix
checkpoint-status |  |  | checkpoint | Valve arrangement installed as per Detail specified drawing
checkpoint-status |  |  | checkpoint | Related AVSUs and pressure sensors installed
checkpoint-status |  |  | checkpoint | All bracings finished and tested for leaks
checkpoint-status |  |  | checkpoint | Seismic Installation
checkpoint-status |  |  | checkpoint | Form B1 - Leak Test
checkpoint-status |  |  | checkpoint | Form B2 - Cross Connection Test
checkpoint-status |  |  | checkpoint | Form B3 - Total Compressed Gas system Test
checkpoint-status |  |  | checkpoint | Contractors Test reports
checklist-flat |  |  | checklist | Summary of Tests |  |  |  |  | Yes | V1 HBH - Summary of Tests | b20a1772-01b1-4a63-83dc-fb4c8b1fff00
checkpoint-status |  |  | checkpoint | Summary of all tests completed
checklist-flat |  |  | checklist | Asbuilts |  |  |  |  | Yes | V1 HBH - Asbuilts | b3d7214a-f082-4c78-982e-65319f974e9f
checkpoint-status |  |  | checkpoint | Asbuilts Approved
checklist-sectioned |  |  | checklist | Fan Coil Units |  |  |  |  | Yes | Fan Coil Units | b46015ec-5b72-4315-9459-83d09485f82c
checkpoint-group |  |  | section | QA - First Fix
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | u/s of Unit at correct height
checkpoint-status |  |  | checkpoint | Mounting and Springs Installed
checkpoint-status |  |  | checkpoint | Correct Hanger Spacing
checkpoint-status |  |  | checkpoint | Location as per drawings
checkpoint-group |  |  | section | QA - Second Fix
checkpoint-status |  |  | checkpoint | Unit Plenum Boxes to be installed
checkpoint-status |  |  | checkpoint | Filters installed
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
checkpoint-status |  |  | checkpoint | P - trap installed
checkpoint-status |  |  | checkpoint | Driptray installed
checkpoint-status |  |  | checkpoint | Condensate Drains installed
checkpoint-status |  |  | checkpoint | Tundish provided by others
checkpoint-status |  |  | checkpoint | E4M wiring complete
checkpoint-status |  |  | checkpoint | E4M isolators installed in correct location
checkpoint-status |  |  | checkpoint | Temperature sensors and controllers installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | Equipment # |  |  |  |  | Yes | V1 HBH - Equipment # | bdfc0b1e-c7da-4f19-b9f5-9316541394a7
checkpoint-status |  |  | checkpoint | Make
checkpoint-status |  |  | checkpoint | Model
checkpoint-status |  |  | checkpoint | Serial Number
checkpoint-status |  |  | checkpoint | Transit bolts and locking pins removed
checkpoint-status |  |  | checkpoint | Correct location
checkpoint-status |  |  | checkpoint | Securely fixed as specified
checkpoint-status |  |  | checkpoint | Seismic mounts where applicable
checkpoint-status |  |  | checkpoint | Check unit for damage
checkpoint-status |  |  | checkpoint | Filters in place
checkpoint-status |  |  | checkpoint | Drains and moisture sensors
checklist-flat |  |  | checklist | Internal Duct Work Insulation |  |  |  |  | Yes | Internal Duct Work Insulation | c735b872-d409-4a5f-89aa-63b95820bd1f
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Duct materials - Fibreglass
checkpoint-status |  |  | checkpoint | Fixed with Adhesive weld pins and speed clips located not more than 75mm from the edges of the ducts and spaced not more than 300mm centres.
checkpoint-status |  |  | checkpoint | Longitudinal corner joints fixed with:
checkpoint-status |  |  | checkpoint | duct dimensions less than 300mm -25mmx25mm angles
checkpoint-status |  |  | checkpoint | duct dimensions 300mm and greater -50mmx50mm angles
checkpoint-status |  |  | checkpoint | Joints taped between adjacent of insulation with a 75mm wide strip of reinforced aluminium foil laminate tape.
checkpoint-status |  |  | checkpoint | Tape joints protected with 75mm wide sheet metal cover strip, pop riveted to the corner angles.
checklist-flat |  |  | checklist | Insulation QA |  |  |  |  | Yes | V1 HBH - Insulation QA | c9e6c1fe-331c-4ed2-b1b2-f76c13d18f71
checkpoint-status |  |  | checkpoint | Duct wrap insulation materials as per specs.
checkpoint-status |  |  | checkpoint | Approved aluminum foil duct as per specs.
checkpoint-status |  |  | checkpoint | Steel weld pins dia. Size (Flat head) As Per Specs
checkpoint-status |  |  | checkpoint | Duct pins spacing as per specs
checkpoint-status |  |  | checkpoint | Across minimum flange joints as per specs
checkpoint-status |  |  | checkpoint | Minimum lap at each joints as per specs
checkpoint-status |  |  | checkpoint | Have a secure vapor seal (Using aluminum foil tape)
checkpoint-status |  |  | checkpoint | Insulation edges tightly butted against flanges and adjoining insulation
checkpoint-status |  |  | checkpoint | Additional banding plastic blue straps.
checkpoint-status |  |  | checkpoint | Whenever possible, apply insulation to ducts prior to lifting into position, particularly where they are installed hard against walls or slabs
checklist-flat |  |  | checklist | Cable Installation Checklist |  |  |  |  | Yes | V1 HBH - Cable Installation Checklist | caa3c813-345f-4cb8-9b1d-cd1bc9754ab7
checkpoint-status |  |  | checkpoint | Document Reference
label | 75c22144-cced-5f3f-99c6-c2efd0c67451 |  | note | AES-CI-QUA-ITC-002
label | 84bde59d-039b-59c8-8d2a-52de1696bb69 |  | note | Issue Date – May 2018
checkpoint-status |  |  | checkpoint | Cable/s fastened securely along its entire length.
checkpoint-status |  |  | checkpoint | Correct segregation is maintained.
checkpoint-status |  |  | checkpoint | Cable/s clear of sharp edges and protected from mechanical damage.
checkpoint-status |  |  | checkpoint | Cable labels correspond to drawings.
checkpoint-status |  |  | checkpoint | Cable glands are tight and secure at both ends.
checkpoint-status |  |  | checkpoint | Cable/s terminated as per termination drawing.
checkpoint-status |  |  | checkpoint | Terminations are tight (torque records complete where required).
checkpoint-status |  |  | checkpoint | Report for completed works sent
checklist-flat |  |  | checklist | Brace Checklist |  |  |  |  | Yes | Brace Checklist | cc40cd2b-73bc-45d5-9f7f-63848c889675
checkpoint-status |  |  | checkpoint | Brace type
checkpoint-status |  |  | checkpoint | Fixing to structure
checkpoint-status |  |  | checkpoint | Service supporting
checkpoint-status |  |  | checkpoint | As per drawings
checklist-flat |  |  | checklist | Fans QA |  |  |  |  | Yes | V1 HBH - Fans QA | d775772b-e850-470c-ba97-7c3d44f530ca
checkpoint-status |  |  | checkpoint | Confirm Model Number
text | e54e9ea9-2c14-562c-88e0-0c2d0c7febbb |  | textbox | Serial number
checkpoint-status |  |  | checkpoint | Labelling
checkpoint-status |  |  | checkpoint | Upstand height 200mm Minimum high side
checkpoint-status |  |  | checkpoint | Fixed Securely
checkpoint-status |  |  | checkpoint | Under flashing / waterproofing completed
checkpoint-status |  |  | checkpoint | Check for Damage
checkpoint-status |  |  | checkpoint | Electrical QA Received
checklist-flat |  |  | checklist | Cowls |  |  |  |  | Yes | Cowls | da2220e3-a731-4422-a10f-1a709d1cd5ec
checkpoint-status |  |  | checkpoint | Outside Air Roof Cowl Installed
checkpoint-status |  |  | checkpoint | Builder - Waterproof and Seal to be installed
checklist-sectioned |  |  | checklist | Ductwork Insulation QA |  |  |  |  | Yes | V1 HBH - Ductwork Insulation QA | dbbf92e9-eaf6-43ba-a531-14510cfcbabb
checkpoint-group |  |  | section | External Duct Work Insulation
checkpoint-status |  |  | checkpoint | Using Approved Insulation Duct wrap materials - Multitel 18kg Density foiled 1-side 25mm thick
checkpoint-status |  |  | checkpoint | Cover entire surface with insulation including all flanges, stiffeners and support angles.
checkpoint-status |  |  | checkpoint | Provide 50mm over lapping at all joints.
checkpoint-status |  |  | checkpoint | Tape all joints with 75mm width (72mm on the Market) Aluminium foiled tape.
checkpoint-status |  |  | checkpoint | for all Ducts over 900mm in height or width where this is possible fixed bottom and sides of insulation with pin fixings at 450mm centres.
checkpoint-status |  |  | checkpoint | Using polypropylene fixing Bands 600mm centres.
checkpoint-status |  |  | checkpoint | Provide an overlap of at least 300mm where insulation changes from the inside of the duct to the outside.
checklist-flat |  |  | checklist | Condensate Insulation |  |  |  |  | Yes | Condensate Insulation | e0356e32-acc2-414a-975d-d15c5606d07c
checkpoint-status |  |  | checkpoint | Approved materials have been used (e.g. Elastomeric closed cell insulation), min 9m thick
checkpoint-status |  |  | checkpoint | Entire surface of pipe is covered from the indoor units' condensate trap, for a distance of 2m down the line
checkpoint-status |  |  | checkpoint | Adhesive is applied to any longitudinal and circumferential joints, as well as to the ends of the insulation to the pipe
checkpoint-status |  |  | checkpoint | Finish circumferential joints by wrapping with 50mm wide pressure-sensitive pre-adhered PVC tape.
checklist-sectioned |  |  | checklist | Ductwork QA |  |  |  |  | Yes | V1 HBH - Ductwork QA | e7fea584-70e3-49e8-b787-111174a7ea99
checkpoint-group |  |  | section | Rough in
checkpoint-status |  |  | checkpoint | Check-off shop drawings. Is it all installed correctly: i.e. each run complete
checkpoint-status |  |  | checkpoint | U/S of duct heights correct as per workshop drawings
checkpoint-status |  |  | checkpoint | All volume dampers set fully open
checkpoint-status |  |  | checkpoint | F/D access panel installed
checkpoint-status |  |  | checkpoint | Fire dampers
checkpoint-status |  |  | checkpoint | Duct hangers (Is spacing correct, is it level, are locknuts fitted)
checkpoint-status |  |  | checkpoint | Duct jointing (Are cleats fitted)
checkpoint-status |  |  | checkpoint | Flexible duct and supports (1m spacing)
checkpoint-status |  |  | checkpoint | Butterfly and outlet dampers open
checkpoint-status |  |  | checkpoint | Equipment / plant installed (FCU's, Chill beams, etc..)
checkpoint-status |  |  | checkpoint | Mounting and springs installed
checkpoint-status |  |  | checkpoint | Duct / equipment connections including flexibles, nuts, bolts and washers correct and tight
checkpoint-status |  |  | checkpoint | Approval
checkpoint-group |  |  | section | Fit off
checkpoint-status |  |  | checkpoint | Air Outlets
checkpoint-group |  |  | section | Volume control dampers manual & motorised
checkpoint-status |  |  | checkpoint | Installed in correct position
checkpoint-status |  |  | checkpoint | Full and correct movement available
checkpoint-status |  |  | checkpoint | Motors installed correctly and bracketed to prevent flexing
checkpoint-group |  |  | section | Valves and Pipe fittings
checkpoint-status |  |  | checkpoint | Installed as per Schematics and Piping layouts
checkpoint-status |  |  | checkpoint | Installed to allow proper clearances for access
checkpoint-status |  |  | checkpoint | No access to be installed anywhere near switchboards or electrical gear
checkpoint-group |  |  | section | Pumps
checkpoint-status |  |  | checkpoint | Installed as per manufacturer's instructions
checkpoint-status |  |  | checkpoint | Flexible couplings installed correctly and checked for alignment
checkpoint-status |  |  | checkpoint | Mechanical or gland seals correctly piped
checkpoint-status |  |  | checkpoint | Spring mounts fitted and level
checkpoint-group |  |  | section | Test gauges and test points
checkpoint-status |  |  | checkpoint | All test gauges and points installed as per workshop drawings , and easily viewable
checkpoint-group |  |  | section | Air vents
checkpoint-status |  |  | checkpoint | Air vents / air bottles fitted to all system high points
checklist-flat |  |  | checklist | B3 - Leakage Test Report |  |  |  |  | Yes | V1 HBH - B3 - Leakage Test Report | f33cce43-a837-4d92-9946-4d08d434bd38
checkpoint-status |  |  | checkpoint | Test details correctly established
text | c276d5ff-4e39-51ae-b388-56f41fb0ca61 |  | textbox | Hospital
text | 2f5ffa06-8eaf-5d87-a31f-6d0795517fc5 |  | textbox | Location or area
text | b225dad6-6584-5402-8708-c67b14880cdc |  | textbox | Plant ref
text | 99035354-8685-5519-9853-8996be0b7f77 |  | textbox | Test by
text | 7a4b75a1-b9c3-567b-877b-bbd28b3cc637 |  | textbox | Test date
text | 040b42e5-7ff2-54a1-b28c-e58b4f115e80 |  | textbox | Revision
checkpoint-status |  |  | checkpoint | Labelling and marking, sleeving and supports The following checks are to be carried out after the pipeline carcass installation is complete and prior to
checklist-flat |  |  | checklist | Chilled and Medium temp water systems |  |  |  |  | Yes | V1 HBH - Chilled and Medium temp water systems | f8029c09-9a13-49ab-b08c-4fb24a322d23
checkpoint-status |  |  | checkpoint | Pipework installed correctly
checkpoint-status |  |  | checkpoint | Correct installation of Valves, Pumps and hardware
checkpoint-status |  |  | checkpoint | Pipe insulation installed correctly
checkpoint-status |  |  | checkpoint | Pressure test complete
checkpoint-status |  |  | checkpoint | Sign off AE Smith
checkpoint-status |  |  | checkpoint | Sign off DHB
checkpoint-status |  |  | checkpoint | Sign off Hawkins
checklist-flat |  |  | checklist | Brace Number - |  |  |  |  | Yes | V1 HBH - Brace Number - | fd81afba-81ae-497f-9af1-989864c6021b
checkpoint-status |  |  | checkpoint | Brace type
text | e11423f0-8124-5d80-b6b6-91ced0cd3bbc |  | textbox | Enter Brace Type
checkpoint-status |  |  | checkpoint | Fixing to structure
checkpoint-status |  |  | checkpoint | Service Supporting
checkpoint-status |  |  | checkpoint | As per drawing
checklist-flat |  |  | checklist | CHW & HHW Piping (WELDING) |  |  |  |  | Yes | CHW & HHW Piping (WELDING) | feff34f0-9b4b-4f13-90bd-fea6afa8279a
checkpoint-status |  |  | checkpoint | Pipework installed as per Drawing
checkpoint-status |  |  | checkpoint | All fabricators/welders are qualified and have current tickets
checkpoint-status |  |  | checkpoint | Pipe sizing is correct and valving in correct location
checkpoint-status |  |  | checkpoint | Valve arrangement installed as per Detail specified drawing ie Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Expansion tank / Dosing Pod
checkpoint-status |  |  | checkpoint | Insulation blocks installed where required
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | Isolating and Control valve installed correctly
checkpoint-status |  |  | checkpoint | Hose piping installed
checkpoint-status |  |  | checkpoint | Air vents installed at all high points
checkpoint-status |  |  | checkpoint | All materials are in accordance with applicable AS/NZ standard
checkpoint-status |  |  | checkpoint | Welding procedure specification to be applied as per attached
checkpoint-status |  |  | checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint-status |  |  | checkpoint | Welding of pipework
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed