## Resources (2)
Type | Name | Values | Prefix | Postfix | Usage Count | User Addable | Template Name
ESSENTIAL CHECKLISTS
Mechanical Duct
checklist | QA - First Fix
checkpoint | Ducting / equipment connections including flexibles, nuts, bolts and washers correct and tight.
checkpoint | Ducts to be removed relocated / relocated as per drawings
checkpoint | All volume dampers set fully open
checkpoint | Duct Hangers (is spacing correct, installed level etc)
checkpoint | Insulation complete with acceptable standards
checkpoint | Duct jointing (Joints sealed, cleats fitted etc)
checkpoint | Sound attenuators installed
checklist | QA - Second Fix
checkpoint | Access Panels to be installed as per drawing
checkpoint | Flexible ducting installed with proper supports
checkpoint | Grille loaction as per updated drawings
checkpoint | Correct Equipment / Correct Grills / Diffuser Installed
Fan Coil Units
checklist | QA - First Fix
checkpoint Y/N | Correct Unit Installed
checkpoint | u/s of Unit at correct height
checkpoint | Mounting and Springs Installed
checkpoint | Correct Hanger Spacing
checkpoint Y/N | Location as per drawings
checklist | QA - Second Fix
checkpoint | Unit Plenum Boxes to be installed
checkpoint Y/N | Filters installed
checkpoint Y/N | Siesmic Bracing Installed
checkpoint Y/N | P - trap installed
checkpoint Y/N | Driptray installed
checkpoint Y/N | Condensate Drains installed
checkpoint Y/N | Tundish provided by others
checkpoint Y/N | E4M wiring complete
checkpoint Y/N | E4M isolators installed in correct location
checkpoint Y/N | Temperature sensors and controllers installed
checkpoint Y/N | Units Tested and Running
Fire Dampers
checklist | QA - First Fix
checkpoint | Correct FD Installed
checkpoint | Access Panel installed
checklist | QA - Second Fix
checkpoint | Drop Tested
checkpoint | Track is Clear
checkpoint | Fire damper labelled as per drawings
checkpoint | Builder to confirm Fire Sealed
Condensate pipe work
checklist | QA - First Fix
checkpoint | Correct pipe routing as per shop drawings
checkpoint | Proper Pipe size, lenghth, material used
checkpoint | Pipe joints, connections, Tees all tested for leaks
checkpoint | Correct pipe gradient
checkpoint | Correct bracket spacings
checkpoint | Proper pipe routes to drain pipes
External Duct Work Insulation QA
Insulate ducting as per drawing
Using Approved Insulation Ductwrap materials - Multitel 18kg Density foiled 1-side 25mm thick
Cover entire surface with insulation including all flanges,stiffeners and support angles.
Provide 50mm over lapping at all joints.
Tape all joints with 75mm width (72mm on the Market) Aluminium foiled tape.
Fixing for all Duct size 375mm to 750mm steel weld pins on centreline at 400mm spacing bottom surface only.
Fixing for all Duct size 750mm and greater steel weld pins at 400mm spacing maximum.
Fixing for all Duct riser steel weld pins at 400mm spacing maximum.
Using additional polypropylene fixing Bands 600mm centres.
Provide an overlap of atleast 300mm where insulation changes from the inside of the duct to the outside.
CHW & HHW Insulation
Approved material thickness has been used (Thermobreak®).
Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specificaiton
Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
Insulation is glued to the pipe with a 50mm wide band of adhesive (Ados F2®) at both ends of section to form the vapour barrier
Adhesive is applied along all longitudional and circumferential joints
A 50mm wide strip of pressure sensitive tape reinforced aluminium tape is applied to the insulation facing, along and around all joints
Mitre cut elbows have been used on all bends.
Apply reinforced aluminium tape for all longitudinal and circumferentila joints.
Metal cladding
Using approved cladding materials
Pipework less than 150mm outside diameter over insulation-Aluminimum or galv 0.5mm Thick
Pipework 150mm to 450mm outside diameter over insulation -Aluminium 0.7mm thick or Galv. 0.6mm thick.
Pipework/ Vessels / Evaporators over 450mm outside diameter over insulation -Aluminium 1.0 mm thicker Galv. 0.9mm thick.
Minimum 40mm overlapping circumferential joints.
Longitudinal joints faced away from view
Fixed with straps (same materials) for chilled water pipework or refrigerant pipework. Do not violate vapour barrier.
Used lobster back segments for curved surfaces. Seal all holes
Seal up all penetrations for gauges , instruments drains and vents.
Using Suitcase clips for all Readily removable at evaporator heads, strainers, and similar areas where removal for maintenance is anticipated.
Medical Gas - Checklist
checklist | QA - First Fix
checkpoint | Pipework Installed as per drawing eg:( CO2 , O2 , MA4 , N2O , VAC, AGSS )
checkpoint | Pipework Labelled properly
checkpoint | Pipe elbows and Brackets installed
checkpoint | Pipe sizing is correct as per drawing / schematic
checklist | QA - Second Fix
checkpoint | Valve arangment installed as per Detail specified drawing
checkpoint | Related AVSUs and pressure sensors installed
checkpoint | All bracings finished and tested for leaks
checkpoint Y/N | Seismic Installation
checkpoint | Form B1 - Leak Test
checkpoint | Form B2 - Cross Connection Test
checkpoint | Form B3 - Total Compressed Gas system Test
checkpoint | Contractors Test reports
Electrical - Checklist
checklist | QA - First Fix
checkpoint | Switch Board Mounted in correct position and level
checkpoint | Switch Board terminations complete
checkpoint Y/N | Board Tested
checkpoint | COC's Complete
checkpoint | BMS controllers and associated modules installed, wired correctly
checklist | QA - Second Fix
checkpoint | Wiring First Fix Complete
checkpoint | Cable Tray Installed Correctly
checkpoint | Electrical Isolators installed in Correct location
checkpoint | Units Terminated
checkpoint | Temp Sensors and Controllers Installed
checkpoint | Units Tested and Running
checkpoint | BMS controllers and associated modules installed wired correctly
checkpoint | BMS Modules installed / Wired correctly
checkpoint | All IOs are lablled and wired correctly as per BMS contractors instructions
AHU
checklist | QA - First Fix
checkpoint | Check if plinth site is correct
checkpoint | Correct Unit Installed as scheduled
checkpoint | Anti Vibration pads installed
checkpoint | Condensate Piping installed-if required
checkpoint | Tundish installed by others and connected up
checkpoint | Insulation Complete
checkpoint | Siesmic Bracing Installed
checkpoint | Pipework and coils installed
checklist | QA - Second Fix
checkpoint | Filters Installed
checkpoint | Return air fan installed correctly
checkpoint | All Manual and motorized dampers installed
checkpoint | Heating and chilled valves installed
checkpoint | Associated ductworks installed correctly
checkpoint | Flange capping installed correctly
checkpoint | Insulation instelled correctly
checkpoint | Sign off AE Smith
checkpoint | Commissioning complete
checklist | E4MQA - Second Fix
checkpoint | Wiring First Fix Complete
checkpoint | Cable Tray Installed Correctly
checkpoint | Electrical Isolators, VSDs installed in Correct location
checkpoint | Units Terminated
checkpoint | Temperature, pressure sensors and Controllers Installed
checkpoint | Units Tested and Running
Fans
checkpoint | Correct Equipment / plant installed
checkpoint | Mountings / springs installed
checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint | U/S of Fan heights correct as per Workshop Drawings.
checkpoint | Confirm Model number
checkpoint | Labelling
checkpoint | Commissioning complete
checklist | E4MQA - Second Fix
checkpoint | Wiring First Fix Complete
checkpoint | Cable Tray Installed Correctly
checkpoint | Electrical Isolators, VSDs installed in Correct location
checkpoint | Units Terminated
checkpoint | Temperature, pressure sensors and Controllers Installed
checkpoint | Units Tested and Running
Chillers / Buffer Tank / Dosing Pod / Pumps
checkpoint | Check if plinth site is correct
checkpoint | Correct Unit Installed
checkpoint | Setting out point correct
checkpoint | Anti Vibration pads to be installed if required
checkpoint | Corrrect Springs installed ( If required )
checkpoint | Condensate Piping installed ( If required )
checkpoint | Tundish installed by others and connected up ( If required )
checkpoint | Correct pumps installed as scheduled
checkpoint | all installes as per drawing - Drawing reference
checkpoint | Siesmic Bracing Installed
Shop Drawings
checkpoint | Drawing and revision number
checkpoint | Check-off Shop Drawings. Is it all services installed correctly.
checkpoint | If changes - Has been noted on as-built
checkpoint | All installed as per final revision shop drawings
Refrigiration pipework
checkpoint | Correct pipe routing as per drawings
checkpoint | Pipeworks are pressure tested with 580psi held for 24 Hrs
checkpoint | Proper brackets/supports spacings
checkpoint | proper specified insulation thickness/size installed on copper pipes
checkpoint | Correct labelling as per drawings
VRF Units
checklist | QA - First Fix
checkpoint | Correct model/make selected units installed
checkpoint | VRF units are installed in correct loaction as per drawings and schedule
checkpoint | VRF and condensing units are installed with correct vibration isolation on mountings
checkpoint | Confirm safety tray and/or condensate drainage provided to the units and they are piped to adjacent waste point
checkpoint | Confirm correct refrigeration pipe work and distribution boxes are installed as per the approved drawings
checkpoint | Proper brackets/support hangers installed
checklist | QA - Second Fix
checkpoint | Confirm adequate access provided to perform routine maintenance
checkpoint | Confirm correct electrical connections to the refrigeration system as per the manufacturers wiring schematic
checkpoint | Unit Mechanically and electrically Commissioned
checkpoint | Confirm, correct location on As Built drawings for record purposes
EXTRA CHECKLISTS
Cowls
checkpoint | Outside Air Roof Cowl Installed
checkpoint | Builder - Waterproof and Seal to be installed
Heater banks
checkpoint | Correct Equipment / plant installed
checkpoint | Mountings / springs installed
checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint | U/S of Equipemnt heights correct as per Workshop Drawings.
checkpoint | Fire rated insulation installed as per spec
checkpoint | All E4M wirings are installed and tested
Radiant Heaters
checkpoint | Correct Equipment / plant installed
checkpoint | Mountings / springs installed
checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint | U/S of Equipemnt heights correct as per Workshop Drawings.
checkpoint | All E4M wirings are installed and tested
Fire Rated Duct Insulation
checkpoint | Insulate ducting as per drawing
checkpoint | Using Approved Insulation Fire rated Ductwrap materials - 38mm thick Fyrewrap Elite 1.5 (FRL 120/120/120)
checkpoint | Install as per Manufacturer's Standards: (Trafalgar-Fyrewrap)
checkpoint | Fyrewrap duct wrap must completely covered the duct and there must not be any exposed sections or gaps.
checkpoint | A 100mm miniimum overlap must be used on all joints. Only the Three specified methods (telescope, checkerboard and butt splice methods.) of overlap may be used when adjoining Fyrewrap duct wraps.
checkpoint | Cut edges must be completely sealed with the specified pressure-sensitive aluminium foiled tape.
checkpoint | ≤600 x600 duct size Steel banding only spacing 40mm from edges over the overlap and one additional between overlaps.
checkpoint | ≤1200 x1200 duct size Steel banding and pins bottoms only spacing 40mm from edges over the overlap and one additional between overlaps. Pre-welded Pins grid 200mm centres.
checkpoint | ≥1200 x1200 duct size pins only all sides of duct pre-welded Pins grid 200mm centres.
checkpoint | Wall penetrations up to 1600mm duct size 75mm x 75mm x1.6mm steel angle 100mm width x 60mm thick maxilite board.
checkpoint | Length of second layer from the fire barrier FRL 60/60/60
checkpoint | Duct size 600mm x 600mm or less -second layer 1350mm
checkpoint | Duct size 600mm x 1200mm or less -second layer 1600mm
checkpoint | Duct size 600mm x 600mm -second layer 1900mm
checkpoint | Duct size 200mm x 2400mm -second layer 2500mm
checkpoint | Duct size 2400mm x 3600mm -second layer 2700mm
checkpoint | Used only Trafalgar Access Panels -must be fitting directly over the existing duct access panels fixed with rivets and fyreflex fire rated sealant, with a second local layer of Fyrewrap.
Internal Duct Work Insulation
checkpoint | Insulate ducting as per drawing
checkpoint | Using Approved Insulation Duct materials - Fibreglass
checkpoint | Fixed with Adhesive weld pins and speed clips located not more than 75mm from the edges of the ducts and spaced not more than 300mm centres.
checkpoint | Longitudinal corner joints fixed with:
checkpoint | duct dimensions less than 300mm -25mmx25mm angles
checkpoint | duct dimensions 300mm and greater -50mmx50mm angles
checkpoint | Joints taped between adjacent of insulation with a 75mm wide strip of reinforced aluminium foil laminate tape.
checkpoint | Tape joints protected with 75mm wide sheet metal cover strip, pop riveted to the corner angles.
External Acoustic Insulation (FCU's)
checkpoint | Insulate ducting as per drawing
checkpoint | Using Approved Insulation Acoustic wrap materials - 50mm Polyester sheet cover with 5kg wave bar
checkpoint | Cover all surface of the FCU units with insulation excluding the Vents and pipe outlet area.
checkpoint | fixing using self adhesive pins and polypropylene Bands with with buckles .
checkpoint | Tape all joints with 50mm width reinforced Aluminium foiled tape.
Condensate Insulation
checkpoint | Approved materials have been used (e.g. Elastomeric closed cell insulation), min 9m thick
checkpoint | Entire surface of pipe is covered from the indoor units' condensate trap, for a distance of 2m down the line
checkpoint | Adhesive is applied to any longitudional and circumferential joints, as well as to the ends of the insulaiton to the pipe
checkpoint | Finish circumferential joints by wrapping with 50mm wide pressure-sensitive pre-adhered PVC tape.
CHW & HHW Piping ( WELDING )
checkpoint Y/N | Pipework installed as per Drawing
checkpoint | All fabricators/welders are qualified and have current tickets
checkpoint | Pipe sizing is correct and valving in correct location
checkpoint | Valve arangment installed as per Detail specified drawing ie Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Exspansion tank / Dosing Pod
checkpoint | Insulation blocks installed where required
checkpoint Y/N | Correct hanger spacing
checkpoint | Isolating and Control valve installed correctly
checkpoint | Hose piping installed
checkpoint | Air vents installed at all high points
checkpoint | All materials are in accordance with applicable AS/NZ standard
checkpoint | Welding procedure spectification to be applied as per attached
checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint | Welding of pipework
checkpoint Y/N | Seismic Bracing Installed
CHW & HHW Piping ( VICTAULIC )
checkpoint Y/N | Pipework installed as per Drawing
checkpoint | All fabricators/welders are qualified and have current tickets
checkpoint | Pipe sizing is correct and valving in correct location
checkpoint | Valve arangment installed as per Detail specified drawing ie Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Exspansion tank / Dosing Pod
checkpoint | Insulation blocks installed where required
checkpoint | Correct hanger spacing
checkpoint | Isolating and Control valve installed correctly
checkpoint | Hose piping installed
checkpoint | Air vents installed at all high points
checkpoint | All materials are in accordance with applicable AS/NZ standard
checkpoint | The pipe OD and groove dimensions are within tolerance range as per victaulic specification
checkpoint | The corect coupling has been used for the correct joint i.e flexible or rigid
checkpoint | All fitting are vicataulic approved
checkpoint | Victaulic grease has been applied to the gasket and OD of pipe
checkpoint | Couplings are tightened by alternating sides equally
checkpoint | Bolt pads havefirm metal to metal contact
checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint Y/N | Seismic Bracing Installed
Duct / Equipment Cleaning
checkpoint | Specialized Cleaning contractor to clean Outdoor / Supply and Return air Ducting and equipment in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
checkpoint | Verification of ductwork cleanliness shall be by vacuum test ( gravimetric analysis ) in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
checkpoint | Undertake a second vacuum test immediately prior to handover.