## QA Folder Structure
QA Folder Structure |  |  |  |  | Checklists
Site QA
Resilience Australia
|  | Ground Floor & Interstatial Area | Offices Wet Fire
|  |  |  | Sprinklers Rough In & Fit Off | ENT-004 - Sprinkler rough in and fit off
|  |  |  | Hydrant Rough In & Fit Off | ENT-006 - Hydrants & Hosereels rough in and fit off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Extinguishers | ENT-016 - Fire Extinguishers
Offices Dry Fire
|  |  |  | Fire Electrical Rough In and Fit Off | ENT-013 - Fire Electrical rough in and fit off
|  |  |  | EWIS Rough in and Fit off | ENT-020 - Occupant Warning System/EWIS
Plantrooms Wet Fire
|  |  |  | Sprinklers Rough In & Fit Off | ENT-004 - Sprinkler rough in and fit off
|  |  |  | Sprinkler Control Valves | ENT-003 - Sprinkler control valves
|  |  |  | Hydrant Rough In & Fit Off | ENT-006 - Hydrants & Hosereels rough in and fit off
|  |  |  | Pumps | ENT-008 - Fire Service Pumps
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Extinguishers | ENT-016 - Fire Extinguishers
Plantrooms Dry Fire
|  |  |  | Fire Electrical Rough In and Fit Off | ENT-013 - Fire Electrical rough in and fit off
|  |  |  | EWIS Rough in and Fit off | ENT-020 - Occupant Warning System/EWIS
Drug Substance Wet Fire
|  |  |  | Sprinklers Rough In & Fit Off | ENT-004 - Sprinkler rough in and fit off
|  |  |  | Hydrant Rough In & Fit Off | ENT-006 - Hydrants & Hosereels rough in and fit off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Extinguishers | ENT-016 - Fire Extinguishers
Drug Substance Dry Fire
|  |  |  | Fire Electrical Rough In and Fit Off | ENT-013 - Fire Electrical rough in and fit off
|  |  |  | EWIS Rough in and Fit off | ENT-020 - Occupant Warning System/EWIS
Drug Product Wet Fire
|  |  |  | Sprinklers Rough In & Fit Off | ENT-004 - Sprinkler rough in and fit off
|  |  |  | Hydrant Rough In & Fit Off | ENT-006 - Hydrants & Hosereels rough in and fit off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Extinguishers | ENT-016 - Fire Extinguishers
Drug Product Dry Fire
|  |  | . | Fire Electrical Rough In and Fit Off | ENT-013 - Fire Electrical rough in and fit off
|  |  |  | EWIS Rough in and Fit off | ENT-020 - Occupant Warning System/EWIS
|  | Level 1 | Plantroom Wet Fire
|  |  |  | Sprinklers Rough In & Fit Off | ENT-004 - Sprinkler rough in and fit off
|  |  |  | Hydrant Rough In & Fit Off | ENT-006 - Hydrants & Hosereels rough in and fit off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Extinguishers | ENT-016 - Fire Extinguishers
Plantroom Dry Fire
|  |  |  | Fire Electrical Rough In and Fit Off | ENT-013 - Fire Electrical rough in and fit off
|  |  |  | EWIS Rough in and Fit off | ENT-020 - Occupant Warning System/EWIS
Warehouse Wet Fire
|  |  |  | Sprinklers Rough In & Fit Off | ENT-004 - Sprinkler rough in and fit off
|  |  |  | Hydrant Rough In & Fit Off | ENT-006 - Hydrants & Hosereels rough in and fit off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Extinguishers | ENT-016 - Fire Extinguishers
Warehouse Dry Fire
|  |  |  | Fire Electrical Rough In and Fit Off | ENT-013 - Fire Electrical rough in and fit off
|  |  |  | EWIS Rough in and Fit off | ENT-020 - Occupant Warning System/EWIS
|  | Preaction & Gas Risks | Ground Floor File & QA Doc Storage
|  |  |  | Gaseous Suppression Rough in & Fit off | ENT-002 - Gaseous Suppression
|  |  |  | MASDS Rough In & Fit off | ENT-019 - MASDS
|  |  |  | Pre Action Sprinkler Rough In & Fit Off | ENT-025 - Pre Action Sprinkler Rough In and Fit Off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
Ground Floor Switchroom
|  |  |  | Fire Electrical Rough In and Fit Off | ENT-013 - Fire Electrical rough in and fit off
|  |  |  | EWIS Rough in and Fit off | ENT-020 - Occupant Warning System/EWIS
|  |  |  | Pre Action Sprinkler Rough In & Fit Off | ENT-025 - Pre Action Sprinkler Rough In and Fit Off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
Level 1 - IDF 2111
|  |  |  | Gaseous Suppression Rough in & Fit off | ENT-002 - Gaseous Suppression
|  |  |  | MASDS Rough In & Fit off | ENT-019 - MASDS
|  |  |  | Pre Action Sprinkler Rough In & Fit Off | ENT-025 - Pre Action Sprinkler Rough In and Fit Off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
Level 1 - IDF 2122
|  |  |  | Gaseous Suppression Rough in & Fit off | ENT-002 - Gaseous Suppression
|  |  |  | MASDS Rough In & Fit off | ENT-019 - MASDS
|  |  |  | Pre Action Sprinkler Rough In & Fit Off | ENT-025 - Pre Action Sprinkler Rough In and Fit Off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
Level 1 - IDF 2130 & 2132
|  |  |  | Gaseous Suppression Rough in & Fit off | ENT-002 - Gaseous Suppression
|  |  |  | MASDS Rough In & Fit off | ENT-019 - MASDS
|  |  |  | Pre Action Sprinkler Rough In & Fit Off | ENT-025 - Pre Action Sprinkler Rough In and Fit Off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
Level 1 - IDF 2143
|  |  |  | Gaseous Suppression Rough in & Fit off | ENT-002 - Gaseous Suppression
|  |  |  | MASDS Rough In & Fit off | ENT-019 - MASDS
|  |  |  | Pre Action Sprinkler Rough In & Fit Off | ENT-025 - Pre Action Sprinkler Rough In and Fit Off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report

## Fire QA Checklists
type | name | values | prefix | postfix
checklist | ENT-001 - Inspection and Test Plan Schedule
section | Design
checkpoint | Hydraulic Calculations
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:2118
checkpoint | Gaseous System Design
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:14520
checkpoint | Fire Electrical
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:1670, AS:1668, AS:3000
section | Drafting
checkpoint | Drafting sprinkler
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:2419, AS:2441
label | QC Form: Drawing Register
checkpoint | Drafting Gaseous Suppression
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:4214
label | QC Form: Drawing Register
checkpoint | Drafting Fire Electrical
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:1670, AS:1668, AS:3000
label | QC Form: Drawing Register
section | Samples
checkpoint | Sample Tech Data
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: Specification
label | QC Form: Sample Register
section | Off-Site Manufacture
checkpoint | Fire pumps and tanks
label | Works By: Supplier
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:2941
checkpoint | Fire Indicator Panel
label | Works By: Supplier
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:1670, AS3000
section | Incoming Inspection
checkpoint | Sprinkler pipe
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:2118
label | QC Form: ENT-006 Hydrants and hosereels
checkpoint | Fire pumps and tanks
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:2941
label
checkpoint | Gaseous Fire Suppression
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:4214
label | QC Form: ENT-002 - Gaseous Suppression
checkpoint | Fire Electrical
label | Works By: Subcontractor
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Acceptance Criteria: AS:1670, AS:1668, AS:3000
label | QC Form: ENT-013 - Fire Detection
section | Installation
checkpoint | Fire Hydrant / Hosereels - Rough-In & Fit-Off
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:2419, AS:2441
label | QC Form: ENT-004 - Sprinkler rough in and fit off
checkpoint | Gaseous Fire Suppression - Rough-In & Fit-Off
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:4214
label | QC Form: ENT-002 - Gaseous Suppression
checkpoint | Fire Electrical - Rough-In & Fit-Off
label | Works By: Subcontractor
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:1670, AS:1668, AS:3000
label | QC Form: ENT-013 - Fire Detection
section | Commissioning
checkpoint | Fire Hydrant / Hosereels
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:2419, AS:2441
label | QC Form: ENT-006 - Hydrants & Hosereels
checkpoint | Gaseous Fire Suppression
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:4214
label | QC Form: ENT-002 - Gaseous Suppression
checkpoint | Fire Electrical
label | Works By: Subcontractor
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:1670
label | QC Form: ENT-015
checkpoint | Interface Checks - Mechanical / Fire
label | Works By: Entire
label | Entire: Review/Approve & Submitted
label | Consulting Engineer: Review/Approve
label | Builder: Review/Approve
label | Statutory Authority: Inspect & Review/Approve
label | Acceptance Criteria: AS:1670, AS:1668
label | QC Form: ENT-015
checkpoint | As-Installed Drawings and - Manuals (inc. Test Data)
label | Works By: Entire
label | Entire: Submitted
label | Consulting Engineer: Inspected & Review/Approve
label | Builder: Inspected & Review/Approve
checkpoint | Final Defects List
label | Works By: Entire
label | Entire: Inspected
label | Consulting Engineer: Inspected & Review/Approve
label | Builder: Inspected & Review/Approve
section | Defects Liability & Warranty
checkpoint | Entire to Provide Servicing information for Defects Liability Period
label | Works By: Entire Service Department
label | Entire: Provide
label | Builder: Review/Approve
label | Acceptance Criteria: AS:1851.3
checkpoint | Entire to Provide Warranty Information
label | Works By: Entire Service Department
label | Entire: Provide
label | Builder: Review/Approve
label | Acceptance Criteria: AS:1851.4
checklist | ENT-002 - Gaseous Suppression
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:2414
checkpoint | Pipe, Fittings, Manifolds, Hoses, Nozzles
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Cylinders
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Mains, ranges & riser pipes
checkpoint | Hangers location & spacing
checkpoint | Cylinders mounted as per manufacturer's recommendations
checkpoint | Cylinder hoses fitted correctly to discharge manifold
checkpoint | Cylinder pressure gauges fitted and indicating correctly
checkpoint | Discharge solenoid fitted
checkpoint | Manual release device fitted
checkpoint | Barometric dampers fitted
checkpoint | Penetrations Sealed
section | Installation Fit-Off
checkpoint | Discharge nozzles fitted
label | Certification AS:14520
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | ENT-003 - Sprinkler control valves
section | Installation
checkpoint | Specification reference checked
label | Specification Ref: AS:2118 and drawing
checkpoint | Valves and valve monitors installed
checkpoint | Pressure switches supplied and operable
checkpoint | Pressure gauges fitted
checkpoint | Drains connected
checkpoint | Statutory Labelling
checkpoint | Certification
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | ENT-004 - Sprinkler rough in and fit off
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:2118 and drawing
checkpoint | Pipe + Fittings
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Sprinklers
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Mains & branches installed to drawing
checkpoint | Hangers Location
checkpoint | Concealed spaces sprinker heads installed
checkpoint | Outlets capped
label | Specification Ref: drawing
checkpoint | Pressure test carried out
label | Specification Ref: ENT-009
checkpoint | Pentrations sealed
section | Installation Fit-Off
checkpoint | Sprinkler heads fitted to final locations as per coordinated RCP
checkpoint | Pressure test fit off
label | Specification Ref: ENT-009
section | Commissioning
label | By Independent Certifier - Attached below as applicable
checkpoint | Certification
label | Specification Ref: AS:2419, AS:2414
label | By Independent Certifier - Attached below as applicable
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-flat | ENT-005 Site works completion summary (sprinklers)
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Drawing number
text | Sprinklers rough in (ENT-004) date completed
text | Sprinklers fit off (ENT-004) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | ENT-006 - Hydrants & Hosereels rough in and fit off
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:2118, AS:2415, AS:2414, AS:1530, AS:2419 and drawing
text | Drawing & Revision # (or Attach photo below)
checkpoint | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint | Pipe + Fittings
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Hose Reels / Millcocks
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Mains & branches installed to drawing
checkpoint | Hangers Location
checkpoint | Pentrations sealed
section | Installation Fit-Off
checkpoint | Hose Reels (Minimum Clearances)
checkpoint | Millcocks (Minimum Clearances)
checkpoint | Pressure Test
label | Specification Ref: QCF-ENT-009
text | Test No.
checkpoint | Pipe Identification Labelling
checkpoint | Statutory Signage
label | Completed By Others
section | Commissioning
checkpoint | Flow Tests
label | By Independent Certifier - Attached below as applicable
checkpoint | Certification
label | By Independent Certifier - Attached below as applicable
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | ENT-007 Site works completion summary (hydrants and hosereels)
checkpoint | Drawing number
text | Hydrants/hosereels rough in (ENT-006) date completed
text | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (ENT-006) date completed
text | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (ENT-006) date completed
text | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (ENT-006) date completed
text | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (ENT-006) date completed
text | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (ENT-006) date completed
text | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (ENT-006) date completed
text | Hydrants/hosereels fit off (ENT-006) date completed
checkpoint | Drawing number
text | Hydrants/hosereels rough in (ENT-006) date completed
text | Hydrants/hosereels fit off (ENT-006) date completed
text | Sprinklers control valves (ENT-003) date completed
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes,No
checklist | ENT-FIRE-ITC07B Automatic Fire Sprinkler Flow Test Report Sheet
section | Pre-test details
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
text | Grid Ref
button | Area clear, tidy and accessible | Yes,No
label | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint | Year & Height - pass once entered
text | Year of installation
text | Head height (m)
select | Classification | xlh,oh,xhh,other (Specify below)
text | Other (Specify here)
checkpoint | Block Plan Flow 1 - pass once entered (n/a if not applicable)
text | l/min
text | kPa
checkpoint | Block Plan Flow 2 - pass once entered (n/a if not applicable)
text | l/min
text | kPa
checkpoint | Block Plan Flow 3 - pass once entered (n/a if not applicable)
text | l/min
text | kPa
checkpoint | Block Plan Flow 4 - pass once entered (n/a if not applicable)
text | l/min
text | kPa
checkpoint | Block Plan Flow5 - pass once entered (n/a if not applicable)
text | l/min
text | kPa
checkpoint | Water supply and mains - pass once entered
button | Water supply - grade | 1,2,3
text | Towns main #1
text | Towns main #2
checkpoint | Tank details - pass once entered
button | Tank supply (Y/N) | Yes,No
text | Capacity
text | Status
checkpoint | Pump details - pass once entered
select | Pump type | Electric,Diesel
text | Make
text | Serial no
text | Rated flow & pressure
text | Cut-in pressure
text | Pump orifice size (if electric)
text | K-factor (if electric)
text | Annubar size (if diesel)
button | Annubar type (if diesel) | Round,Diamond
text | Measuring device
section | Pressure Tests (kPa)
checkpoint | Pressure test 1 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 2 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 3 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 4 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 5 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 6 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 7 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 8 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 9 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
checkpoint | Pressure test 10 (n/a if not required)
text | %
text | L/min
text | T/main no.1
text | Inst. gauge
text | T/main no.2
text | Inst. gauge
text | Comb. main
text | Inst. gauge
section | Pressure Tests (psi)
checkpoint | Pressure test 1 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 2(n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 3 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 4 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 5 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 6 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 7 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 8 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 9 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
checkpoint | Pressure test 10 (n/a if not required)
text | %
text | L/min
text | Diesel disch.
text | Diesel suction
text | Inst. gauge
text | Elect. disch
text | Elect. suction
text | Inst. gauge
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | ENT-008 - Fire Service Pumps
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:2118, AS:2941 and drawing
checkpoint | Pumps
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Pipe
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Valves, Pressure Switch, Gauge
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation
checkpoint | Plinths positioned
checkpoint | Pipes installed to drawing
checkpoint | Valves located as drawing
checkpoint | Hangers location and spacing
checkpoint | Pipework, pressure switches and gauges and ancillary valves
checkpoint | Water Supply Available
checkpoint | Power available
checkpoint | Pressure Switches Set
checkpoint | Flow Test
checkpoint | Statutory Labelling
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist-flat | ENT-009 - Pressure Test Report
checkpoint | Test Details & Results
select | Select correct test criteria for Test | TEST CRITERIA HYDRANT HOSEREELS - HYDROSTATIC TEST – 1700kpa 2 HOURS,TEST CRITERIA FIRE SPRINKLERS - HYDROSTATIC TEST – 1700kpa 2 HOURS,TEST CRITERIA GAS SUPPRESSION - PNEUMATIC TEST – 300kpa 10 MINS - PRESSURE DROP SHALL NOT EXCEED 20% (60kpa),TEST CRITERIA WATER MIST - HYDROSTATIC TEST – 3300kpa 2 HOURS,Other (Specify below)
text | Other (Specify here)
text | Test No.
text | Gauge Reference (or Attach photo below)
text | Start Date
text | Start Time
text | Start Pressure
text | Final Pressure
text | Finish Time
checkpoint | Sign-Off Test completed to specification/drawings & Area left clean/tidy
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes,No
checklist-flat | ENT-010 - Calibration Record x5
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | 1.Calibration Details - Pass once entered
text | Equipment
text | ID Number
text | Expiry (If applicable)
text | Record Number
text | Date Calibrated
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes,No
checklist-flat | ENT-011 - Action Request Form
checkpoint | Action Request Details - Pass once entered
text | Action Request Number
label | This action request is a result of (Tick below)
bool | Audit
bool | Failure
bool | Non-Conformance
bool | Process Improvement Idea
bool | Customer Complaint
bool | Corrective/Preventative Action
checkpoint | Description of failure/Non Conformance/Improvement Idea/Customer Complaint
label | Send to Quality Manager for allocation of number and passing to appropriate person for action
text | Details
text | Reported By
text | Date
checkpoint | Investigate cause and list details
label | State action when and if there is a deeper underlying issue or problem
text | Details
text | Assigned To
text | Date of Completion
label | Signature Sign-Off attached below
checkpoint | List details of deeper underlying issue and corrective action
label | This section only applicable if above indicates the need
text | Details
text | Assigned To
text | Date of Completion
label | Signature Sign-Off attached below
checkpoint | Verification/Follow-up
text | Details
text | Assigned To
text | Date of Completion
label | Signature Sign-Off attached below
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Quality Manager Signature Sign-Off added below | Yes,No
checklist-flat | ENT-012 - Register of Non-Conformance Reports x10
checkpoint | Item 1. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes,No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes,No
checkpoint | Item 2. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes,No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes,No
checkpoint | Item 3. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes,No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes,No
checkpoint | Item 4. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes,No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes,No
checkpoint | Item 5. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes,No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes,No
checkpoint | Item 6. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes,No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes,No
checkpoint | Item 7. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes,No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes,No
checkpoint | Item 8. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes,No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes,No
checkpoint | Item 9. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes,No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes,No
checkpoint | Item 10. Pass once entered
text | Report Number
text | Description
button | Non-Conformance rectified (Input date below) | Yes,No
text | Date rectified
button | Non-Conformance approved (Input date below) | Yes,No
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes,No
checklist | ENT-013 - Fire Electrical rough in and fit off
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:1670, AS:3000, AS:1760, BCA and drawing
text | Drawing & Revision # (or Attach photo below)
checkpoint | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint | Cable/Conduit/Tray
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Fire Devices
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Correct cable used (eg Fire rated as required)
checkpoint | Cable Support
checkpoint | Segregation from other electrical services
checkpoint | Type of cable fixing and spacing
checkpoint | No cable joins between equipment
checkpoint | Conduit type
checkpoint | Conduit fixings
checkpoint | MASDS
section | Installation Fit-Off
checkpoint | Sensor locations as shown on drawings
checkpoint | Warden intercom phone locations
checkpoint | Break glass alarm located per drawings
checkpoint | Hold open devices located per drawings
checkpoint | Interface with Mechanical services
checkpoint | Interface with DDC
checkpoint | Sensors fixed correctly
checkpoint | FIP installed & connected
checkpoint | Connection of system to Tyco for Monitoring
checkpoint | MASDS Panel Fit Off
checkpoint | Strobes
section | Commissioning
checkpoint | Confirm all devices indicate at FDCIE
checkpoint | Confirm operation of all ancillary functions from FDCIE
checkpoint | FDCIE. Operate each alarm test, isolate and reset for each alarm zone
checkpoint | ASE. Confirm the master alarm facility receives all alarms
checkpoint | ASE. Confirm the master alarm facility receives all alarms
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | ENT-014 - Site Works Completion Summary (Fire Electrical)
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
text | Date completed
text | Level and/or area
checkpoint | Electrical Rough in (ENT-013)
checkpoint | Electrical Fit off (ENT-013)
section | Sign-Off
text | Date completed
checkpoint | Sign-Off Records completed
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Entire Fire Signature Sign-Off added below | Yes,No
checklist | ENT-016 - Fire Extinguishers
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:2444, AS:2941 and drawing
text | drawing reference
section | Installation
checkpoint | Secure cabinet
checkpoint | Extinguishers installed
checkpoint | Signage to meet code compliance
checkpoint | Hangers location and spacing
checkpoint | Fire blankets
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | ENT-018 - Water mist installation
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:4587, AS:1530, AS:2419, AS:2414 and drawing
checkpoint | Pipe, Fittings
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Nozzles
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Mains, ranges & riser pipes
checkpoint | Hangers location & spacing
checkpoint | Manual and automatic isolation valves
checkpoint | Pressure test carried out
label | Specification Ref: ENT-009
text | Test number
checkpoint | Penetrations sealed
section | Sign-Off
label | By Independent Certifier - Attached below as applicable
checkpoint | Certification
label | By Independent Certifier - Attached below as applicable
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | ENT-019 - MASDS
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:1670, AS:3000, BCA and drawing
checkpoint | Cable/Conduit/Tray
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | MASDS Sampling Pipework
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | MASDS Unit
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Correct cable used (eg Fire rated as required)
checkpoint | Cable Support
checkpoint | Segregation from other electrical services
checkpoint | Type of cable fixing & spacing
checkpoint | No cable joins between equipment
checkpoint | Conduit type
checkpoint | Conduit fixings
checkpoint | MASDS
section | Installation Fit-Off
checkpoint | Sampling Points Installed
checkpoint | MASDS installed & connected to FIP
checkpoint | MASDS Panel Fit Off
checkpoint | Strobes/ Illuminated signs installed
checkpoint | Confirm obscuration and alarm thresholds
checkpoint | Measure transport times
section | Commissioning
checkpoint | Obscuration Levels Set
checkpoint | Confirm Travel Times
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | ENT-020 - Occupant Warning System/EWIS
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:1670, AS:3000 and drawing
text | Drawing & Revision # (or Attach photo below)
checkpoint | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint | Cable/Conduit/Tray
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Speakers/Strobes
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Correct cable used (eg Fire rated as required)
checkpoint | Cable Support
checkpoint | Segregation from other electrical services
section | Installation Fit-Off
checkpoint | Speakers/Strobes
checkpoint | OWS Panel
section | Commissioning
checkpoint | Confirm operation of all speakers/strobes
checkpoint | Confirm decibel levels
checkpoint | Confirm OWS operation initiated from FDCIE
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable
checklist | ENT-025 - Pre Action Sprinkler Rough In and Fit Off
section | Pre-Start
checkpoint | Specification reference checked
label | Specification Ref: AS:2118 and drawing
checkpoint | Pipe + Fittings as Specified
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
checkpoint | Sprinklers
label | PASS if received in good condition - If not FAIL & Attach Photos/Comments below
section | Installation Rough-In
checkpoint | Mains & branches installed to drawing
checkpoint | Hangers Location
checkpoint | Concealed spaces sprinker heads installed
checkpoint | Outlets capped
label | Specification Ref: drawing
checkpoint | Pressure test carried out
label | Specification Ref: ENT-009
checkpoint | Pentrations sealed | Yes,No
label | Confirm pipework installed fall back to drain
checkpoint | Mains minimum 2mm per 1m. AS 2118.1 | Yes,No
checkpoint | Ranges minimum 4mm per 1m. | Yes,No
section | Installation Fit-Off
checkpoint | Sprinkler heads fitted to final locations as per coordinated RCP | Yes,No
checkpoint | Confirm all open ends capped.
label | Outlets capped | Yes,No
checkpoint | Confirm isolation and drain valves are closed.
label | Valves Closed | Yes,No
checkpoint | Fill pipework with air to 50kpa to confirm no open ends.
checkpoint | Pressure holds | Yes,No
checkpoint | Pressure test fit off
label | Specification Ref: ENT-009
section | Commissioning
label | By Independent Certifier - Attached below as applicable
checkpoint | Certification
label | Specification Ref: AS:2419, AS:2414
label | By Independent Certifier - Attached below as applicable
section | Sign-Off
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy - Builder final signature to be attached below if applicable

## EXAMPLE
QA Folder Structure |  |  |  |  | Checklists
These folders click through to one another - they need to move down a row and across a column
Site QA
Town Square
|  | B3 |  | Checklist is directly to the right of it's folder
South East Sprinklers
|  |  |  | Rough In & Fit Off | ENT-004 - Sprinkler rough in and fit off
|  |  |  | Pressure Test | ENT-009 - Pressure Test Report