## Project Structure
Folder Structure |  |  |  |  | Checklists
Site QA
| FD Photos | Riser | Level | FD # | FD Installation Photos Checklist
|  | B4 | L5 | 05-FD-9
05-FD-216
05-FD-217
05-FD-218
05-FD-219
05-FD-220
|  |  | L6 | 06-FD-209
06-FD-210
06-FD-211
06-FD-212
06-FD-213
06-FD-214
|  |  | L7 | 07-FD-211
07-FD-212
07-FD-214
07-FD-215
07-FD-243
07-FD-217
|  | B6 | L5 | 05-FD-215
|  |  | L6 | 06-FD-215
|  |  | L7 | 07-FD-218
|  | B10 | L4 | 04-FD-234
|  |  | L5 | 05-FD-259
|  |  | L6 | 06-FD-216
06-FD-217
06-FD-218
|  |  | L7 | 07-FD-229
|  | B12 | L8 | 8-FD-4
8-FD-5
8-FD-6
8-FD-7
|  | D8 | L6 | 06-FD-230
06-FD-231
06-FD-232
06-FD-233
06-FD-234
06-FD-235
06-FD-236
06-FD-237
06-FD-238
06-FD-239
|  |  | L7 | 07-FD-219
07-FD-220
07-FD-7
07-FD-222
07-FD-223
07-FD-224
07-FD-225
|  | E8 | L5 | 05-FD-228
05-FD-229
05-FD-233
05-FD-234
05-FD-235
05-FD-236
05-FD-237
05-FD-27
|  |  | L6 | 06-FD-244
|  |  | L7 | 07-FD-6

## Checklists
type | name | values
checklist-flat | FD Installation Checklist
checkpoint | FD Dimensions
Drawing #
label | Min Penetration = (1.01W + 10mm) x (1.01H + 10mm)
label | Max Penetration = (W+F) x (H+F)
label | F= Side of the angle against Fire Wall (mm)
label | AS.1682.2:2015
text | FD Size (W X H):
text | Flange Size (F):
text | Minimum Peno Size (W X H):
text | Maximum Peno Size (W X H):
text | Current Peno Size (W x H)
checkpoint | FD fully open; blades free to close and latch
checkpoint | FD orientation and air flow direction is correct
checkpoint | FD wholly within wall/ Slab; case is square
checkpoint | FD and Duct attached correctly/ Breakaway
checkpoint | Packing/expansion metal installed around casing
checkpoint | Opening in fire rated structure is correct
checkpoint | FD Flanges attached correctly
checkpoint | FD # corresponds to the one detailed on drawing
checkpoint | FD location corresponds to the one detailed on drawing
checkpoint | FD accessible for maintenance and service purposes
checkpoint | FD Installer Label complete
checkpoint | Fusible Link Fitted
checkpoint | Floor Mounted-2000 mm of Duct insulated above FD
checkpoint | Installation is approved
checkpoint | Corrective actions have been undertaken
checklist-flat | FD Installation Photos Checklist
checkpoint | Penetration Width
checkpoint | Penetration Height
checkpoint | Left and/or Rigth Gap
checkpoint | Top and/or Bottom Gap
checkpoint | FD c/w Retention Angles
checkpoint | FD Open
checkpoint | FD Close
checkpoint | FD Break Away Joint
checkpoint | FD with AP
checkpoint | Gaps Around FD Sealed
checkpoint | Sticker