## Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Documents & Photos |  | Documents & Photos | bffcef0f-8021-48d0-944a-42e1474d79e7
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| checkpoint | Please upload the relevant document(s) / photos and press PASS.
| checklist | GAJV-ITP-00184_5.0 - Concrete Work Diversion Chamber & Confluence Chamber | itp | GAJV-ITP-00184_5.0 - Concrete Work Diversion Chamber & Confluence Chamber | 6a67622b-c869-4a18-98ba-4c586e13f8ff
| section | 1.0 - Preliminaries
| checkpoint | 1.1 - Check - Drawings are IFC and current
57928a9a-9a51-566a-bf40-64518f620318 | note | RESPONSIBILITY - GAJV
9812caa8-b379-50a1-ab72-eb3228011770 | note | REQUIREMENTS / REFERENCE - Ensure the latest IFC drawings are used and available onsite
9fc89341-1bbe-5515-a90c-11bc0095066f | note | CONFORMANCE CRITERIA - Sighting of drawings
0dbe57ae-8ac8-5d05-ad4e-15da54830f4a | note | METHOD - Retain drawings
67af8400-aa37-5493-96c2-869f7a658b30 | note | FREQUENCY/PROCESS HELD - Before project execution
59d326fd-3565-55dd-8082-6326fe6e073a | note | TYPE - H
d5eed21c-df95-5f9f-8290-26c530676250 | note | ATTENDANCE REQUIRED - GAJV
70bd351d-62e7-57d5-88b1-8f726437df31 | note | RECORDS OR CHECKLISTS - DWG register with the drawing revision.
| signoff | HOLD POINT
| checkpoint | 1.2 - Check - CEP, SWMS, TMP and ESCP in place and signed off by personnel
94cf0369-51a5-5bb0-83e1-7e5adc8ea7fd | note | RESPONSIBILITY - GAJV
865055ef-36fb-54fe-a4bb-e4ac7a5db478 | note | REQUIREMENTS / REFERENCE - Ensure latest IFC plans are used and available onsite
8c0797b9-6d58-52f6-90f4-6a881a4438e2 | note | CONFORMANCE CRITERIA - Sighting of plans
2628175b-c241-5db8-b35d-3a5a19af6a5d | note | METHOD - Retain plans
b4adbe42-1e20-5db0-8fa6-629c4c8fc3be | note | FREQUENCY/PROCESS HELD - Before project execution
3ab964f4-6519-5fb8-badd-69c5462f546c | note | TYPE - H
3ccfe2df-5e62-55d0-9a26-6bbfe84cb282 | note | ATTENDANCE REQUIRED - GAJV
71511e78-b1e2-5303-8f85-3991be4bebaa | note | RECORDS OR CHECKLISTS - Plan register with the revision used
| signoff | HOLD POINT
| section | 2.0 - Materials (approval)
| checkpoint | 2.1 - Steel reinforcing
13aae76a-7987-5a75-b4bf-eedd86317b95 | note | RESPONSIBILITY - SEIPP
5d85eb84-f26f-51a0-9298-76ecb9b6734f | note | REQUIREMENTS / REFERENCE - DWG 2012036 Series NZS 4671/ 3109 GC-C4P – 4.1 and 4.1.1.10
bfb75160-6b11-5649-8258-509266c8d76a | note | CONFORMANCE CRITERIA - Grade 500E
a3db6e4f-2c9f-5a98-9c07-df9eafa77b41 | note | ○ Produced using micro-alloy process
09b359a3-c56e-569f-a7a2-873965476d27 | note | ○ GRP 16
fd276b04-7da1-56e9-8cdf-ef7b2d2c982d | note | ○ Chemical Anchor
b2dc386b-d50f-5b6f-ac6d-46dfb96ea8d9 | note | METHOD - Review mill certificate Reinforcing ID
c97c4e83-831d-5425-8c07-90f20708f306 | note | FREQUENCY/PROCESS HELD - Each batch
7afc5d92-7095-55bf-a780-49dd45a5d4e7 | note | TYPE - MAR
cffb35ad-b580-5cd4-9d96-7985e3a90e1e | note | ATTENDANCE REQUIRED - GAJV
09015887-0ecd-5b59-83cc-ccaca7fa0451 | note | RECORDS OR CHECKLISTS - Mill Certificates
| checkpoint | 2.2 - Concrete Mix Design (base, wall, benching)
5208219a-9ae0-54e5-ab3a-d149e935a1e1 | note | RESPONSIBILITY - SEIPP
6b8cf30c-a158-509f-a905-05edee8eebdd | note | REQUIREMENTS / REFERENCE - NZS3104, MS-41P – 5P, 5.2P DWG 2012036.861
956a8a5c-96e3-58a8-9ff0-f2e01a960fea | note | CONFORMANCE CRITERIA - Grade 45 MPa OPC
60bb38f8-4a04-5e4c-9d15-6c3691048237 | note | METHOD - Review mix design
fa8b0db4-71a6-5d46-8484-80a01f831467 | note | FREQUENCY/PROCESS HELD - Each mix design
e00e36b4-a598-58fd-b8a3-4fe3c8c94b09 | note | TYPE - MAR
2afd5adb-d70f-5435-a1ba-91d8c432af7a | note | ATTENDANCE REQUIRED - GAJV
e25ad336-2b83-5bdf-afbf-782df33aff9e | note | RECORDS OR CHECKLISTS - Aconex approval mail
| checkpoint | 2.3 - Block out infill concrete
a731c42f-baa5-5872-9467-662bd337ea85 | note | RESPONSIBILITY - SEIPP
f113a525-667f-5e61-b10f-b22f74d34c31 | note | REQUIREMENTS / REFERENCE - DWG 201236.862
d4a485f4-7f01-596c-83fb-475653c55ef8 | note | CONFORMANCE CRITERIA - Infill concrete to be S45/10
9dcb4ec8-e3db-5002-8768-019d0389a6ba | note | ○ Additional dosage of shrink reduction admixture as per drawing to be Sika control plus as or approved equivalent at 2.25% by weight of cement mass and shall comply with manufacturers requirements.
7215e53f-75ac-5f14-90e2-609e70c84e2b | note | ○ Additional dosage of admixture as per drawing to be Xypex admix C-5000 additive or approved equivalent at 0.6% by weight of cementitious content and shall comply with manufacturers requirements.
e6ec8baa-0dd6-5aab-8c10-f6377fad8cc9 | note | METHOD - Review dockets
48402f16-9b70-57bf-8146-5e0234fde2f6 | note | FREQUENCY/PROCESS HELD - Each delivery
8d0573d4-3422-50d4-89df-e81a1ffb511d | note | TYPE - S
afce5eb6-f139-57ff-9d10-36086f75f68a | note | ATTENDANCE REQUIRED - GAJV
6151ef63-8ec3-5297-87ca-11f790854837 | note | RECORDS OR CHECKLISTS - Material dockets
| checkpoint | 2.4 - Epoxy grout
ad8d8195-61fc-5c49-afb2-d7c7a6deaa4a | note | RESPONSIBILITY - SEIPP
cda24dde-3ef8-510b-ba59-40594a8c5b0d | note | REQUIREMENTS / REFERENCE - DWG 2012036.908, DWG 2012036.863 GC-C4P
7bc8cf31-d4f1-5825-878e-8c03361071b9 | note | CONFORMANCE CRITERIA - As per manufacturers data sheet
9f182802-f00e-5ac6-94a4-cc92baf956b5 | note | ○ 25W x 20 NITOSEAL SC600 SEALANT
b72c13d3-8cd6-552f-866b-e69f8edb37d2 | note | METHOD - Review product data sheet
35514aff-30c6-5ac1-9db2-da22c9ee8650 | note | FREQUENCY/PROCESS HELD - Each delivery
32468550-0b1b-5be5-92c9-c54e09bc3c39 | note | TYPE - MAR
5ab82b95-1153-5dbf-b5cf-25b44f598823 | note | ATTENDANCE REQUIRED - GAJV
97b0ab78-e1b4-59d6-80c7-b3726e022a91 | note | RECORDS OR CHECKLISTS - Material dockets
| checkpoint | 2.6 - Concrete pipe DN2100
9afd9b24-5d3f-5c40-b863-418b3233482c | note | RESPONSIBILITY - GAJV
9e85d86b-a511-5973-ad3e-ad5b1a7c3e3e | note | REQUIREMENTS / REFERENCE - DWG 2012034.183 MS-03
624fa07f-c0ec-5a0f-89d9-c9eb361189f9 | note | CONFORMANCE CRITERIA - RCRRJ Class 4
efda7093-a104-564c-8ff8-fe4239416318 | note | METHOD - Review shop drawings
0dc52f57-7ab9-5cbf-b02a-f9d0130ae7b6 | note | FREQUENCY/PROCESS HELD - Each Delivery
07f69663-c863-55e3-8f95-d3b29b871846 | note | TYPE - MAR
9e6795e6-5fa2-5f1e-b5fe-cfa1cf45c30f | note | ATTENDANCE REQUIRED - GAJV
a48ff96b-4c9e-576e-9874-579a7034d3f8 | note | RECORDS OR CHECKLISTS - QA from supplier
| checkpoint | 2.7 - Hydrophilic Strip
d4a05c3c-5c58-515b-950d-6845cdde3bfb | note | RESPONSIBILITY - SEIPP
78b2fd33-5fdb-5144-b443-e30c7e016f5b | note | REQUIREMENTS / REFERENCE - DWG 2012036.873, DWG 2012036.908
33fdf9eb-9158-5fec-bc79-9a2a786e8a24 | note | CONFORMANCE CRITERIA - CJ-0725-3K or approved equivalent
561a3aeb-a79b-5634-b29c-f06ea187b915 | note | METHOD - Review product data sheet
db9d0ab3-77ce-5d97-b157-cf755759c7cd | note | FREQUENCY/PROCESS HELD - Prior to commencement of work
bc41819c-29c4-516d-b167-c32e208cbd05 | note | TYPE - MAR
d0e28124-7aa1-5a02-97ae-25efda0f5821 | note | ATTENDANCE REQUIRED - GAJV
8f3a579d-d971-5508-a393-3991b8a2d388 | note | RECORDS OR CHECKLISTS - Material dockets
| checkpoint | 2.8 - PE Liner & filler rod
9a16867f-009a-5713-bada-1f283336d7a2 | note | RESPONSIBILITY - GAJV
84027ae3-b3f3-595f-8da5-c57bee2414d6 | note | REQUIREMENTS / REFERENCE - CG-C27P - Table 5-1
bdd261be-e06f-5810-ad0f-01a95e1e0f75 | note | CONFORMANCE CRITERIA - Technical data sheets
759ebfe4-7cd2-50f5-864d-15bd8f9ec853 | note | ○ Manufacturers certificates of compliance
da8bc667-b8d5-5cac-a744-f4b07cfd6643 | note | METHOD - Manufacturers certificate of compliance
0b9ccaf9-7b4b-53f2-9ebc-5a24e16fd62a | note | FREQUENCY/PROCESS HELD - Prior to commencement of work
cec16154-6a08-5ff0-9492-2bd71087db4c | note | TYPE - MAR
2f5d6747-5434-5362-9cd9-3b4c758f3566 | note | ATTENDANCE REQUIRED - GAJV
cdf61569-a78c-52e6-8a46-0d2c0326f32e | note | RECORDS OR CHECKLISTS - Material certificate and aconex mail approval
| checkpoint | 2.9 - Approved Curing compounds
2a71eb3f-e6a1-5862-aec5-9366362de1ed | note | RESPONSIBILITY - SEIPP
e7766869-61f9-5f33-b490-97f3ed6e130c | note | REQUIREMENTS / REFERENCE - MS-41P 11.3P
812d275b-42c2-5f66-8c75-3d42b12f5133 | note | CONFORMANCE CRITERIA - Curing to be accepted by the engineer
cbb8339e-34c3-56c8-a864-61109f42e016 | note | ○ Curing to meet the requirements of MS-41P
cebff3bc-7e56-51dc-be67-be0726656acf | note | ○ E-cure As per GAJV-MAR-000035
ce9614c5-a646-549f-80eb-a450c48e06a3 | note | METHOD - Review technical data
99ae1f18-2228-500f-a20b-5e1117782b4e | note | FREQUENCY/PROCESS HELD - Prior to commencement of work
645bc6d3-f228-55e0-bfa3-450666b3d36f | note | TYPE - MAR
29f997e4-41bc-55f2-a6f3-b0b807743742 | note | ATTENDANCE REQUIRED - GAJV
d854ea54-5fa9-5c77-98e2-103e6dc950df | note | RECORDS OR CHECKLISTS - Material certificate and aconex mail approval
| checkpoint | 2.10 - Materials for Concrete Repairs
a9f72906-7d44-5432-991d-959cb8c72e20 | note | RESPONSIBILITY - SEIPP
b41d4c7d-b3b0-5998-a132-246d401976e0 | note | REQUIREMENTS / REFERENCE - MS-41P
ad20d7fb-823c-522d-9ccc-3668812e9bd4 | note | CONFORMANCE CRITERIA - Technical data sheets
a40eebf4-1b72-52bc-a976-80c252ca4cf1 | note | METHOD - Review technical data
51e953fc-ced6-593b-89cd-ef933c7cad90 | note | FREQUENCY/PROCESS HELD - Prior to commencement of work
1d61f85c-28fb-5690-a15a-bfa9e998a589 | note | TYPE - MAR
61cf62b7-8277-5a01-99dc-16499d73682c | note | ATTENDANCE REQUIRED - GAJV
841246e2-2805-549e-a78a-895f87edbfbf | note | RECORDS OR CHECKLISTS - Material data sheet and aconex mail approval
| checkpoint | 2.11 - Manhole Covers
9b35259b-79fb-5986-b121-b7779c99e1f1 | note | RESPONSIBILITY - SEIPP
a1292044-99c7-574e-9056-0aa6cda5fa27 | note | REQUIREMENTS / REFERENCE - DWG 2012036 Series, NZS 3996 CG-
78397acb-47fc-596d-a965-8cac0fb99254 | note | CONFORMANCE CRITERIA - PAMREX DN700
3e29ba88-99c7-55ca-a10d-fcefb224e638 | note | ○ Gatic GM302C1212D, GM309C66D, GM303C6122D
ea01c962-251f-5b20-9bca-c8f0d28e9be8 | note | ○ Class D400 HN-HO-72 rated
80534048-9808-53af-bfde-6243dfa63f22 | note | ○ Manufacturers certificates of compliance
5ea99a5e-ed05-5a51-8777-18bc0bdfdbc2 | note | ○ Shop drawings.
c1571d31-22a5-5b74-a283-2166f6e89af5 | note | METHOD - Manufacturers certificate of compliance
e9e28f70-e439-5c71-8d6f-50ebe991d1f3 | note | FREQUENCY/PROCESS HELD - Prior to commencement of work
42fa9791-707f-5d62-b1a7-0ca5761dcbed | note | TYPE - S
70e05d8f-c2ff-5e73-8867-6f242d881876 | note | ATTENDANCE REQUIRED - GAJV
dfcb7428-f964-5a98-b1ea-cff2fbae6de2 | note | RECORDS OR CHECKLISTS - Dockets
| checkpoint | 2.12 - Stainless Steel Safety Grille
4c8f81eb-ba37-56d4-8de1-7403d6f2e7e0 | note | RESPONSIBILITY - SEIPP
8f3bfafb-132c-521a-8be8-8c4b1470a78d | note | REQUIREMENTS / REFERENCE - DWG 2012034.161, NZS 3996
9074333f-8363-57f6-9cc4-c541c6867ad1 | note | CONFORMANCE CRITERIA - Manufacturers certificates of compliance
ba60b03e-a37a-526c-bdf1-8fd07f6d73ac | note | ○ Shop drawings.
80387d39-b29d-5abe-a127-6c8d00d67c61 | note | METHOD - Final design and detail to be submitted to Watercare for review and approval
902d81a1-f4c9-5de7-94bd-f6c1ee08fc11 | note | FREQUENCY/PROCESS HELD - Prior to commencement of work
4d561a89-7da7-55c1-aaa6-b303737e4d6a | note | TYPE - MAR
4ddd1e87-514f-5879-9406-4d58c7bcd8be | note | ATTENDANCE REQUIRED - GAJV
57c66f7d-92ca-5b89-8f4d-aa78ac5fe533 | note | RECORDS OR CHECKLISTS - Material Approval
| checkpoint | 2.13 - Water stop
b737953f-1558-50a2-9130-97a099a9cd43 | note | RESPONSIBILITY - SEIPP
65009414-8321-52b7-9bd6-a4093bbfe72b | note | REQUIREMENTS / REFERENCE - CG-C4P 4.1.2P DWG 2012036.862
c19862ed-6035-5017-a79b-c68c99b1a4c2 | note | CONFORMANCE CRITERIA - Supercast Rearguard R or approved equivalent
0adebf48-bd1c-5055-9a43-d1fec0ba1fc8 | note | METHOD - Review product data sheet
dbd09a03-69da-5072-baae-2ac41c11e396 | note | FREQUENCY/PROCESS HELD - Prior to commencement of work
8d9b714f-2fad-5d26-9f52-a4927be981ad | note | TYPE - MAR
c981156d-10d6-55cf-84d5-4846a0870e3c | note | ATTENDANCE REQUIRED - GAJV
6242dd7c-cd2a-5230-9d3c-a680fb3ee819 | note | RECORDS OR CHECKLISTS - Material dockets
| checkpoint | 2.14 - Backfill Material – 7/3
b85d5733-02a6-5fbf-a360-6d54b7c44de2 | note | RESPONSIBILITY - SEIPP
bf576469-f8c0-5970-9256-d9afeb68460a | note | REQUIREMENTS / REFERENCE - Table C2-1 - Behind walls or chambers, CG_1, GAJV-RFI-002719
7c984fd8-0b98-53e9-a9fa-470360c4b49d | note | CONFORMANCE CRITERIA - Approved DM7/3
c579e338-f626-5ba9-9dea-a3945a28abb3 | note | METHOD - Material order review
9ef3a19d-a092-52c5-9dc3-0507be32dbd6 | note | FREQUENCY/PROCESS HELD - Before procurement
8e8ff7d2-ab28-5572-8367-5838cf19f027 | note | TYPE - MAR
952b022a-c593-581b-82f2-a8226c7c8170 | note | ATTENDANCE REQUIRED - GAJV
26ccd37e-9b1f-53a8-8581-683a86759fe1 | note | RECORDS OR CHECKLISTS - Delivery dockets, Quarry material test results for PSD, MDD
| checkpoint | 2.15 - Backfill Material – Flowable Fill
bfecd30b-1042-56d8-a991-e18953023fef | note | RESPONSIBILITY - SEIPP
ba5c8161-3f56-55ff-b7e1-4c50959b9cc3 | note | REQUIREMENTS / REFERENCE - GAJV-RFI-002719
eac8ee26-4427-5630-9b10-9d82d86aad65 | note | CONFORMANCE CRITERIA - Min 5 MPa flowable fill
52e72987-51ab-59c7-996b-5bf5ddf2f155 | note | METHOD - Review mix design
b3195485-fd75-55c8-b272-fe17e31c13b3 | note | FREQUENCY/PROCESS HELD - Each mix design
2bba1330-c92e-54b6-ac6a-9077d5d0962b | note | TYPE - MAR
fca1cd01-e419-52df-92cf-5d4a3231e4b9 | note | ATTENDANCE REQUIRED - GAJV
f6ba3218-56ba-5951-bd69-08da83a8a7a0 | note | RECORDS OR CHECKLISTS - Aconex approval mail
| section | 3.0 - Construction: Reinforcing Cages
| checkpoint | 3.1 - Reinforcement Placement
b85805c1-b165-5980-b11a-b1e65d20f400 | note | RESPONSIBILITY - SEIPP
f654b832-bc95-5bc8-b249-80c574f6e9cf | note | REQUIREMENTS / REFERENCE - DWG 2012036 Series
b722476e-2a65-5624-8b65-4b39a8cf3cf0 | note | ○ DWG 2012036.861
df851d69-da9c-5e2d-af99-b148242f5535 | note | ○ DWG 2012036.909
4b396f90-537a-5995-a594-fcaaf81b7f6a | note | ○ DWG 2012036.907
a374c504-b52f-5021-a161-6ed3425aa576 | note | ○ DWG 2012036.906
10d129db-38e1-5adf-9ade-264758f5d691 | note | ○ DWG 2012036.903
e61d9b0c-dde8-5b20-9e81-4b4b3d3ca5bd | note | ○ DWG 2012036.902
037b6f14-91de-5d64-9e45-d694ef5bbd2b | note | ○ DWG 2012036.900
a94f8aff-db17-572f-9650-a34b1f0bb3a2 | note | ○ DWG 2012036.893
030522c5-019e-5add-b6e4-dd8f68de50b9 | note | ○ DWG 2012036.891
74fdbcfe-3daa-5432-b013-3b955b6a1b16 | note | ○ DWG 2012036.890
1ddfe716-a861-5e30-8e99-7f7fcb19e044 | note | ○ DWG 2012036.889
5e8e180d-44c3-527d-98df-04bfbfdf2bd0 | note | ○ DWG 2012036.888
8f82a114-e9cc-5489-b70c-9caea27625c5 | note | ○ DWG 2012036.887
74e7c249-6781-58bd-beff-f99742bc3c3f | note | ○ DWG 2012036.886
8a7f0032-695c-5a41-9e84-c7d3df2f88f8 | note | ○ DWG 2012036.883
fc39bd38-a18c-5053-852c-eb8b0c19e21a | note | ○ DWG 2012036.882
baf6a022-ec80-592a-9ec4-27ac2337ed22 | note | ○ DWG 2012036.881
66d5e0df-b9a0-5105-92d6-b3b3b158e30b | note | ○ DWG 2012036.880
a514c3e4-9ad9-57da-a21a-0024a559c180 | note | ○ DWG 2012036.879
eadc96dc-a9b3-56cd-ad0a-ebf3437ae0a9 | note | ○ DWG 2012036.878
b1f8f8f5-6d94-52bf-987f-f353e6a53aed | note | ○ DWG 2012036.877
0fb926de-b538-5633-ad2c-cffeb3ac52c8 | note | ○ DWG 2012036.876
7d3bc8ba-cc5c-5756-9dad-c6842e13c826 | note | ○ DWG 2012036.875
0009e66b-5db8-5b7a-a1e6-f218ab310fde | note | ○ DWG 2012036.872
6346479d-4b0b-54b9-9a85-4a9f65168a82 | note | ○ DWG 2012036.871
98367d04-c76e-53de-b5d1-08f3fa298a42 | note | ○ DWG 2012036.870
ec4c2706-9c65-5ff3-8782-00dc8b8b9288 | note | ○ CG-C4P - 4.1.1 and 4.1.1.17 in accordance to NZS3109
43d3332f-6ae4-5e74-83b0-42219ef12f21 | note | CONFORMANCE CRITERIA - Ensure that the placed reinforcement complies in all respects with the Design Drawings and this Specification
7d5d5a13-9dbc-5170-8438-38f8a2f178f6 | note | ○ Minimum cover over reinforcement shall be as noted on the Design Drawings
002379cf-810c-5619-8aa4-1b72d6d124c4 | note | ○ Lap lengths shall generally be as detailed on the Design Drawings or otherwise as per 2012036.861
f2f68a8b-b8ce-524f-8e8d-0dbe43f45484 | note | ○ Not more than 50% of the reinforcing bars shall be lapped at any one section, i.e. laps shall be staggered.
ee5ede1c-be3a-5e45-8a39-f5490db7cd3f | note | METHOD - Visual Inspection and measurement on site
1a3ef4cc-9bbc-5fcc-8e9e-5a91c480e7b0 | note | FREQUENCY/PROCESS HELD - During and after steel placement
dbab0dbf-0b17-5aa7-8c91-5e0bd203f7f5 | note | TYPE - HP
1a899a32-9d8b-50f6-aa8f-dc130a747f98 | note | ATTENDANCE REQUIRED - WSL/GAJV
11dabfa9-0655-578a-89e0-883e650d51ec | note | RECORDS OR CHECKLISTS - Pre-pour checklist Photographs
| signoff | HOLD POINT
| checkpoint | 3.2 - Chemical Anchors/ Chem Set Bars
96681baa-8dfa-549c-b647-1a1924b61dc3 | note | RESPONSIBILITY - SEIPP
a8f23585-d557-54f1-9b9b-0647c643c118 | note | REQUIREMENTS / REFERENCE - DWG 2012036.909, DWG 2012036.861
18f58a90-ba96-5451-86b1-ce3b81a1fda2 | note | CONFORMANCE CRITERIA - SAF2507 Stainless Steel Anchors.
5ee9d484-0b33-5dd1-ad11-185b84d45ef1 | note | ○ HILTI RE-500-SD Injection Adhesive
f0901236-276b-5cf0-9133-08f20deacceb | note | METHOD - Review product data sheet. Manufacturers certificate of compliance.
bfe96271-6504-5cf0-8d43-374334502547 | note | FREQUENCY/PROCESS HELD - Prior to and after installation.
3d606f3b-45e2-55ba-840d-8ec6b7f523e1 | note | TYPE - HP
fbb5c964-d084-544d-83eb-0f6a9087963b | note | ATTENDANCE REQUIRED - WSL/GAJV
bae06ae3-c924-5e32-84ec-20e3a59aadb7 | note | RECORDS OR CHECKLISTS - Installation checklist
| signoff | HOLD POINT
| checkpoint | 3.3 - Rebar Couplers
50efa885-599f-5367-8c30-2778c0fb2bfd | note | RESPONSIBILITY - SEIPP
0d9ed5e3-0e0e-5240-a0b7-c5139ba0f7d6 | note | REQUIREMENTS / REFERENCE - NZS 3101, DWG 2012036.862
fbfad3ed-90cc-538c-8ca1-78ebe0a4e3ac | note | CONFORMANCE CRITERIA - ReidBar Steel coupler
1632d03e-0975-5657-90e9-b403bb3f6788 | note | ○ Use EPCON C8 XTREME as per manufactures instructions.
15fbb4ce-71d8-540f-a9df-7575d606f7f7 | note | ○ RB25CS instead.
6d7f3faa-cf5a-5990-8887-57a4865cfec1 | note | METHOD - Review product data sheet. Visual inspection.
0f70baaf-dae6-5821-bfa1-250ea102908d | note | FREQUENCY/PROCESS HELD - During and after placement
0a871ea1-1e23-56dc-8cf9-764b2395d26a | note | TYPE - HP
e52260e1-0623-5300-abe5-eda74e1f3fd7 | note | ATTENDANCE REQUIRED - WSL/GAJV
f94f15a9-077a-513b-bd25-4abb3bcdfb4d | note | RECORDS OR CHECKLISTS - Pre-pour checklist
| signoff | HOLD POINT
| checkpoint | 3.4 - Construction Joints and Water Stop Placement
4beca576-e024-58b2-9143-d333f6b43121 | note | RESPONSIBILITY - SEIPP
556835ad-b4f7-55d5-a559-bd33e39218e9 | note | REQUIREMENTS / REFERENCE - CG-C4P - 4.1.2P
df6514a0-3d80-526d-ad57-fa6a1a2a43af | note | ○ NZS 3109, Clause 5.6.3
e2a1b93e-2c99-52dc-b8df-7bd1670bc275 | note | ○ DWG 2012036 Series
34407715-de2f-5fdd-b471-88755841941c | note | ○ DWG 2012036.861
002bdbb0-c048-5963-9e33-4dbbfb81267d | note | ○ DWG 2012036.862
271db01b-fb80-5265-b53e-6c041bb4faad | note | ○ DWG 2012036.863
b1326505-99b2-54f9-ad77-caf8c511b981 | note | ○ DEG 2012036.873
903e608e-977a-5f83-98ad-3676cc8c9d34 | note | ○ DWG 2012036.903
d93ee42f-ef74-597e-98c0-1f03847116f0 | note | CONFORMANCE CRITERIA - Construction joints shall conform to NZS 3109, Clause 5.6.3, type B
f9c9d7b8-8873-596f-9c07-909f70b1435e | note | ○ Joint position shall be as shown on the Design Drawings unless otherwise agreed with the engineer
7ef2a640-7eef-5417-a871-42e95288a160 | note | ○ Water stops shall be placed as indicated on the drawings
f9da6d37-b544-5d49-ab0b-d4c0984ba064 | note | ○ Installed as per manufacturer’s specification
a2c8b43b-a2d7-554a-bdd9-c129dc2ae01e | note | ○ and care taken to prevent damage during concrete placement.
b88710db-31db-5f3b-9283-ed65d0786ec8 | note | METHOD - Visual inspection with reference to DWGS
8ced29a4-e2d7-5b2b-ad6b-b03812aae151 | note | FREQUENCY/PROCESS HELD - Before concrete pour
4ce7ec68-449a-5972-9ea9-43eea92a0d44 | note | TYPE - WP
39f8c772-962b-57fc-8d60-5b69781c7258 | note | ATTENDANCE REQUIRED - GAJV
3bfa0454-5ef7-5ca9-96a1-13cfa218d8e6 | note | RECORDS OR CHECKLISTS - Pre-pour checklist
| section | 4.0 - Construction: Formwork
| checkpoint | 4.1 - Formwork
58129c24-70d0-538f-ba5c-5391a024c8db | note | RESPONSIBILITY - SEIPP
29cc5094-79b1-51a5-ba6d-7758c869f1fd | note | REQUIREMENTS / REFERENCE - DWG 2012036 Series CG-C4P - 4.5P, NZS 3109 Section 5
d80fac02-b14a-54c9-8e00-cb7b6bb0b41b | note | CONFORMANCE CRITERIA - Formwork adequately supported and restrained – Design approved if necessary.
50cf4ba2-6e55-5d0b-9d99-08756c044b25 | note | ○ Formwork to be treated with release agent where in direct contact with concrete.
af8fa12d-9978-53c6-96cb-a955908e0062 | note | ○ Formwork must produce cast surfaces within a tolerance of +15 or -12mm on the given dimensions for width and ± 12mm for vertical height, and without visible offsets, bulges, or misalignment of the concrete.
bc5ae306-e88d-5eff-aeb6-5b4de86ad70b | note | METHOD - Visual Inspection
cd4c672c-1d61-5adc-8e91-4eb340293c58 | note | FREQUENCY/PROCESS HELD - Prior to concrete pour
f055d887-46a7-5647-a388-d96ed9830581 | note | TYPE - WP
6b531ce0-1298-5a8b-9686-02563bc1bec5 | note | ATTENDANCE REQUIRED - GAJV
8e92f4b3-df08-582b-af38-d8baa38e7792 | note | RECORDS OR CHECKLISTS - Pre-pour checklist Photographs
| checkpoint | 4.2 - Cast in items
2a500cea-32d8-53de-96bb-0eda90c7ce07 | note | RESPONSIBILITY - SEIPP
3d9318d9-e591-57bf-ba6c-836f1b3ef25d | note | REQUIREMENTS / REFERENCE - CG-P, DWG 2012034.185, DWG 2012036.863
bec0e20f-e057-59fa-a8b5-f2f967a7f381 | note | CONFORMANCE CRITERIA - Carry out inspection and confirm correct position prior to concrete pour.
a33f1710-83f4-59c7-b090-ec020ce54acd | note | ○ Ensure correct cover is achieved around the item.
bd46e036-792c-5a4d-b3b7-c89de490eee2 | note | METHOD - Visual Inspection
e83ad437-5692-5776-92ae-038e34872579 | note | FREQUENCY/PROCESS HELD - Prior to concrete pour
a1b9102a-a585-5bdb-9bf4-1c7605f85f9d | note | TYPE - HP
72d43436-b290-5af2-baed-2a4211c02335 | note | ATTENDANCE REQUIRED - WSL/GAJV
f4f4bb11-49db-50f3-8c57-1d77ee685cf2 | note | RECORDS OR CHECKLISTS - Pre-pour checklist
| signoff | HOLD POINT
| checkpoint | 4.3 - Block-out infill pipe penetration (if required)
631aa76a-333e-5110-85c3-09aaf90d5e40 | note | RESPONSIBILITY - SEIPP
7535d11c-2b21-598a-b961-6487eeae3faf | note | REQUIREMENTS / REFERENCE - CG-C4P-4, DWG 2013036.862
a14a4e31-8f56-5845-81cd-50c6e640d513 | note | CONFORMANCE CRITERIA - Ensure all reinforcement is to be continuous through block-outs during construction.
1255a8f8-1196-52e0-995d-107ef50d246b | note | ○ Ensure correct cover is achieved prior to concrete pour.
27815f49-4fb9-5cbc-86f6-67b837c9d33e | note | METHOD - Visual Inspection, Construction methodology and associated reinforcement curtailment details for approval before construction
9f0162cb-9fb7-5d73-80e3-5793498946cf | note | FREQUENCY/PROCESS HELD - Prior to concrete pour
87704685-197c-5e04-94f5-a5a75dd28521 | note | TYPE - HP
e821b146-92f3-5b62-930b-09d7d1b775ff | note | ATTENDANCE REQUIRED - WSL/GAJV
e8be86a9-de06-511b-a534-c38ae4522362 | note | RECORDS OR CHECKLISTS - Pre-pour Checklist
| signoff | HOLD POINT
| section | 5.0 - Post Construction: Concrete Works
| checkpoint | 5.1 - Concrete Testing (Consistency, 28-day compressive strength, Shrinkage, Permeability, Water absorption, Sulphite content, Alkali content, Chloride content, Temperature rise)
35b09046-0c97-50f8-b9ba-c49480e76b16 | note | RESPONSIBILITY - SEIPP
d5cbb6dd-d86d-5d85-b8ad-1f17fa295242 | note | REQUIREMENTS / REFERENCE - MS-41P - 5P MS-41P - 12P, MS-41P – table 6.1P
9159c022-14d5-5d0a-9e78-ff8a182ef923 | note | ○ Consistency: NZS 3109 and NZS 3112
2c986d5a-f5ba-52eb-abf9-159be3293d94 | note | ○ 28-day compressive strength: NZS 3109, Section 9 and NZS 3112
1392af3f-a443-5b93-81bc-bede1953da6d | note | ○ Shrinkage: AS 1012.13
7941fa39-fb1a-5c37-9aa8-2086854c8245 | note | ○ Permeability: DIN 1048
2122424d-aadb-5b52-a868-520499ba0ddf | note | ○ Water absorption: AS 4058, Appendix F
0e4e4609-3ba1-5157-993f-06a0694b1d38 | note | ○ Sulphite content: AS 1012.14
a256f902-25e5-5be2-beff-a29b0d373990 | note | ○ Alkali content: Chloride content: AS 1012.14
99a91fa0-6215-50ab-82f1-6c99c18416cf | note | ○ Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan)
472a08c5-3167-5ee7-b230-f2ef0686cce3 | note | CONFORMANCE CRITERIA - Consistency: For water retaining structures, slump tolerances shall be half those given in Table 9.1 of NZS 3109
bfb5b2aa-c7fb-5b94-86e1-8b08f0f786f1 | note | ○ 28-day compressive strength: 45 MPa
5d1d7cd0-586e-5fa1-bb3d-c4d17369b808 | note | ○ Shrinkage: 430mS at 21 days, 600 mS at 56 days with variance 10% precast & 15% for cast in-situ
ab881578-b9e9-56b4-bdb8-5c83a11aa033 | note | ○ Permeability: <20mm
db003975-1b77-5264-86f6-4d76a019110b | note | ○ Water absorption: <6.5%
3d13f50c-9f33-5341-b6bb-fc8e0d22ae9f | note | – Sulphite content: <4% by mass
295ab3dc-e13f-59a7-a42b-f792d386b787 | note | – Alkali content: <2.5kg/m3
441b5322-f7c0-5521-b506-c8609f9da00e | note | – Chloride content: As per table 5-1 of MS-41P
2a083951-57c2-58e1-a777-723b48889d51 | note | – Temperature rise: The lesser of: Thermal Control Plan limits
e57014bb-4853-58f1-b5c6-87c4bd42888b | note | • <70°C maximum
6a65017e-73fc-5de9-a142-e0a3745a722b | note | • <40°C temperature rise from its fresh concrete casting temperature
564ea6f4-a724-5810-8a5c-c32174426e87 | note | METHOD - IANZ Lab tests
171df7e0-140a-5d5d-949b-d52399951866 | note | FREQUENCY/PROCESS HELD - Consistency: Slump test every batch 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift or per 75m3 poured (NZS 3104), whichever is more frequent.
692f558a-6cf8-5049-8c13-fb2047970778 | note | ○ Shrinkage: Every 1,500m3 of concrete
0b9558fb-bac3-53c1-98f8-a016e5914814 | note | ○ Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete
d4c715b7-98e8-5259-81b4-a182f065a5a7 | note | ○ Shrinkage: Every 1,500m3 of concrete
21b5760d-0e52-54b7-9bff-60b96e5c3452 | note | ○ Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete
839ad3d3-2d8a-583b-afeb-67e23d4baa6e | note | ○ Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan)
3a29ed86-9a09-59fb-bbd5-99ee079ba9ee | note | TYPE - WP
1cb83cda-ccbb-5b71-b215-f76ff35179de | note | ATTENDANCE REQUIRED - WSL/GAJV
e8e9fae9-aa27-58ac-b112-50579dabc56d | note | RECORDS OR CHECKLISTS - Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests.
| checkpoint | 5.2 - Concrete Curing
aff8c174-9ef6-5e8d-8c7b-353c84f73362 | note | RESPONSIBILITY - SEIPP
877cc2af-9464-597c-827d-2aca7455373a | note | REQUIREMENTS / REFERENCE - NZS 3109 Clause 7.8 MS-41P 11P
8bdcca70-d7ba-5096-a732-982ce0b9d0fc | note | CONFORMANCE CRITERIA - Curing of cast-in-situ concrete elements shall be undertaken in accordance with the appropriate Material Specification
f970afcd-d33c-5014-abed-0e6077c08a42 | note | METHOD - Visually monitored on site as per thermal control plan
15566c19-4d8e-5802-9d3d-b93cbdc306e8 | note | FREQUENCY/PROCESS HELD - Hourly during peak sun hours and as required elsewhere
d7159479-0e60-57df-afde-59b5b292f4b2 | note | TYPE - WP
20a06f42-15f2-5fe6-985f-21f7e56023a5 | note | ATTENDANCE REQUIRED - SEIPP
83c041ae-f4ae-5ab0-95bb-5072d247d0cb | note | RECORDS OR CHECKLISTS - Post pour check sheet
| checkpoint | 5.3 - Concrete finishes
7b5c9115-c136-5a57-8641-0c3c8ef0f4ed | note | RESPONSIBILITY - SEIPP
c9ca5ea1-448b-5249-bd3d-afd7f5f2990a | note | REQUIREMENTS / REFERENCE - CG-C4P - 4.1.6P DWG 2012036.900
7ad27002-8e21-54ab-bfc9-ee22ed928fe7 | note | CONFORMANCE CRITERIA - Concrete finishes to be in line with the design drawings and specification.
12660eac-4185-5450-8e16-9ea257d49b70 | note | ○ Concrete finish to be U3/ F3 or approved finish where not PE lined.
7e9f4170-ec21-5abe-a4ce-20f9b41c85a2 | note | METHOD - Visual Inspection
06d1adf8-9582-51b9-808d-d9819512e70e | note | FREQUENCY/PROCESS HELD - Post pour
7304a0d8-1f40-529d-a44a-128f23067c38 | note | TYPE - WP
16963586-c536-5572-862f-1f5d897067f3 | note | ATTENDANCE REQUIRED - SEIPP
9de6bf6e-0034-5089-92c9-a0a3c3a4a832 | note | RECORDS OR CHECKLISTS - Post pour check sheet
| checkpoint | 5.4 - Concrete Benching
17bb2fc2-dd37-5e61-ba89-b62e9c9d21ce | note | RESPONSIBILITY - SEIPP
3401d4d4-a7eb-57ed-9247-52b0fc73b590 | note | REQUIREMENTS / REFERENCE - DWG 2012034.161, DWG 2012034.183 CG-C4.2.1
e97f6e37-31bd-5279-a5c8-5a759f453d05 | note | CONFORMANCE CRITERIA - Benching slope shall be 1:12 minimum unless otherwise noted in the drawings.
b748ad77-944c-5238-bf9a-41a8bd5c5b3f | note | ○ Plastering over the concrete finish is not accepted. The troweled finish is to be a U2 finish.
f09846f0-d6ca-5be8-b8ef-d4a4adc6774e | note | ○ Should have the same grade as walls and base slab.
cc3c9e7f-7bcd-545c-b1c0-35ace559602a | note | METHOD - Visual inspection
6c8a6b10-e9bf-555e-9917-9c97284222fa | note | FREQUENCY/PROCESS HELD - Post pour
79b47f91-f1a1-57e6-884f-caf98dd7a9d3 | note | TYPE - WP
13ee558e-0f36-58b0-bc68-70218d936f20 | note | ATTENDANCE REQUIRED - GAJV
943628b7-d1ca-5b68-9e29-dbf28d673ca4 | note | RECORDS OR CHECKLISTS - Post-pour check sheet
| checkpoint | 5.5 - Concrete Grouting lid panel joints
1a0b7a0a-eb61-579b-b5c7-210e84c94a01 | note | RESPONSIBILITY - SEIPP
4f7877ea-341d-564f-ba0d-1646f3f6a2f3 | note | REQUIREMENTS / REFERENCE - DWG 2012036.908
4396af12-468e-5a1f-b5e3-cf425bfe27ea | note | CONFORMANCE CRITERIA - Ensure joint details are as per the drawings
961d16ae-6d21-5029-ac85-8846c42f8f56 | note | METHOD - Visual inspection
d6c201ff-c908-5f66-b20b-e7a5d016c88d | note | FREQUENCY/PROCESS HELD - Before epoxy
93fc433d-84b4-5ea1-bf2a-58de219e13f2 | note | TYPE - WP
e0e3069d-66b0-55b4-984c-08e457157221 | note | ATTENDANCE REQUIRED - SEIPP
4666979d-f62d-5362-a490-376b95534785 | note | RECORDS OR CHECKLISTS - QA Check sheet
| checkpoint | 5.6 - Post Pour Inspection
2ee30d35-878e-504a-8979-534fb32bb446 | note | RESPONSIBILITY - SEIPP
ce6b63cc-f84e-5bb8-a6a2-1a431bf8a465 | note | REQUIREMENTS / REFERENCE - MS-41P
0f7d0bf5-c8e3-5820-b32b-5b9ac0927916 | note | CONFORMANCE CRITERIA - Full post pour inspection review of the concrete finish to identify surface defects, ensuring the specified curing has been undertaken, concrete cover checks or any other defects identified or non-conformances.
42795497-8f05-5c7e-aad7-b0ff25f35426 | note | METHOD - Visual Inspection
1315f51a-669a-5de8-9407-c15978ac1692 | note | FREQUENCY/PROCESS HELD - Post pour
9aa22dea-881b-548a-b20e-b03d6dd1f188 | note | TYPE - HP
6d900c15-2b23-52ee-b736-1bf50acbcff4 | note | ATTENDANCE REQUIRED - WSL/GAJV
d2e88ed2-8879-5926-9cba-5868299b418b | note | RECORDS OR CHECKLISTS - Post pour check sheet
| signoff | HOLD POINT
| checkpoint | 5.7 - Concrete Repairs
44ad43fa-5eab-53f7-a02b-3eef0b8ef5a9 | note | RESPONSIBILITY - SEIPP
66919a5d-19e9-5df2-9a28-dec48b2755e1 | note | REQUIREMENTS / REFERENCE - CG-C4P-4.6.1.4P
0986576a-4bc4-568d-b020-a05047ece8de | note | CONFORMANCE CRITERIA - Concrete repair using resin as per concrete structures specification.
0f983392-42f0-5150-9bfc-5bb89e6c5a5a | note | ○ As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure
2108480b-717e-58dd-afe6-e2ab95b1f39d | note | METHOD - Visual Inspections
79f5ed8c-53e7-5e73-87b7-b5cf4ceb122f | note | FREQUENCY/PROCESS HELD - Post Pour
26c6fd02-42b6-5e78-8bfc-e4c1cd56f480 | note | TYPE - HP
059435ee-957b-51fd-a490-c6657e933a24 | note | ATTENDANCE REQUIRED - WSL/GAJV
afa77e09-a889-51ae-8f40-28e76efe4066 | note | RECORDS OR CHECKLISTS - Post pour check sheet
| signoff | HOLD POINT
| section | 6.0 - Construction: Construction PE Liner
| checkpoint | 6.1 - PE Liner shop drawing
78c7c49c-7099-580b-b3d4-4597bbf83eb7 | note | RESPONSIBILITY - GAJV
46a6157c-e995-57fb-8bec-e539b35fb3f0 | note | REQUIREMENTS / REFERENCE - CG-C27P
c8097b20-9d73-57c7-9923-e779cf8630bf | note | CONFORMANCE CRITERIA - Shop drawing to be submitted to WSL
0413ad09-4339-5543-a571-8c2370f44f11 | note | METHOD - Submission
a1de3205-5191-5644-86ba-c2aa29dc41a0 | note | FREQUENCY/PROCESS HELD - 4 weeks prior to installation
6815f31a-b46e-5def-aa6c-27c4b35a90ff | note | TYPE - HP
54950d61-2379-56e3-83d9-6b01508fd7c0 | note | ATTENDANCE REQUIRED - GAJV
9dd4b7f4-fd7b-50c5-81a9-97078be5f6bc | note | RECORDS OR CHECKLISTS - Shop drawing submission
| signoff | HOLD POINT
| checkpoint | 6.2 - Extrusion weld certificates
6229bff4-66f4-58ec-9c6d-7fcd90bcdf0d | note | RESPONSIBILITY - SEIPP
dace4c30-549b-5258-a9e1-9a7a9c55d5f8 | note | REQUIREMENTS / REFERENCE - CG-C27P
9a874dda-025f-5a9c-b7eb-0d0bf5e8da90 | note | CONFORMANCE CRITERIA - Welders’ certificates for welding
62792879-b64f-5b02-bdd2-c25c10475bf8 | note | METHOD - Copy of certificates
44a992bf-a87d-5a6e-8cc3-69106414653a | note | FREQUENCY/PROCESS HELD - All welders
f1b02f95-0723-5aef-baf9-f4301754769e | note | TYPE - WP
b6edbc8a-567a-5b55-94b5-47dbc39e14f0 | note | ATTENDANCE REQUIRED - GAJV
f353eb18-2db9-5e3d-925c-be15ed00a40a | note | RECORDS OR CHECKLISTS - Copy of certificates
| checkpoint | 6.3 - PE Liner Prior To Pour
cabb64e8-8f39-5a94-a217-299f0d16cc36 | note | RESPONSIBILITY - SEIPP
14bb66d2-81be-5c6e-a517-25f01ad81077 | note | REQUIREMENTS / REFERENCE - CG-C27P
03bdc329-df2e-5d13-af66-83476757dbfb | note | CONFORMANCE CRITERIA - Final inspection of the liner to ensure its adequately restrained, no visible holes, no fixings left on the inside face, drainage lines are correctly positioned, no folds, bulges, all joints on the liner are adequately secured.
59a21d8a-ebb9-598e-8d1b-853cacb7ab17 | note | METHOD - Visual Inspection
71840d84-21c3-559a-bfc8-97c9e9de95fe | note | FREQUENCY/PROCESS HELD - Each pour
ddc3e763-648a-5db0-836b-7845e2bea2ca | note | TYPE - HP
28985758-bc86-52c2-a8a5-cfe46a72bcdf | note | ATTENDANCE REQUIRED - WSL/GAJV
15e004d2-17d9-5623-96bc-0cad8c498798 | note | RECORDS OR CHECKLISTS - Pre-Pour Inspection
| signoff | HOLD POINT
| checkpoint | 6.4 - Extrusion weld testing
837fa614-6630-567f-8864-e990de984cd1 | note | RESPONSIBILITY - SEIPP
fa82135c-a7ab-5f22-b497-9f6c397b45f8 | note | REQUIREMENTS / REFERENCE - CG-C27P, ASTM D4437, ASTM D5641, DVS 2227-1
0d549baf-8875-567c-b18f-624471169bfa | note | CONFORMANCE CRITERIA - As a minimum all site welds shall be tested.
056e9b3b-36c2-5835-a630-2f79bc0a8a5f | note | METHOD - Either vacuum box testing or high voltage spark testing. Visual inspection.
b23a26d5-1c87-533a-a1e0-233b2a014be5 | note | FREQUENCY/PROCESS HELD - All welds
67c08e62-f2a9-5521-9494-29c89a62f03b | note | TYPE - WP
92bc4faf-21ee-5154-9361-4473801675b9 | note | ATTENDANCE REQUIRED - WSL/GAJV
c17b38f2-1fe9-569f-b649-7245aa7f1fde | note | RECORDS OR CHECKLISTS - As recommended by the manufacturer. Checklist for visual inspection.
| checkpoint | 6.5 - Tapping Survey
5bee112f-af44-51a8-bbb9-e7d60ac9a8c7 | note | RESPONSIBILITY - SEIPP
cc61ed7b-7e3c-56e0-81d0-888076cffcfe | note | REQUIREMENTS / REFERENCE - AGRU Design & Installation Handbook. CG-C27P
f54372e6-7f09-5771-b468-729e8b3cb3d2 | note | CONFORMANCE CRITERIA - Tapping survey to identify voids
f3be2512-7e58-548e-974a-63fec3b3565b | note | ○ Voids to be repaired as recommended by the manufacturer.
8dff2356-db94-5973-928c-df2328667360 | note | ○ Pages 24 & 34 of Design & Installation handbook.
ad969df7-c4e7-510a-ad8a-33087c06d5d8 | note | METHOD - As recommended by the manufacturer. Rubber mallet delamination survey.
06f942df-f3cc-51f7-b79b-2386acaf1247 | note | FREQUENCY/PROCESS HELD - As recommended by the manufacturer
9d384670-aa51-5702-b6de-c5e332800938 | note | TYPE - WP
77b82b9e-784d-5f8b-ba11-6c8df887a985 | note | ATTENDANCE REQUIRED - WSL/GAJV
71a26719-a11b-5bb6-beeb-3ce880dee645 | note | RECORDS OR CHECKLISTS - Post pour check sheet
| checkpoint | 6.6 - Liner repairs
55a3a4d8-c15e-5b3e-9156-0cf97579f484 | note | RESPONSIBILITY - SEIPP
4ee6d182-db1e-52a3-aeb6-0607bcf5ade1 | note | REQUIREMENTS / REFERENCE - AGRU Design & Installation Handbook. CG-C27P, DVS 2227-1
05df669c-355f-5439-aae1-fa7919750ac6 | note | CONFORMANCE CRITERIA - As recommended by the manufacturer
160e118d-fa9f-5556-bbdb-eb0ea88507b7 | note | ○ Clearly mark out areas for repair
f03277e9-80a5-5525-8117-0e01e8230bd4 | note | ○ Extrusion welding
55c1139b-af0d-50f5-82f0-a43488d829a6 | note | ○ As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure
c8e6d862-b8de-530b-be02-ad0612f079fb | note | METHOD - Visual Inspection. Surfacing welds. Blanks. Panel strips.
e35d3706-702f-513d-a2fa-144c21edf58d | note | FREQUENCY/PROCESS HELD - As recommended by the manufacturer
7b9e7550-caf1-5027-a863-4e079ec6eda5 | note | TYPE - HP
f6756263-21bf-5d47-a26b-f2da318b3305 | note | ATTENDANCE REQUIRED - WSL/GAJV
29a381c1-4c30-57c2-ae8f-58e9147eab3b | note | RECORDS OR CHECKLISTS - PE Liner Checklist
| signoff | HOLD POINT
| section | 7.0 - Post Construction
| checkpoint | 7.1 - Final As built including PE membrane
37ee8d3f-7279-577b-8228-29ce8ed6c8a6 | note | RESPONSIBILITY - GAJV
369198de-c77c-55af-8078-7e979aea8480 | note | REQUIREMENTS / REFERENCE - IFC Drawings – 2012036 series, 2012034 series
69c66037-a58b-521f-a269-c3791c3e1156 | note | CONFORMANCE CRITERIA - Survey
30a5b875-7c15-5025-9426-5ffad1378567 | note | METHOD - Survey
384fcc34-d1d9-5fb6-8923-8a968b0c1ee1 | note | FREQUENCY/PROCESS HELD - At completion
a2478ca3-53a3-5a87-951b-248997c7bbc9 | note | TYPE - WP
f10471e5-2957-5474-a380-e47c6948c4a6 | note | ATTENDANCE REQUIRED - GAJV
fafbb76c-7885-5d0e-b03c-ef395c95f649 | note | RECORDS OR CHECKLISTS - As built drawings
| checkpoint | 7.2 - Hydrostatic testing
faa3bcb2-f8cd-5709-98aa-c0a07da1a3d2 | note | RESPONSIBILITY - SEIPP
c33f5d7e-3971-5b95-8367-6eebc215937c | note | REQUIREMENTS / REFERENCE - GC_1 10.5.2 D)
47bc0d91-f0f6-5da2-aea6-ade15425cc08 | note | CONFORMANCE CRITERIA - Infiltration test for manholes over 3.5m deep
2b982184-75c6-5945-ab97-eb00be23ee65 | note | ○ There are no visible leaks, wet patches or “sweating” at any of the pipe penetrations, seals or riser joints.
6b469645-ec7d-5a5b-aaa1-6c493c8fecc1 | note | METHOD - Infiltration test
17a089da-823f-5f33-8d21-fbc5f94e035d | note | FREQUENCY/PROCESS HELD - At completion
5d5a6171-e518-56e2-85c1-b99ea6aa7f57 | note | TYPE - HP
606878c1-002d-54f2-aa11-9f90b03e696e | note | ATTENDANCE REQUIRED - WSL/GAJV
c9df5c3e-6121-59ca-8a2a-b342dbb4a562 | note | RECORDS OR CHECKLISTS - Test record sheet
| signoff | HOLD POINT
| checkpoint | 7.3 - Backfilling – 7/3
9b75c1a1-d614-5aaf-a54d-b83336a52738 | note | RESPONSIBILITY - SEIPP
1b054af8-ed71-5587-baf4-0c11dcd9dd6d | note | REQUIREMENTS / REFERENCE - GAJV-RFI-002719
a6819cfc-1280-5012-b6f6-ca2e5f47eef7 | note | CONFORMANCE CRITERIA - Compacted to 90% of Maximum Dry Density
24abfcf5-a615-52df-9224-293d2a8b33fa | note | METHOD - NDM Test
a8470c2b-a024-58c2-b737-e25e632e8059 | note | FREQUENCY/PROCESS HELD - 1 Test per 500mm layer surrounding chamber
070bd5c7-a08e-5832-b880-55f157bf76c9 | note | TYPE - HP
26df0bab-5557-5001-9d03-b95a34e20980 | note | ATTENDANCE REQUIRED - GAJV
9fdb14fa-19b6-531a-a607-52df3607d050 | note | RECORDS OR CHECKLISTS - NDM Test Results
| signoff | HOLD POINT
| checkpoint | 7.4 - Concrete Testing – Flowable Fill (Consistency, 28-day compressive strength)
a6e9537b-fc30-547c-8fb1-157a771cac87 | note | RESPONSIBILITY - SEIPP
dccf7e2c-cd30-5910-81e4-9082d85af7d1 | note | REQUIREMENTS / REFERENCE - GAJV-RFI-002719
4c75413b-7168-5413-9abd-02b0f03e4505 | note | ○ Consistency: NZS 3109
deb8b7be-53a8-526e-be0b-441c81238527 | note | ○ 28-day compressive strength: NZS 3109, Section 9 and NZS 3112
329379fd-1fbb-5535-91ed-16cdea6c8369 | note | CONFORMANCE CRITERIA - Consistency: +/- 40mm - NZS 3109
d975ae82-e6c8-5d8d-b27d-dc381e933941 | note | ○ 28-day compressive strength: 5 MPa
559653b2-0903-5acc-82f7-09c8d6c74908 | note | METHOD - IANZ Lab tests
23ce4a37-1f46-5460-8e4a-dab424ef7d5b | note | FREQUENCY/PROCESS HELD - Consistency: Slump test every batch
0d17fd88-d1c5-5bd5-ab07-7aefb23320c7 | note | ○ 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift
31eac7ac-1045-554f-8030-dc128ef75946 | note | TYPE - WP
45d08e8e-0ca7-5b30-b888-ec6f55467172 | note | ATTENDANCE REQUIRED - GAJV
27d7014c-7487-5601-8b40-745cd373f732 | note | RECORDS OR CHECKLISTS - Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests.
| checkpoint | CONFORMANCE / VERIFICATION STATEMENT
751a52c1-2031-5758-bd22-fadafa4cac17 | note | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete, and any non-conformances have been closed out in accordance with the Projects requirements.
6b75df01-2a2a-5b41-a751-4859c0b96806 | note | Construction Lot checked by the Senior Project Engineer responsible for the works
4bbcaa59-5eda-5479-9a68-3aa2a265424c | textbox | Senior Project Engineer - PRINT NAME:
e670eda3-eb25-50a3-882f-c780b02bd1ef | date | Senior Project Engineer - DATE:
92642f58-0ba9-54a6-aecc-090da420b14b | note | Construction Lot verified and closed by Quality Management Representative
0065fe32-c757-52d9-9192-0c560e8f7bc1 | textbox | Quality Management Representative - PRINT NAME:
fd17d169-d6d8-586e-a32a-b314ba08d0c0 | date | Quality Management Representative - DATE:
afeecd1f-032d-5f3b-b092-32e672363bc6 | note | Independent Verification Review (if required) by:
8f992019-3fd3-5528-b216-6f5948b3916e | textbox | PRINT NAME:
3f8f4918-b41c-5a17-8adb-e87624ca7ee7 | date | DATE:
| signoff | ADD SIGNATURE
| checklist | Job Details |  | Job Details | 6db5edbe-7210-4246-bed4-bb95088244d8
| checkpoint | Project details entered below
25a133d8-dcfa-59d0-b63e-3c57dbb8e8ff | textbox | Job File Number
7bb91d29-fcaf-5a62-a491-7aff61c65c6d | textbox | Project Name
59a7327f-2b62-573a-8faf-29a0aac9d64d | textbox | Site Address
de1673e1-bb60-54aa-ba06-27e10e4306c4 | textbox | Main Contractor
01404661-b7c7-5c9a-8f00-b6f4a00e35a3 | textbox | Main Contractor POC
ab72d406-c7b5-5ea5-9afd-e109ca9033a5 | textbox | Structural Engineer
016bbd58-1720-5607-bdd0-60cd1259edd1 | textbox | Architect
| checklist | Site Visit Report |  | Site Visit Report | 881e2d4e-2310-412e-b9c7-3c83d3103f24
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| checkpoint | Details - Site Visit
2538dd73-8ee1-5b91-9dfe-9cfeaf2ca1de | textbox | Site/job:
4512d6eb-7cd7-5f8b-8ba5-3c714f06414a | textbox | Persons on site:
88615748-ebf4-5e68-802e-e46f681d520d | date | Date of site visit:
4aec21c2-3664-5c54-a43f-191ddae5a449 | textbox | Weekly report discussed with Site Manager:
1d069748-ffea-5542-a956-7e4644a40ad6 | textbox | Verify stage of work (provide comments):
09cdbe5d-90ac-5346-a8d5-e67ab812ae18 | textbox | Potential issues (provide comments):
| checkpoint | QA - Confirmation of quality of works completed since last site visit/QA
d8fa74ad-6e4c-5e6d-8bbb-4c9b3e3cb67f | tickbox | Walk through site with Lead Hand
fd78c28d-4e1d-5587-a84d-8ce90e4229b1 | tickbox | Visual check
b2fe804c-e505-573c-a0cb-6d954d122662 | tickbox | Query the Lead Hand's Install process
c6603646-c378-5782-86c1-f37a4366d0b8 | tickbox | Query the site contact satisfaction with work to date
d2409299-2760-5d39-a393-a3096a9d2dc4 | textbox | Other:
| checkpoint | Outstanding RFIs
| checkpoint | Outstanding VO's for approval
| checkpoint | Labour requirements for upcoming week
| checkpoint | Completion
| signoff | Click here to signoff
| checklist | Template Guide |  | Template Guide | 82451ab4-4381-429b-8142-c39b2e64ba80
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| checkpoint | This is a checkpoint
| checkpoint | This is a checkpoint with a dropdown (you can select only one option)
145540f4-b62e-575b-a498-ea8bfaa62f9d | dropdown | Select: | Option 1, Option 2, Option 3
| checkpoint | This is a checkpoint with a textbox
f5c30acb-33c6-5406-a831-b4a28ad5b898 | textbox | Description:
| checkpoint | This is a checkpoint with buttons (you can select only one option)
f727b086-0afe-5c0d-a05a-6f504d6efb14 | button | Select: | Option 1, Option 2, Option 3
| checkpoint | This is a checkpoint with a note
60371edb-6d7e-56c0-ae67-99660976431d | note | This is a note
| checkpoint | This is a checkpoint with tickboxes (you can select more than one option)
84e45ba3-a637-5274-9566-7f77ba64aabe | tickbox | White
5fbcc69f-8be7-5667-855a-86fdbed51c6b | tickbox | Grey
0b282e40-8662-52a5-8579-0a66654706e1 | tickbox | Black
| checkpoint | This is a checkpoint with a signoff
| signoff | SIGN HERE OR REQUEST SIGNOFF