## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | GAJV-ITP-00102_4.0 - Air Valve Install | itp |  |  |  |  | GAJV-ITP-00102_4.0 - Air Valve Install
section | 1.0 - Preliminaries
checkpoint | 1.1 - Drawing
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC drawing
label | CONFORMANCE CRITERIA - Latest issue of IFC drawings to be used for construction.
label | METHOD - Review construction drawings.
label | FREQUENCY/PROCESS HELD - Prior to construction.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Drawing register.
holdpoint | HOLD POINT
section | 2.0 - Fabrication and Material
checkpoint | 2.1 - Stainless steel pipe
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E.
label | CONFORMANCE CRITERIA - SS316L seamless SCH.80 pipe.
label | METHOD - Review material certificate.
label | FREQUENCY/PROCESS HELD - Upon delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate.
holdpoint | HOLD POINT
checkpoint | 2.2 - Flanges
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E.
label | CONFORMANCE CRITERIA - DN450, AS2129 table D flange with hole as per detail E of drawing 2012034.038. DN150, EN1092 PN16 RF flange, SS316L.
label | METHOD - Review material certificate.
label | FREQUENCY/PROCESS HELD - Upon delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate.
holdpoint | HOLD POINT
checkpoint | 2.3 - Gaskets
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E.
label | CONFORMANCE CRITERIA - DN450 3mm EPDM gasket to AS2129. DN150 2mm James Walker INCA or approved to suit EN1092.
label | METHOD - Review material certificate.
label | FREQUENCY/PROCESS HELD - Upon delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate.
holdpoint | HOLD POINT
checkpoint | 2.4 - Bolts/nuts/washers
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E.
label | CONFORMANCE CRITERIA - Stainless steel bolt set, bolt with hex nut and 2 washers, M20×8/set.
label | ○ Bolt: A4-70.
label | ○ Nut: A4-80.
label | ○ Washer: Class 100 HV.
label | METHOD - Review material certificate.
label | FREQUENCY/PROCESS HELD - Upon delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate.
holdpoint | HOLD POINT
checkpoint | 2.5 - Gate valve
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E. MS-15, MS-15P.
label | CONFORMANCE CRITERIA - Clockwise closing gate valve with EN1092, PN16 flange.
label | METHOD - Review material certificate.
label | FREQUENCY/PROCESS HELD - Upon delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate.
holdpoint | HOLD POINT
checkpoint | 2.6 - Air relief valve
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E. MS-40P.
label | CONFORMANCE CRITERIA - RF, EN1092 PN16, Vent-O-Max RGX or approved equivalent.
label | METHOD - Review material certificate.
label | FREQUENCY/PROCESS HELD - Upon delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate.
holdpoint | HOLD POINT
checkpoint | 2.7 - Welding procedure
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - General Mechanical Construction Standard - Section 6. ASME 9.
label | CONFORMANCE CRITERIA - Procedure Qualification Record (PQR).
label | METHOD - Review procedure.
label | FREQUENCY/PROCESS HELD - Before delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Approved WPS and PQR.
holdpoint | HOLD POINT
checkpoint | 2.8 - Weld cleaning
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - ASME B31.3
label | CONFORMANCE CRITERIA - Pickling and passivation to be done on all welds prior to delivery.
label | METHOD - Review procedure.
label | FREQUENCY/PROCESS HELD - Before delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pickling and passivation procedure. Supplier QA
holdpoint | HOLD POINT
checkpoint | 2.9 - Welding consumable
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - General Mechanical Construction Standard - Section 6. ASME II.
label | CONFORMANCE CRITERIA - As per ASME II, Part C.
label | METHOD - Review certs.
label | FREQUENCY/PROCESS HELD - Before delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Consumable certificates.
holdpoint | HOLD POINT
checkpoint | 2.10 - Welder qualification
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - General Mechanical Construction Standard - Section 6. ASME IX.
label | CONFORMANCE CRITERIA - Qualification approved as per ASME IX.
label | METHOD - Review qualification.
label | FREQUENCY/PROCESS HELD - Before fabrication.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Welder qualification certified.
holdpoint | HOLD POINT
checkpoint | 2.11 - Non-destructive testing (NDT)
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - General Mechanical Construction Standard - Section 6. ASME V. ASME B31.3.
label | CONFORMANCE CRITERIA - ASME V and ASME B31.3.
label | METHOD - Review test certificates.
label | FREQUENCY/PROCESS HELD - Before delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - NDT report.
holdpoint | HOLD POINT
checkpoint | 2.12 - NDT operator qualification
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - General Mechanical Construction Standard - Section 6. ASME V.
label | CONFORMANCE CRITERIA - Valid qualification.
label | METHOD - Review qualification.
label | FREQUENCY/PROCESS HELD - Before test.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Qualification record.
holdpoint | HOLD POINT
checkpoint | 2.13 - PE pipe
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E, 2012034.090 Rev A, 2012034.091 Rev A, 2012034.092 Rev A.
label | ○ 203 The Supply of Polyethylene (PE) Pipes and Fittings and 203P The Supply of Polyethylene (PE) Pipes and Fittings.
label | CONFORMANCE CRITERIA - PE 100 pipe. SDR as per drawing 2012034.038, 2012034.090, 2012034.091, 2012034.092.
label | ○ Pipe size: DN160.
label | METHOD - Review material certificate.
label | FREQUENCY/PROCESS HELD - Upon delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - QA record of the pipe.
holdpoint | HOLD POINT
checkpoint | 2.14 - PE pipe fitting
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E, 2012034.090 Rev A, 2012034.091 Rev A, 2012034.092 Rev A.
label | ○ 203 The Supply of Polyethylene (PE) Pipes and Fittings and 203P The Supply of Polyethylene (PE) Pipes and Fittings.
label | CONFORMANCE CRITERIA - PE 100 pipe. SDR as per drawing 2012034.038, 2012034.090, 2012034.091, 2012034.092.
label | ○ Pipe size: DN160.
label | METHOD - Review material certificate.
label | FREQUENCY/PROCESS HELD - Upon delivery.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - QA record of the pipe fitting.
holdpoint | HOLD POINT
checkpoint | 2.15 - Electrofusion test sample
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Section 225 - Installation of PE Pipelines, Section 225.16.
label | CONFORMANCE CRITERIA - Pre-construction test weld results pass.
label | METHOD - Review test certificates.
label | FREQUENCY/PROCESS HELD - Before site works.
label | TYPE - H
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - Passed test results.
holdpoint | HOLD POINT
checkpoint | 2.16 - Trench bedding and surround
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no.2010070.005 Rev C.
label | CONFORMANCE CRITERIA - Trench bedding and surround to be SAP7.
label | METHOD - Submit MAR to WSL.
label | FREQUENCY/PROCESS HELD - Before site works.
label | TYPE - H
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - Material certificate, approved MAR.
holdpoint | HOLD POINT
section | 3.0 - Construction
checkpoint | 3.1 - Compaction test for backfill
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - General Civil Construction Standard.
label | CONFORMANCE CRITERIA - Backfill compacted to 95% MDD.
label | METHOD - Nuclear density meter (NDM) test.
label | FREQUENCY/PROCESS HELD - Before fixing reinforcing.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - NDM test results.
holdpoint | HOLD POINT
checkpoint | 3.2 - Formwork install
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E.
label | CONFORMANCE CRITERIA - Dimensions are as per drawing 2012034.038.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - Pre-pour.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Concrete inspection checksheet.
checkpoint | 3.3 - Reinforcing placement
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E.
label | CONFORMANCE CRITERIA - Reinforcing to have minimum 75mm cover at the bottom and 50mm cover at the top.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - Once reinforcing is placed.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Concrete inspection checksheet.
checkpoint | 3.4 - Concrete testing
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Cylinder for compression strength testing.
label | CONFORMANCE CRITERIA - To be 30MPa in 28 days.
label | METHOD - Cylinder test.
label | FREQUENCY/PROCESS HELD - Requested at the time of order.
label | TYPE - W
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - Concrete test results.
checkpoint | 3.5 - Concrete pour
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Concrete pour complete.
label | CONFORMANCE CRITERIA - Concrete finish to be U5.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - Pre-pour and post pour.
label | TYPE - H
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - Concrete inspection checksheet.
holdpoint | HOLD POINT
checkpoint | 3.6 - Gasket install
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E. General Mechanical Construction Standard - Section 8.
label | CONFORMANCE CRITERIA - Correct size and correct gasket in place.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - During and post install.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Flanged connection checklist.
checkpoint | 3.7 - Bolts lubricated prior to install
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E. General Mechanical Construction Standard - Section 8.
label | CONFORMANCE CRITERIA - Bolts have lubrications. Lubrication to be nickel anti-seize compound.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - During and post install.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Flanged connection checklist.
checkpoint | 3.8 - Pipes and instruments assembled in the correct position and orientation
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E.
label | CONFORMANCE CRITERIA - Pipe and instruments installed in correct order as per drawing no. 2012034.038 Rev E.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - Post install.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Flanged connection checklist.
checkpoint | 3.9 - Valve operational (before and after installation)
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Valve manual.
label | CONFORMANCE CRITERIA - Valve opens and closes fully.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - Pre and Post install.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Flanged connection checklist.
checkpoint | 3.10 - All flanges to have correct number of bolts and bolts to be tightened to specified torque.
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing no. 2012034.038 Rev E – Note 3. General Mechanical Construction Standard - Section 8.3.2.
label | CONFORMANCE CRITERIA - All flanges have the correct number of bolts required.
label | ○ DN450 flanges to be torqued to 250Nm in 110Nm increments. DN150 flanges to be torqued to 138Nm.
label | ○ Torque meter calibration record.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - Post install.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Flanged connection checklist. Torque meter calibration record.
checkpoint | 3.11 - Weld surface preparation
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - PIPA POP001 – Electrofusion Jointing of PE Pipes and Fittings for Pressure Applications - Issue 8.1 August 2021.
label | CONFORMANCE CRITERIA - Surface cleaned before peeling pipe.
label | ○ Correct pipe peeling tool used - Metal files, rasps, emery paper etc are NOT to be used.
label | ○ Surface cleaned with an authorised Isopropanol impregnated pipe wipe.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - During pipe peeling.
label | TYPE - H
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - PE pipe install checklist.
holdpoint | HOLD POINT
checkpoint | 3.12 - Electrofusion construction weld test
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Section 225 - Installation of PE Pipelines, Section 225.16.
label | CONFORMANCE CRITERIA - Construction test weld results pass.
label | METHOD - Weld test result.
label | FREQUENCY/PROCESS HELD - During pipe welding.
label | TYPE - W
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - PE pipe install checklist.
checkpoint | 3.13 - Trench bedding
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no.2010070.005 Rev C.
label | CONFORMANCE CRITERIA - Trench bedding as per 2010070.005 - Rev C, Granular Surround. Bedding to be minimum 150mm.
label | ○ Compaction to be 95% MDD or 32CIV.
label | ○ Backfill in 230mm layers
label | METHOD - Visual inspection. Clegg test
label | FREQUENCY/PROCESS HELD - Prior to pipe laying.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - PE pipe install checklist. Clegg value recorded on checklist.
checkpoint | 3.14 - Pipe install
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no.2012034.090 Rev A.
label | CONFORMANCE CRITERIA - Pipe installed at the correct invert level.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - Prior to trench fill.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - PE pipe install checklist.
checkpoint | 3.15 - Trench surround
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawing no.2010070.005 Rev C, General Civil Construction Standards.
label | CONFORMANCE CRITERIA - Trench surround as per 2010070.005 - Rev C, Granular Surround. Pipe surround to be 150mm cover.
label | ○ Compaction to be 95% MDD or 32CIV.
label | ○ Backfill in 230mm layers
label | METHOD - Visual inspection. Clegg test.
label | FREQUENCY/PROCESS HELD - Prior to backfill.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - PE pipe install checklist. Clegg value recorded on checklist.
checkpoint | 3.16 - Tracer wire and label strip
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - AS/NZS 2033.
label | CONFORMANCE CRITERIA - Tracer wire and label strip installed the trench surround.
label | METHOD - Visual inspection.
label | FREQUENCY/PROCESS HELD - Prior to backfill.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - PE pipe install checklist and photo.
checkpoint | 3.17 - Trench backfill
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - AS/NZS 2033, General Civil Construction Standards.
label | CONFORMANCE CRITERIA - Backfill over pipe surround as per AS/NZS 2033 - Section 5.
label | ○ Compaction to be 95% MDD or 32CIV.
label | ○ Backfill in 230mm layers
label | METHOD - Visual inspection. Clegg test
label | FREQUENCY/PROCESS HELD - Once backfill is complete.
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - PE pipe install checklist. Clegg value recorded on checklist.
checkpoint | 3.18 - As-builts
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - -
label | CONFORMANCE CRITERIA - As Built surveys to be completed
label | METHOD - Record any changes.
label | FREQUENCY/PROCESS HELD - During construction.
label | TYPE - W
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - Asbuilt Survey
checkpoint | 3.19 - Install Odour Bed 3 South ARV Leacheate Pipework
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - As per DWG2012034.114
label | CONFORMANCE CRITERIA - Pipe support clamps to be spaced at maximum 2m centres.
label | ○ DN50 PN12 PVC pipe to be used Proposed PVC pipe to be fixed at a minimum grade of 1:180
label | METHOD - Visual inspection
label | FREQUENCY/PROCESS HELD - During installation
label | TYPE - W
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - Delivery Dockets, Pipe installation checksheet
checkpoint | 3.20 - Connection to Manhole
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - As per DWG2012034.114 As per DWG2001151.018
label | CONFORMANCE CRITERIA - 150mm concrete surround to 160dia uPvc
label | METHOD - Visual inspection
label | FREQUENCY/PROCESS HELD - During installation
label | TYPE - W
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - Pipe installation checksheet
checkpoint | CONFORMANCE / VERIFICATION STATEMENT
label | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete, and any non-conformances have been closed out in accordance with the Projects requirements.
label | Construction Lot checked by the Senior Project Engineer responsible for the works
textbox | Senior Project Engineer - PRINT NAME:
date | Senior Project Engineer - DATE:
label | Construction Lot verified and closed by Quality Management Representative
textbox | Quality Management Representative - PRINT NAME:
date | Quality Management Representative - DATE:
label | Independent Verification Review (if required) by:
textbox | PRINT NAME:
date | DATE:
holdpoint | ADD SIGNATURE