## Master List Templates
Id | Type | Name | Values | Prompting Name | Postfix
7e478553-8018-48e7-97a5-8b017bac9a29 | checklist | ITC001.0 Ductwork Roughin Rev1 | itp | ITC001.0 Ductwork Roughin
858499cd-8276-44f8-8fc1-9c5c9f417862 | section | Ductwork Rough In
1c6f5f8f-da16-4965-a6c0-667f61c9af5e | checkpoint | Layout correct to latest drawing
8e5e4703-5716-4291-af0a-60ff04379782 | checkpoint | Size correct
fba72cb8-1a02-427d-bd49-5c2937ed6217 | checkpoint | Duct Height correct
3edd2473-e8ef-4c86-86dd-930c8a6cadfb | checkpoint | Hanger spacing correct
d78181e6-5c50-46b5-913b-6a73df96020b | checkpoint | Seismic restraint as per seismic details
38811d60-6671-45e5-a5f2-d381ff17f409 | checkpoint | Clear to other services
3dd49126-44b0-4cf6-b6e2-37d092cb9a9b | checkpoint | Duct joints sealed / Flange tape/ Mastic / Cleats
983b2b4d-7307-4d7e-9258-7170acf901fb | checkpoint | Duct open ends sealed
de8360db-129e-4f8f-a1ac-939a471876d0 | checkpoint | Insulation: Internal / External / Nude
8c1a5f78-30cd-4488-8571-88817e091997 | checkpoint | Threaded rod ends trimmed
22a2b9df-4cae-446d-a115-e797c5f80ce9 | checkpoint | Exposed Duct labels removed from duct
2a1fdcab-c15c-4e20-b380-331e813d0113 | checkpoint | VCD installed, Manual or Motor Checked for free movement, Locked open
038b1813-a28b-4aeb-bd61-371f982e582b | checkpoint | NRD installed, Checked direction, Checked for free movement
3cdbeb57-91dc-483b-8b48-204ca023975a | checkpoint | Sign Off
ce74c59d-073b-597a-bdc1-d6c70e87e7ba | note | EQAC REPRESENTATIVE
d46b5ea2-108d-59cd-97d5-88f7ebf7a4bd | textbox | NAME
89f3e9a6-dd84-56cb-9738-46ab4bff2ba9 | textbox | POSITION
40cf1623-cc26-5814-9786-2c5c2f2debd3 | button | APPROVED (YES/NO) | Yes,No
09461ab5-7bb8-5aab-852f-978b14a81caa | date | DATE
e652f244-25a7-41a9-b27c-720042b8f3cc | signoff | SIGNATURE
66fcd819-7fe8-4f6e-8a2e-e4b3cc25eea2 | checklist | ITC003.0 Pipe & Duct Insulation Rev1 | itp | ITC003.0 Pipe & Duct Insulation
4b4f3fcf-6f7e-46b9-ba03-043803128fbd | section | Installation Inspection
3bd60c5a-9111-410a-83d6-1c59fe903f4d | checkpoint | Check insulation is installed as per latest drawing & revision
0e1da7af-c0bd-42c9-8072-e5bb55beaf4e | checkpoint | Check insulation is correct type and R value as per design
fdd82853-ea2a-447e-8c04-391b62d3fd1a | checkpoint | Check insulation is not damaged
03ac71bb-eb9e-4837-8829-9dd256691dab | checkpoint | Check mounting blocks ID & OD and bracketing correct
4e771140-124b-4c71-8d16-59241bfc76ae | checkpoint | Check bracketing is spaced correct
58cece79-468a-4675-93a2-8235e0d83edd | checkpoint | Confirm pipe/ duct pressure testing complete and approved
ae07180b-a6a5-401b-8240-f46b86247ec2 | checkpoint | Ensure insulation requirements for access and maintenance
e795e203-154a-4faf-8362-b3f28b306b5b | checkpoint | Check vapor barrier is continuous
5675e3ec-3dc8-4a27-af59-e5739457ecf0 | checkpoint | Check Insulation is continuous and sealed
ee1192d6-14f5-465d-930d-33a5e6c92006 | checkpoint | Check insulation is strapped is correct material and spaced at correct intervals
b6e6f809-2c24-4c94-ad45-1f3b580eec6d | checkpoint | Ensure all pipe fittings valves and ancillaries are insulated as per design.
6c089bcf-64c6-46a9-bb96-5f7f6173e1cb | checkpoint | Confirm areas of insulation requiring metal sheathing and type of material.
bf31b3fc-94ed-4b43-955a-11b1ecddf9ad | checkpoint | Ensure metal sheathing has been installed with moisture barrier and seam locks
89376df0-d591-46c3-a1cf-92c134706f2d | checkpoint | Ensure sheathing is fitted correctly for future access and maintenance.
b1c360a3-2bdb-48a5-a815-6b2e2f56cb59 | checkpoint | Sign Off
f3484b42-a8fd-56ec-bd53-a0a9fc927ad3 | note | EQAC REPRESENTATIVE
046c8bac-7e42-5468-a3f1-c12e91526fbb | textbox | NAME
48867589-254f-5a06-9fac-cf67bd426dcf | textbox | POSITION
3c072c20-a30c-535d-b53b-d2d99edb672e | date | DATE
710a463f-0e61-455e-ba42-1819ef7599b7 | signoff | SIGNATURE
30a9baa4-7bd8-4efd-a136-e12f9f08a5dd | checklist | ITC004.0 Pipework Pressure Test Rev1 | itp | ITC004.0 Pipework Pressure Test
04429061-38a9-4129-8edd-6104322e4a5b | section | Pipework Pressure Test
d3728a8a-81ae-470a-bc87-001db38ab699 | checkpoint-no-value | Details
e35076de-9865-5c70-9a11-c45fb0349c00 | note | Test Medium:
877aec12-da05-50c0-9e17-cf58a6f2006c | tickbox | Air
0aa927f5-5748-501e-a647-bbab7ed114a3 | tickbox | Water
e93ded5b-fbfb-5c36-9c4f-be8823b1f3cc | tickbox | Nitrogen
5155d753-16c7-5b49-a8a5-38d48b8f75a4 | textbox | Service:
67d7ade2-9069-51af-9ecb-df9f399594b3 | textbox | Device Used:
c04995dc-6a67-588c-846c-24b3deb1548b | textbox | Model number:
af9c79ff-c622-5ff0-8cb7-8e1a03baafea | textbox | Serial number:
2ae3180b-53b1-540c-b61b-1b6dda728c96 | button | Calibration Certificate attached: Y/N | Yes,No
3b62f22f-d9bf-5e2e-80bf-c39febdd088c | textbox | System working pressure: |  |  | kPa
d2249089-3f09-555e-b6cb-912c971b494e | textbox | Test Pressure 1.5 X working pressure: |  |  | kPa
ab565798-9be2-4657-85ec-056ee1dcc9b6 | checkpoint-no-value | Initial Sighting:
28e1b277-bb1b-5d3c-909c-899189c1568c | date | Date:
6ce3b257-8db1-5e03-9994-bd90aa38bc20 | textbox | Time:
3928c9f2-2752-5026-9599-a7cc4958acb6 | textbox | Pressure: |  |  | kPa
178a70ed-b662-4aa9-a263-773deccd7913 | checkpoint-no-value | Final Sighting:
a02a95c8-82ca-545c-950f-225db3920547 | date | Date:
fe678ea6-4cac-5eec-824b-f323b24ef733 | textbox | Time:
56192869-b7ba-5d44-b2bd-de32e0f7b7d2 | textbox | Pressure: |  |  | kPa
1fac4462-a372-4d0c-a4b0-f5479e9839b4 | checkpoint-no-value | Comments: Maximum test duration 120 min @ 1.5 X working pressure to a Max 2500kPa
6008094c-6c77-481c-b809-2852370ca63b | checkpoint | Sign Off
54aac2b0-ea67-5efe-bf02-7e9e108753e5 | note | EQAC REPRESENTATIVE
73a51c5f-96d9-551a-8632-d2ac2eaa8dab | textbox | NAME
ded869c3-2c26-540b-8062-f781792b2b5c | textbox | POSITION
1c7ff99e-8ebd-5bbc-b5f5-fb949a7950e7 | button | APPROVED (YES/NO) | Yes,No
841b1d59-d622-56cd-baca-a4c2411ab624 | date | DATE
833766b5-e8ce-442d-ae5d-51f7c6a09f79 | signoff | SIGNATURE
567f3315-5390-4220-b126-afb2560b449a | checklist | ITC006.0 Ductwork Fitout Rev1 | itp | ITC006.0 Ductwork Fitout
07da0261-d928-4f56-b2b4-7ff1090b06ee | section | Ductwork Fitout
95f0c853-3ad4-46fc-a005-63aeb7f75ccb | checkpoint | Layout as per latest drawing
8b7549ad-6cf2-418f-ab3a-8d2f7b538269 | checkpoint | Grilles installded as per latest RCP
2131aa6f-d9af-4083-99eb-d5225e812982 | checkpoint | Grilles & Cushion head box mounted correctly
a3719987-66f2-40dc-856c-f4c8b4bdff24 | checkpoint | Correct Grill installed
099c4554-0197-4e0e-83a4-c1383f6f5412 | checkpoint | Clear of other services
89e09368-30cf-475f-854f-f823e22332a9 | checkpoint | Flexi Duct installed as per AS4254.1
ae6ef036-2271-40fb-811c-3b8ab601473a | checkpoint | Flexi Duct installed and supported with min SAG (no more than 40mm with ±20mm tolerance over a meter
1a98b3a8-c39e-4613-934c-548efc93eb43 | checkpoint | Flexi duct supported with approved safddles at max 1.5m intervals
fd27a84c-ebc4-44d1-8958-4f65b85d9be1 | checkpoint | Flexi duct mechanical fixed; taped and sealed.
2d3481e7-23bf-4c78-aafb-9d8773fe850f | checkpoint | Sign Off
ac8d9567-ba24-568f-a8b7-e6f8c52c334f | note | EQAC REPRESENTATIVE
c84c494a-3275-54c4-8e11-9fcc7367667a | textbox | NAME
2d76537d-46af-5809-a41e-9d04f5a7659b | textbox | POSITION
b754f326-a190-5cfd-814c-9b82bccc9cd3 | button | APPROVED (YES/NO) | Yes,No
311d26ba-2bcc-5d44-a4d5-aa40dca12a5f | date | DATE
bafd608e-dfd3-4be6-8367-64f1e9d52ae5 | signoff | SIGNATURE
abe135ce-41ab-4585-ba94-0d75a61bb1c8 | checklist | ITC008.1 Fans Installation Rev1 | itp | ITC008.1 Fans Installation
79c9a063-806b-4b6e-a5e5-aee88e96eea0 | section | Installation Inspection
e5708a02-fa8c-4799-8903-1e485e499789 | checkpoint | Ensure fan matches schedule prior to installation.
a221ee1d-7408-4041-8f03-846d9c470319 | checkpoint | Ensure all shipping restraints, hold-down bolts, etc. are removed prior to installation.
086ef4ed-c426-4c36-97f0-8cc392ff9e8b | checkpoint | Ensure fan installed as per latest drawing & clearly labelled.
f2068a88-d65a-4e1e-b02f-dee0ee87f663 | checkpoint | Check airflow direction and orientation is correct.
85a50ed9-1c4a-4f25-9b57-6ba998db218e | checkpoint | Ensure vibration isolation mounts are installed correctly.
f5a3ce1c-6667-4766-91a7-fcbfa356e571 | checkpoint | Ensure seismic restraints are fitted where required
49714d05-65e5-4eac-bdc1-51b43c9df370 | checkpoint | Ensure fan blades rotate freely and are not obstructed or damaged.
0ba32f4d-e257-4b46-906e-5aafc7408b5a | checkpoint | Ensure filters are installed where required prior to energization
e0ad267e-75b3-483f-9769-9b104610c2b9 | checkpoint | Ensure all dampers fitted to system are open prior to energisation.
65a50771-4eb9-4a62-88f5-8af7b494a65d | checkpoint | Confirm electrical connection to the fan is secure.
5f39a931-d29b-4f79-a7c4-04ac8d5a2698 | checkpoint | Ensure lockable isolators installed and in the off position
665aa049-765d-43b2-91fa-5c24664b5a94 | checkpoint | Ensure fan and isolator are labeled correctly
4dc6f460-9042-41a3-a896-09a00cd3495d | checkpoint | Ensure circuit breaker is off and locked and or tagged
5cecbf31-39ab-4b0b-a27b-bcdfcaebfa0f | checkpoint-no-value | Fan ready for energisation:
7bdd4b72-05f4-5e73-a21a-35d2ef024622 | note | Continue to ITC N0: ITC012 Fan Start-up Checklist
565793f2-68e1-4c5c-9383-2ccfcba8d444 | checkpoint | Sign Off
500532d3-4761-50d2-97be-f8a4b94189fc | note | EQAC REPRESENTATIVE
134a9ea8-31d5-5555-adc0-6d027c070c72 | textbox | NAME
1a680f17-26e9-5ef0-a7f7-f06df410879d | textbox | POSITION
701619af-fe6b-5dc3-8649-7e3f48080e9f | date | DATE
8ec21b5e-d039-40f9-b524-771f988b5aca | signoff | SIGNATURE
dfb9f8e2-88a9-4fa3-92dc-2c2183ce9a85 | checklist | ITC008.3 AHUs and FCUs Install Rev1 | itp | ITC008.3 AHUs and FCUs Install
ddae252c-b550-4f25-a01d-1734cbd1f3b9 | section | Section A (General)
8e53f36c-a86c-4f79-a9f4-66bae5799eba | checkpoint | Unit Data is as per technical data schedule
130394f1-d051-4873-b828-6c77179f3c6f | checkpoint | Units are installed in correct location as per latest drawings
2c378c20-cbb6-427e-9aa8-23f0f96e09ad | checkpoint | Unit is clearly labelled
bf8b82c9-2f61-4a5b-ace6-2eec8ba9f712 | checkpoint | Unit is installed with approved vibration isolation
16060c86-e0be-4f0f-a3df-0a585a45ca35 | checkpoint | Flexible connection between unit supply and return air
fb943f9d-3ca1-4408-8c90-0309e52a86ef | checkpoint | Safety tray installed and sized to give maximum cover
59613b4f-71fe-4b74-823c-8afd8d090997 | section | Section B (Pipework)
40291563-646c-4e7b-9064-7048f960c642 | checkpoint | Pipework installation completed including valves & ancillaries as per drawing schematic with service valves open
70cdbe79-6ef9-49d5-b27d-22cd7897222d | checkpoint | Drain piping installed including trap
7f8acf3b-a76f-457a-9137-1cea4180e923 | checkpoint | Confirm drain has been tested.
20d80b4e-8908-4a9c-92bb-c351cc2caf1a | checkpoint | Confirm System pressure test completed as per ITC004
6c083f58-6982-454b-a2c8-69a6161d759d | checkpoint | Confirm Pipework Insulation Completed as per ITC003
b7ea8ec9-bf74-4211-8d26-c3c7f9c390e4 | section | Section C (Electrical)
2db6baed-4a96-4599-9660-0a8a98631703 | checkpoint | Check electrical cabling is secure and labeled.
ed01c7a3-9ba4-462d-944d-24859d7460e3 | checkpoint | Confirm all electrical connections, including Mains & Control as per the manufacturers wiring schematic
b2252198-6726-4228-9534-29a24493dde9 | checkpoint | Confirm unit is addressed as per manufactures schematic.
26ae1615-777c-4b00-a14d-a998664b8f2f | checkpoint | Check isolator is installed labeled and switched off.
9589c365-4d7a-45d0-8cc1-b4b3fe0bf7dd | checkpoint | Check circuit breaker in MSSB is switched off, locked out and or tagged.
97b1bf30-bbed-4bc8-a8c5-13324a292c7d | checkpoint | FCU is now ready for energisation.
ddadb26d-dc37-4855-8924-3a68e6727708 | checkpoint | Sign Off
c50aae24-618d-58fa-b303-ae68c805ef26 | note | EQAC REPRESENTATIVE
0f924fbf-0c88-5026-8036-864cc2317896 | textbox | NAME
a58ce9a7-c0e1-56a5-b611-7ef69b46ea49 | textbox | POSITION
a2e7304c-3f15-55bb-b07a-11c9f3088269 | date | DATE
291a575c-2cd3-4a11-aa96-9ca78d1ab965 | signoff | SIGNATURE
b99cdb9e-3d18-4598-9e95-cfbb7233fa5e | checklist | ITC008.3.1 Fan Coil Unit Drain Pipe Test Rev1 |  | ITC008.3.1 Fan Coil Unit Drain Pipe Test
75657b66-a4e7-4319-afa9-fcd9e92878a3 | section | Fan Coil Unit Drain Pipe Test
2dd4016d-7104-440f-8662-ad6b53a44b68 | checkpoint | Details
f51df0ef-7aaf-5573-b6b5-4363b42608c3 | textbox | Unit Tag
e5251a8d-8999-58f5-aa8b-599ec554b545 | textbox | Unit Model
a3dadbb0-c92a-52e3-896a-8914b5aa20a8 | button | Drain Test (Yes/No) | Yes,No
945b7a64-fb1c-49df-a529-8ea3054b0ab9 | checkpoint | Sign Off
74a47c81-059a-5263-9950-d82b36300de7 | note | EQAC REPRESENTATIVE
b6692d11-8c44-5b59-bc26-9af8418b5837 | textbox | NAME
672bbef3-fd64-5a96-972d-32811ed45d66 | textbox | POSITION
865db6be-ada7-5f2f-b74d-0e1ab165d074 | date | DATE
b17e1ed8-2108-49c1-b1ef-8ff2c196d616 | signoff | SIGNATURE
135f3abb-e3e4-44a3-b75d-5bebcecda6eb | checklist | ITC0010.0 Duct Pressure Leakage Test Rev1 |  | ITC0010.0 Duct Pressure Leakage Test
6ed275d5-429d-47c8-b99f-574aedb3a5fc | section | Ductwork Pressure Leakage Test
a835e45e-be8d-4c52-b52d-8e564ce92873 | checkpoint | PASS/FAIL
a0416761-55af-5a97-a4a8-4b77f57e3758 | textbox | System Design Static Pressure (Pa)
145e561a-5bbc-5c32-ae77-756aba352707 | textbox | Design airflow in section (L/s)
ef0b286d-aa04-570d-9018-f906d074b926 | textbox | Allowable Leakage (5% of tested section, L/s)
579e0a6f-fa46-53bb-b4ba-af45d71d4003 | textbox | Orifice Plate setting(mm)
8ee9e7ea-c4b0-5b58-a0a1-5b6c4cc41277 | textbox | Actual Test Pressure (Pa) |  |  | (min 1.25 x System Static Pressure)
f644805f-4c74-5891-83ce-ded53a37d4c1 | textbox | Pressure Drop (Pa)
9342625f-3b36-55d3-b14f-d3fc53c80b19 | textbox | Air flow leakage rate (L/s)
2f1323d3-b30b-4f13-a887-010ae0f53831 | checkpoint | Sign Off
d82b4fbc-af86-5f7c-9a40-96e6a4c5ab45 | note | EQAC REPRESENTATIVE
279c55c0-33c0-5a7f-bf81-8d73ee710639 | textbox | NAME
b9d82ff6-8306-52bc-9a97-55417ab32567 | textbox | POSITION
d38a4406-2298-5e0f-8871-d368d740f553 | date | DATE
68be243e-86a9-414b-b891-ef9311f3605d | signoff | SIGNATURE
885def5e-984c-458d-999d-9eb11830c4d9 | checklist | ITC0012.0 Fan Startup Checklist Rev1 | itp | ITC0012.0 Fan Startup Checklist
30ddecc8-e811-4be7-b00c-3f36699cf5eb | section | Fan Startup Checklist
b17e2ea8-e5f5-4110-82ad-f07bcee11194 | checkpoint | Signage and barricading in place prior to testing and start-up
458c0a81-bda3-4144-b539-cec14122101f | checkpoint | Confirm Isolator and circuit breaker are locked out. Power is available
ae628488-bc75-4083-977a-208d404aa841 | checkpoint | Check Fan location matched latest drawing
92ee2894-5231-4101-8d2f-54b449c122e0 | checkpoint | Check Fan ID matches schedule
c8e8ede1-dfb7-423f-b23b-670903473884 | checkpoint | Check Fan orientation/ directional arrows are is correct
61cabd68-8ab6-46f7-b2bd-4b27684c9aae | checkpoint | Belt guards fitted/ Access inspection panels fitted & locked in place
c98515c0-4be1-4bd0-9b10-0018a9bab1f8 | checkpoint | Ducting inspected and confirmed clear of debris and obstructions
51f353e4-deb9-41a5-adc7-04b38eeee759 | checkpoint | Sign Off
12640b54-64a7-5b3a-9f16-7aa381247728 | note | EQAC REPRESENTATIVE
612eb646-c317-5b61-ae60-5a5c8d3cb4cc | textbox | NAME
448e4d81-3ed2-56ed-8c0f-ac795c5022ca | textbox | POSITION
5838321a-bbea-5495-a917-70ae8d9f8846 | button | APPROVED (YES/NO) | Yes,No
002e8e31-4853-58bd-836f-4f74e899fa22 | date | DATE
84738970-2a76-420f-bbbf-900abd8ecf70 | signoff | SIGNATURE
056e0ae5-f3ff-420f-82c7-ed3bcb7f072f | checklist | ITC0013.0 Mechanical Services Switchboard Installation Rev1 | itp | ITC0013.0 Mechanical Services Switchboard Installation
3674fa35-3f60-4d51-a313-c3559524cbd3 | section | Acceptance Criteria
713598f4-1d88-484a-88de-685efc5432f6 | checkpoint | Ensure MSSB installed as per latest revision drawings
05536844-d0a1-4d84-a1c2-150495841fb6 | checkpoint | Ensure all labelling (internal & external) is correct and complete.
a6df38a0-80ae-4180-9b3a-432748d705ac | checkpoint | Ensure cabling is connected and secure (Steel ties for essential services)
0c48d3dc-7804-40ca-b32e-8f6e60ba9881 | checkpoint | Ensure cable protection/ covers installed, internal and external.
3d1b14e7-1c7d-429b-88c8-fe7bdc8b1487 | checkpoint | Ensure adequate access & clearances are provided around and in front of MSSB.
26fcd7cb-c2ef-43e5-9f0e-b65bcde8bd0d | checkpoint | Ensure main isolation switch and all individual circuit breakers/ switches are lockable & switched off
d3fbd28b-2c8e-4823-9d4f-df359a98c53e | checkpoint | Ensure doors are lockable.
ee4a0fd8-a47c-4d5c-9b20-122090cb3c27 | checkpoint | Ensure any live parts are not exposed or are suitably protected.
9ca3f810-15b4-4924-bce7-8d7a3f95c5fe | checkpoint | Ensure all loose items, swarf, etc. cleaned from MSSB prior to energisation.
aec284bc-0635-4979-8470-a232da0afcf3 | checkpoint | Confirm MSSB installation/ wiring contractor has completed all testing and test report is attached
0b010388-9d97-4fde-af03-fa09f50a3c75 | checkpoint | MSSB is now ready for energisation:
e4bc4433-029d-42b3-a9d7-8ae3c0edafb4 | checkpoint | Sign Off
c33f05c2-314f-5d63-a3da-a9fcf8c6c19a | note | EQAC REPRESENTATIVE
07de9255-6790-5539-93f9-c87c1d95433c | textbox | NAME
0a078605-f897-5016-a29d-6605d1380f59 | textbox | POSITION
bbe43fb4-7a46-553d-a1a8-1b1888ee5077 | date | DATE
ba7bd901-baef-4796-a7fa-62b6d92c35a1 | signoff | SIGNATURE
c814cb2d-580a-46ab-94d7-b9fc6409f981 | checklist | ITC0016.0 Pipework Install Rev1 | itp | ITC0016.0 Pipework Install
7b7c88aa-e74d-4989-9950-6ce7daa6743d | section | Item Inspected
70b3719e-98e1-4eaf-a9f9-58dc2e65cc31 | checkpoint | Layout correct per latest drawing
278322bc-ee3f-46ae-b029-6a1082d55d94 | checkpoint | Pipe Size correct
0dbb00f1-b882-4264-bc14-a8312a1036a2 | checkpoint | Pipe & Fitting Pressure rating Correct
939e3d27-90ab-4a64-a2a4-79830f6d545c | checkpoint | Hanger type and spacing correct
3018577b-63d1-43db-8ea9-cd285baf14bf | checkpoint | Seismic restraint req/ Installed
0ea7caca-4c8e-4676-b72f-791917752369 | checkpoint | Clear to other services
dad49a2e-7ff6-4851-b246-389cfe5a5f3d | checkpoint | All Valves and fittings installed as per design schematic
02fea3ed-51b3-4fe3-85da-a52e138f278e | checkpoint | Fire rating complete to approved system
40184755-dbb6-46ca-9156-2c3908e48bed | checkpoint | Pipe Insulation required
4346d01e-914f-4f0c-adc7-0f2ec226fb00 | checkpoint | Pipe label’s installed: Direction and Service
91857286-82ee-4991-8141-c9e888b7a979 | checkpoint | Riser piping ready for pressure testing
ed71fa46-dfe9-4e6b-b310-f6d0028ab91f | checkpoint | Sign Off
f887a72c-4211-5a4c-8e00-c9c33be51055 | note | EQAC REPRESENTATIVE
dc13e8d4-b503-5f3e-8b00-56cd9c4ec689 | textbox | NAME
aa24558c-cc7d-5be8-b5de-89cb2ac890c1 | textbox | POSITION
be1ff36c-1f2f-5e93-b9d6-dbfe84b47bd5 | date | DATE
e8b40af5-b142-48fb-97fd-ce4cf6035822 | signoff | SIGNATURE
7b4bcd50-d21c-4c60-9390-98843e4e081e | checklist | ITC0017 Flushing Test Sheet Rev1 | itp | ITC0017 Flushing Test Sheet
9ff4c957-1e5d-435e-a458-952e096b97f0 | section | Details of Test
2c74b487-9600-4c57-bbbd-14df5ef9b883 | checkpoint | Min Flushing Volume/ Velocity for pipe being flushed
41839c0c-9018-5c36-80b8-e9a6ddc8c2db | textbox | Value:
e7e523df-9fa0-473b-a688-c546d0e051ca | checkpoint | Mains water sample taken
ea33211e-abf9-52a5-9613-c4d173f14b99 | textbox | Value:
880f0458-667e-4291-9634-97c81af84e28 | checkpoint | System flushed and chemicals added.
fc0e5fb3-217d-5b33-a218-403860a2cb12 | textbox | Value:
712a4938-8fe8-4572-87d5-68fb2f0cb7ff | checkpoint | Volume/ Velocity achieved and flushing schematic marked up
e505c20d-5394-5bb0-bc84-f1980671a98c | textbox | Value:
c5fc4519-9cdb-45d5-800a-0f83e8a1953f | checkpoint | System Complete / full of water
d659d3af-08ab-54cc-9442-1c761346e8f2 | textbox | Value:
7d641129-464a-4cba-9abe-8df2c8c37348 | checkpoint | System or Section isolated
f8d85667-9349-5119-8686-60f8d3661d89 | textbox | Value:
437ac50c-0a1b-4fde-ae87-22da6cd374a3 | checkpoint | Sign Off
f2e1dd30-f0bd-5b75-8cca-2887f6894c45 | note | EQAC REPRESENTATIVE
011daf77-db60-5df0-b484-ac92ac4c9ea9 | textbox | NAME
98cc6c9c-b498-539e-aa57-7078f24b9600 | textbox | POSITION
68e8154f-fe75-50c4-b75b-e2c2d6073289 | date | DATE
eb051761-9e56-46d3-a5d8-a09b275d0ffe | signoff | SIGNATURE