## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | CITC-002.01 - Commissioning Data Sheet - AHU | itp |  |  |  |  | CITC-002.01 - Commissioning Data Sheet - AHU Rev1
section | Commissioning Data Sheet - AHU
checkpoint | Check panels are secure
checkpoint | Check for any internal damage
checkpoint | Check coil condition
checkpoint | Check shipping bolts have been removed
checkpoint | Check fan belt tension & pulley is aligned
checkpoint | Anti-vibration pads installed
checkpoint | Unit & isolator labelled correctly
checkpoint | Check pipe work is complete (unit, valves & drain etc)
checkpoint | Check pipework has been insulated
checkpoint | Check electrical is complete including isolator
checkpoint | Check filters have been installed
checkpoint-no-status | Supply voltage
textbox | Volts
checkpoint | Check all electrical connections are tight
checkpoint | Is the system earthed correctly?
checkpoint | Has fire trip been connected and tested?
checkpoint | Sufficient access to unit for maintenance
checkpoint | Check air pressure switch for correct operation
checkpoint | Check chilled water valve for correct operation
checkpoint-no-status | Cooling S/A temperature
textbox | Temperature |  |  | C
checkpoint | Check hot water valve for correct operation
checkpoint-no-status | Heating S/A temperature
textbox | Temperature |  |  | C
checkpoint | Check damper actuators have been installed & stroked correctly
checkpoint | Check damper actuators operate correctly for economy cycle/ smoke pressurisation
section | Fan Amps
checkpoint-no-status | Rated
textbox | Amps
checkpoint-no-status | Drawing
textbox | Amps
section | Settings
checkpoint-no-status | CHW balancing valve settings
textbox | Design flow rate
textbox | Flow rate
textbox | Valve turns
checkpoint-no-status | HHW balancing valve settings
textbox | Design flow rate
textbox | Flow rate
textbox | Valve turns
checkpoint-no-status | S/A Fan
textbox | Design flow rate
textbox | Flow rate
textbox | % or VSD Hz
checkpoint-no-status | R/A Fan
textbox | Design flow rate
textbox | Flow rate
textbox | % or VSD Hz
checkpoint-no-status | O/A Fan
textbox | Design flow rate
textbox | Flow rate
textbox | % or VSD Hz
section | Sign Off
checkpoint | Sign Off
label | SUB-CONTRACTOR REPRESENTATIVE
label | EQAC REPRESENTATIVE
label | BUILDER (IF REQUIRED)
label | QUALITY CHECK
label | Upload signature
checklist | CITC-004.01 - Commissioning Data Sheet - Fan | itp |  |  |  |  | CITC-004.01 - Commissioning Data Sheet - Fan Rev1
section | Commissioning Data Sheet - Fan
checkpoint | Check for any visible damage
checkpoint | Sufficient access to fan
checkpoint | Check airflow direction is correct
checkpoint | Anti-vibration pads installed
checkpoint | Unit labelled correctly
checkpoint | Check electrical is complete including isolator
checkpoint | Check filters have been installed
checkpoint-no-status | Supply voltage
textbox | Volts
checkpoint | Check all electrical connections are tight
checkpoint | Is the system earthed correctly
checkpoint | Check fan direction is correct
checkpoint | Check fan blades rotate freely
checkpoint | Has fan been fire tripped and tested
checkpoint | Has overload been set correctly
checkpoint | Check belt tension and pulley alignment is correct
checkpoint | Correct VSD parameters set as per motor spec
checkpoint | Motor kW RPM
checkpoint | Check all floor and branch dampers open
checkpoint | Fan free of vibration and excessive noise
checkpoint-no-status | Fan Data
textbox | Design flow rate
textbox | Actual flow rate
textbox | VSD Setting
section | Sign Off
checkpoint | Sign Off
label | SUB-CONTRACTOR REPRESENTATIVE
label | EQAC REPRESENTATIVE
label | BUILDER (IF REQUIRED)
label | QUALITY CHECK
label | Upload signature
checklist | CITC-005.01 - Commissioning Data Sheet - FCU | itp |  |  |  |  | CITC-005.01 - Commissioning Data Sheet - FCU Rev1
section | Commissioning Data Sheet - FCU
checkpoint | Check panels are secure
checkpoint | Check for any damage
checkpoint | Check coil condition
checkpoint | Check shipping bolts have been removed
checkpoint | Anti-vibration Pads Installed
checkpoint | Unit & isolator labelled correctly
checkpoint | Check pipe work is complete (unit, valves & drain etc)
checkpoint | Check pipework has been insulated
checkpoint | Check drain connected at both ends
checkpoint | Check electrical is complete including isolator
checkpoint | Check filters have been installed
checkpoint-no-status | Supply voltage
textbox | Volts
checkpoint | Check all electrical connections are tight
checkpoint | Is the system earthed correctly
checkpoint | Has fire trip been connected and tested
checkpoint | Sufficient access to unit
checkpoint | Check air pressure switch for correct operation
checkpoint | Check chill water valve for correct operation
checkpoint-no-status | Cooling S/A temperature
textbox | Temperature |  |  | C
checkpoint | Check hot water valve for correct operation
checkpoint-no-status | Heating S/A temperature
textbox | Temperature |  |  | C
checkpoint | Check damper actuators have been installed & stroked correctly
checkpoint | Check for vibration and excessive noise
checkpoint | RA Temp
checkpoint | Dampers and spigots open
checkpoint | EDH fail safes
section | Running Amps
checkpoint-no-status | Rated
textbox | Amps
label | Motor kW and RPM
checkpoint-no-status | Drawing
textbox | Amps
label | Motor kW and RPM
section | Settings
checkpoint-no-status | CHW balancing valve settings
textbox | Design flow rate
textbox | Flow rate
textbox | Valve turns
checkpoint-no-status | HHW balancing valve settings
textbox | Design flow rate
textbox | Flow rate
textbox | Valve turns
checkpoint-no-status | S/A Fan
textbox | Design flow rate
textbox | Flow rate
textbox | % or VSD Hz
checkpoint-no-status | R/A Fan
textbox | Design flow rate
textbox | Flow rate
textbox | % or VSD Hz
checkpoint-no-status | O/A Fan
textbox | Design flow rate
textbox | Flow rate
textbox | % or VSD Hz
checkpoint-no-status | Fan Belt Size & Type
textbox | Size & Type
checkpoint-no-status | Filter Size
textbox | Size
section | Sign Off
checkpoint | Sign Off
label | SUB-CONTRACTOR REPRESENTATIVE
label | EQAC REPRESENTATIVE
label | BUILDER (IF REQUIRED)
label | QUALITY CHECK
label | Upload signature
checklist | ITC001.0 Ductwork Roughin | itp |  |  |  |  | ITC001.0 Ductwork Roughin Rev1
section | Ductwork Rough In
checkpoint | Layout correct to latest drawing
checkpoint | Size correct
checkpoint | Duct Height correct
checkpoint | Hanger spacing correct
checkpoint | Seismic restraint as per seismic details
checkpoint | Clear to other services
checkpoint | Duct joints sealed / Flange tape/ Mastic / Cleats
checkpoint | Duct open ends sealed
checkpoint | Insulation: Internal / External / Nude
checkpoint | Threaded rod ends trimmed
checkpoint | Exposed Duct labels removed from duct
checkpoint | VCD installed, Manual or Motor Checked for free movement, Locked open
checkpoint | NRD installed, Checked direction, Checked for free movement
checkpoint | EQAC Representative Sign Off
note | Upload signature
checklist | ITC003.0 Pipe & Duct Insulation | itp |  |  |  |  | ITC003.0 Pipe & Duct Insulation Rev1
section | Installation Inspection
checkpoint | Check insulation is installed as per latest drawing & revision
checkpoint | Check insulation is correct type and R value as per design
checkpoint | Check insulation is not damaged
checkpoint | Check mounting blocks ID & OD and bracketing correct
checkpoint | Check bracketing is spaced correct
checkpoint | Confirm pipe/ duct pressure testing complete and approved
checkpoint | Ensure insulation requirements for access and maintenance
checkpoint | Check vapor barrier is continuous
checkpoint | Check Insulation is continuous and sealed
checkpoint | Check insulation is strapped is correct material and spaced at correct intervals
checkpoint | Ensure all pipe fittings valves and ancillaries are insulated as per design.
checkpoint | Confirm areas of insulation requiring metal sheathing and type of material.
checkpoint | Ensure metal sheathing has been installed with moisture barrier and seam locks
checkpoint | Ensure sheathing is fitted correctly for future access and maintenance.
checkpoint | EQAC Representative Sign Off
note | Upload signature
checklist | ITC004.0 Pipework Pressure Test | itp |  |  |  |  | ITC004.0 Pipework Pressure Test Rev1
section | Pipework Pressure Test
checkpoint-no-status | Details
note | Test Medium:
tickbox | Air
tickbox | Water
tickbox | Nitrogen
textbox | Service:
textbox | Device Used:
textbox | Model number:
textbox | Serial number:
button | Calibration Certificate attached: Y/N | Yes,No
textbox | System working pressure:
textbox | Test Pressure 1.5 X working pressure:
checkpoint-no-status | Initial Sighting:
date | Date:
textbox | Time:
textbox | Pressure:
checkpoint-no-status | Final Sighting:
date | Date:
textbox | Time:
textbox | Pressure:
checkpoint-no-status | Comments: Maximum test duration 120 min @ 1.5 X working pressure to a Max 2500kPa
checkpoint | EQAC Representative Sign Off
note | Upload signature
checklist | ITC006.0 Ductwork Fitout | itp |  |  |  |  | ITC006.0 Ductwork Fitout Rev1
section | Ductwork Fitout
checkpoint | Layout as per latest drawing
checkpoint | Grilles installded as per latest RCP
checkpoint | Grilles & Cushion head box mounted correctly
checkpoint | Correct Grill installed
checkpoint | Clear of other services
checkpoint | Flexi Duct installed as per AS4254.1
checkpoint | Flexi Duct installed and supported with min SAG (no more than 40mm with ±20mm tolerance over a meter
checkpoint | Flexi duct supported with approved safddles at max 1.5m intervals
checkpoint | Flexi duct mechanical fixed; taped and sealed.
checkpoint | EQAC Representative Sign Off
note | Upload signature
checklist | ITC008.1 Fans Installation | itp |  |  |  |  | ITC008.1 Fans Installation Rev1
section | Installation Inspection
checkpoint | Ensure fan matches schedule prior to installation.
checkpoint | Ensure all shipping restraints, hold-down bolts, etc. are removed prior to installation.
checkpoint | Ensure fan installed as per latest drawing & clearly labelled.
checkpoint | Check airflow direction and orientation is correct.
checkpoint | Ensure vibration isolation mounts are installed correctly.
checkpoint | Ensure seismic restraints are fitted where required
checkpoint | Ensure fan blades rotate freely and are not obstructed or damaged.
checkpoint | Ensure filters are installed where required prior to energization
checkpoint | Ensure all dampers fitted to system are open prior to energisation.
checkpoint | Confirm electrical connection to the fan is secure.
checkpoint | Ensure lockable isolators installed and in the off position
checkpoint | Ensure fan and isolator are labeled correctly
checkpoint | Ensure circuit breaker is off and locked and or tagged
checkpoint-no-status | Fan ready for energisation:
note | Continue to ITC N0: ITC012 Fan Start-up Checklist
checkpoint | EQAC Representative Sign Off
note | Upload signature
checklist | ITC008.3 AHUs and FCUs Install | itp |  |  |  |  | ITC008.3 AHUs and FCUs Install Rev1
section | Section A (General)
checkpoint | Unit Data is as per technical data schedule
checkpoint | Units are installed in correct location as per latest drawings
checkpoint | Unit is clearly labelled
checkpoint | Unit is installed with approved vibration isolation
checkpoint | Flexible connection between unit supply and return air
checkpoint | Safety tray installed and sized to give maximum cover
section | Section B (Pipework)
checkpoint | Pipework installation completed including valves & ancillaries as per drawing schematic with service valves open
checkpoint | Drain piping installed including trap
checkpoint | Confirm drain has been tested.
checkpoint | Confirm System pressure test completed as per ITC004
checkpoint | Confirm Pipework Insulation Completed as per ITC003
section | Section C (Electrical)
checkpoint | Check electrical cabling is secure and labeled.
checkpoint | Confirm all electrical connections, including Mains & Control as per the manufacturers wiring schematic
checkpoint | Confirm unit is addressed as per manufactures schematic.
checkpoint | Check isolator is installed labeled and switched off.
checkpoint | Check circuit breaker in MSSB is switched off, locked out and or tagged.
checkpoint | FCU is now ready for energisation.
checkpoint | EQAC Representative Sign Off
note | Upload signature
checklist | ITC008.3.1 Fan Coil Unit Drain Pipe Test | itp |  |  |  |  | ITC008.3.1 Fan Coil Unit Drain Pipe Test Rev1
section | Fan Coil Unit Drain Pipe Test
checkpoint | Details
textbox | Unit Tag
textbox | Unit Model
button | Drain Test (Yes/No) | Yes,No
checkpoint | EQAC Representative Sign Off
note | Upload signature
checklist | ITC0010.0 Duct Pressure Leakage Test | itp |  |  |  |  | ITC0010.0 Duct Pressure Leakage Test Rev1
section | Ductwork Pressure Leakage Test
checkpoint-no-status | Details
textbox | System Design Static Pressure (Pa)
textbox | Design airflow in section (L/s)
textbox | Allowable Leakage (5% of tested section, L/s)
textbox | Orifice Plate setting(mm)
textbox | Actual Test Pressure (Pa)
textbox | Pressure Drop (Pa)
textbox | Air flow leakage rate (L/s)
checkpoint | EQAC Representative Sign Off
checkpoint | PASS/FAIL
note | Upload signature
checklist | ITC0012.0 Fan Startup Checklist | itp |  |  |  |  | ITC0012.0 Fan Startup Checklist Rev1
section | Fan Startup Checklist
checkpoint | Signage and barricading in place prior to testing and start-up
checkpoint | Confirm Isolator and circuit breaker are locked out. Power is available
checkpoint | Check Fan location matched latest drawing
checkpoint | Check Fan ID matches schedule
checkpoint | Check Fan orientation/ directional arrows are is correct
checkpoint | Belt guards fitted/ Access inspection panels fitted & locked in place
checkpoint | Ducting inspected and confirmed clear of debris and obstructions
checkpoint | EQAC Representative Sign Off
note | Upload signature
checklist | ITC0013.0 Mechanical Services Switchboard Installation | itp |  |  |  |  | ITC0013.0 Mechanical Services Switchboard Installation Rev1
section | Acceptance Criteria
checkpoint | Ensure MSSB installed as per latest revision drawings
checkpoint | Ensure all labelling (internal & external) is correct and complete.
checkpoint | Ensure cabling is connected and secure (Steel ties for essential services)
checkpoint | Ensure cable protection/ covers installed, internal and external.
checkpoint | Ensure adequate access & clearances are provided around and in front of MSSB.
checkpoint | Ensure main isolation switch and all individual circuit breakers/ switches are lockable & switched off
checkpoint | Ensure doors are lockable.
checkpoint | Ensure any live parts are not exposed or are suitably protected.
checkpoint | Ensure all loose items, swarf, etc. cleaned from MSSB prior to energisation.
checkpoint | Confirm MSSB installation/ wiring contractor has completed all testing and test report is attached
checkpoint | MSSB is now ready for energisation:
checkpoint | EQAC Representative Sign Off
note | Upload signature
checklist | ITC0016.0 Pipework Install | itp |  |  |  |  | ITC0016.0 Pipework Install Rev1
section | Item Inspected
checkpoint | Layout correct per latest drawing
checkpoint | Pipe Size correct
checkpoint | Pipe & Fitting Pressure rating Correct
checkpoint | Hanger type and spacing correct
checkpoint | Seismic restraint req/ Installed
checkpoint | Clear to other services
checkpoint | All Valves and fittings installed as per design schematic
checkpoint | Fire rating complete to approved system
checkpoint | Pipe Insulation required
checkpoint | Pipe label’s installed: Direction and Service
checkpoint | Riser piping ready for pressure testing
checkpoint | EQAC Representative Sign Off
note | Upload signature
checklist | ITC0017 Flushing Test Sheet | itp |  |  |  |  | ITC0017 Flushing Test Sheet Rev1
section | Details of Test
checkpoint | Min Flushing Volume/ Velocity for pipe being flushed
textbox | Value:
checkpoint | Mains water sample taken
textbox | Value:
checkpoint | System flushed and chemicals added.
textbox | Value:
checkpoint | Volume/ Velocity achieved and flushing schematic marked up
textbox | Value:
checkpoint | System Complete / full of water
textbox | Value:
checkpoint | System or Section isolated
textbox | Value:
checkpoint | EQAC Representative Sign Off
note | Upload signature