## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITR No.06 In Slab Conduits
section | Details
checkpoint | Determine origin and destination
checkpoint | Mark out positions of junction boxes and penerations when necessary
checkpoint | Install locating flange/conduit boxes
checkpoint | Install tie down straps on conduit boxes
checkpoint | Tie conduits securely at all joints and midpoints
checkpoint | Observe conduits when concrete is being poured
checklist | ITR No.01 Installation of Temporary Power Board
section | Details
checkpoint | Area accessible & ready
checkpoint | Locate & fix into position, bolt temporary board down with at least 2 fixings
checkpoint | Install submains cabling as appropriate eg: glands/tray/duct
checkpoint | Install lugs and terminate
checkpoint | Any cables not terminated prior to energisation must be removed from cubicle at origin and have ends covered in heat shrink. At destination cables must be covered in heat shrink and be contrained in a junction box
checkpoint | Clearly identify services
checkpoint | When ready to energise proceed in accordance with energisation procedure
checkpoint | Energise & record results on Vast RCD test sheet
checkpoint | Install laminated sign on face of temp board with floor plan and where the board is fed from
checkpoint | Update Temporary Power Board register & save to project folder/design control/temp const.
label | Lodge non prescribed certificate of electrical safety
label | RCBO'S must be fully tested initially and then tested every month with results recorded and c/b’s labelled
checklist | ITP No.02 Construction Wiring, Installation, Test and Tag & Removal
section | Details
checkpoint | Area accessible & ready
checkpoint | Refer to temporary wiring setout plan
label | CABLING MUST BE SUPPORTED AND PROTECTED FROM DAMAGE. CONSTRUCTION WIRING TAPE MUST BE FITTED AT EVERY 5 METRES. TEMPORARY WIRING MUST NOT BE INSTALLED WITH PERMANENT CABLING
checkpoint | Fit off plug base and or powerpoint/isolator
checkpoint | Install light fitting, exit/emg, power
checkpoint | Terminate cable to temp board. Ensure temp board is isolated! Test Test Test
checkpoint | Test & commission
label | Lodge non prescribed certificate of electrical safety
checklist | ITR No.07 Rough in Common areas
section | Details
checkpoint | Area clear, tidy and accessible
checkpoint | Rough in of all lighting circuits- inc Emg/Exits and sensors
checkpoint | Rough in of all power circuits Fed from demolition Zone
checkpoint | Rough in all lighting feeds and label on plan
checkpoint | Rough in dynalite cabling on dedicated cat wire/donut
checkpoint | Rough in all power feeds and label on plan
checkpoint | Check for clashes with other services
checkpoint | Level fire caulked by contractor
checkpoint | Ensure area is left clean
checklist | ITR No.10 Hallway Rough In
section | Details
checkpoint | Area clear, tidy and accessible
checkpoint | Mark out all public L+P in hallway
checkpoint | Rough in lighting, Emg/Exits and sensors
checkpoint | Rough in general power and cleaners power
checkpoint | Rough in comms/zigbee
checkpoint | Rough in comms riser power
checkpoint | Rough in dynalite cabling on dedicated cat wire/donut
checkpoint | Rough in all apartment sub mains from riser to apartment DBs and LABEL
checkpoint | Rough in any relevant comms/access control from one floor to another ( Backbone )
checkpoint | Check for clashes with other services
checkpoint | Level fire caulked by contractor
checkpoint | Fit off plug bases & quick connects
checkpoint | Ensure area is left clean
checklist | ITR No.11 Cable Tray Installation
section | Details
checkpoint | CO-ORDINATE WITH OTHER SERVICES (CHECK FOR ANY CLASHES)
checkpoint | CONFIRM SIZE OF CABLE TRAY
checkpoint | INSTALL FIXINGS AND SUPPORTS AS NEEDED
checkpoint | INSTALL CABLE TRAY
checkpoint | COMPLETE SKETCH/MARK UP DRAWING FOR FUTURE AS BUILTS
checklist | ITR No.20 Mains and Sub Mains
section | Details
checkpoint | Measure cable runs with appropriate accurate measuring instrument eg: tape measure, wheel, rope in conduit
checkpoint | Confirm length of cable
checkpoint | Install cable in applicable method eg: cable stands, electric winch, pulleys etc
label | Any cable not terminated immediately must have the end taped covering the bare copper
checkpoint | Trefoil (refer to details on back for all options) cables and tie cables to support system
checkpoint | Check cable requirements for cable identification and install
checklist | ITP No.30 Structured Cabling Rough In
section | Details
checkpoint-no-status | REFER APPROVED DRAWINGS AND SPECIFICATION.
checkpoint | INSTALL CABLE SUPPORT OR CONDUIT WHERE REQUIRED.
checkpoint | VERIFY CORRECT CABLE TYPE.
checkpoint | REFER TO APPROVED DRAWINGS FOR CABLE NUMBERING SEQUENCE RELEVANT TO FINAL FIT OFF SEQUENCE & RECORD
checkpoint | INSTALL CABLE WITHIN OR ON CABLE SUPPORT SYSTEMS MAINTAINING MIN SEGREGATIONS, ENSURE VELCRO CABLE TIES ARE USED AS PER SPECIFICATION
checkpoint | FORM CABLES INTO RELEVANT FIT-OFF GROUPS AT THE CABINET END.
checkpoint | ENSURE AREA IS LEFT CLEAN
checklist | ITR No.09 Apartment Rough In of Electrical Services
section | Details
checkpoint | Area clear, tidy and accessible
checkpoint | Rough in Hard Actives to all switches
checkpoint | Rough in of Switched Actives from switches to lights & Fit off Quick connects whilst on ladder
checkpoint | Rough in GPOs
checkpoint | Rough in of all kitchen general power (including island bench) above bench, fridge, microwave, rangehood
checkpoint | Rough in Cooktop and timer
checkpoint | Rough in kitchen led strip/figure8 from AP to swb
checkpoint | Rough in all internal lights and pull through noggins
checkpoint | Rough in bathroom pod to AP
checkpoint | Rough in Tstat
checkpoint | Rough in data points to LBNCO hub and TV
label | Ensure Sub Mains are at Switchboard Location
checkpoint | Install switchboard & fit off
checkpoint | Install 150mm stud protecting sub main and earth with nut & bolt
checkpoint | Install 2.5mm earth tags
checkpoint | Fire caulk sub main into DB and all cable entries
checkpoint | Ensure all Quick Connects and juntions boxes are fit off
checkpoint | Ensure all cables are neat, taped to studs and easily accessible for cut out
checkpoint | Ensure all cables are clearly labelled at DB and at party walls
checkpoint | Ensure area is left clean
checklist | ITR No.14 Apartment Cut Out
section | Details
checkpoint | Refer to drawing to determine cable support route and check separation from data/comms services
checkpoint | Cut out for light fittings
checkpoint | Cut out kitchen to kitchen plan
checkpoint | Cut out switches & GPO’s
checkpoint | Ensure Wall light is in correct position
checkpoint | Ensure kitchen outlets are in correct position
checkpoint | Install Fire Boxes and hit all 4 tabs in
checkpoint | Ensure Fire caulking is completed by subcontractor
checkpoint | Ensure area is left clean
checklist | ITR No.13 Hallway Cut Out
section | Details
checkpoint | Confirm sizes of all fittings prior to cut out
checkpoint | Cut out all sensors,emg/exits, light fittings
checkpoint | Cut out all cleaners gpos
checkpoint | Cut out any CCTV
checkpoint | Ensure electric strike cable is in press metal frame cut out
checkpoint | Locate all cables
checkpoint | Install Fire Boxes and hit all 4 tabs in
checkpoint | Ensure area is left clean
checklist | ITR No.13 Common Areas Cut Out
section | Details
checkpoint | Confirm sizes of all fittings prior to cut out
checkpoint | Cut out all sensors,emg/exits, light fittings
checkpoint | Cut out all cleaners gpos
checkpoint | Cut out any CCTV
checkpoint | Ensure electric strike cable is in press metal frame cut out
checkpoint | Locate all cables
checkpoint | Install Fire Boxes and hit all 4 tabs in
checkpoint | Ensure area is left clean
checklist | ITR No.15 Basement Light & Power Fit Off
section | Bakelite and Power
checkpoint | CHECK DRAWINGS FOR QUANTITY, BRAND TYPE AND COLOUR
checkpoint | LOCATION/COMPLIANCE WET AREAS, HAZARDS ETC. MOUNTING HEIGHTS,
checkpoint | FIT OFF AND FIX SWITCHES, WHERE MULTI GANG SWITCHES WITH MULTI CIRCUITS ARE INVOLVED USE SHROUDS ON EACH SWITCH. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
checkpoint | FIT OFF AND FIX GPO’S, WHERE A GPO IS LOCATED WITHIN 150mm OF A METAL STUD, USE SHROUD. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
checkpoint | FIT OFF FINAL APPLIANCES
checkpoint | COVER PLATES (IF REQUIRED)
checkpoint | INSTALL LABEL (IF A SPECIFIED REQUIREMENT)
section | Light Fittings
checkpoint | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
checkpoint | LOCATIONS CO ORDINATE WITH OTHER SERVICES
checkpoint | MARKING OUT IF REQUIRED - REFER TO REFLECTED CEILING PLAN FOR SET OUT
checkpoint | PLUG IN OR FIT OFF LIGHT / PLUG BASE
checkpoint | INSTALL LIGHT FITTING
checkpoint | INSTALL LAMPS AND DIFFUSER
checkpoint | CLEAN FITTING, LAMP DIFFUSER
checklist | ITR No.16 Bakelite & Power Fit Off
section | Details
checkpoint | CHECK DRAWINGS FOR QUANTITY, BRAND TYPE AND COLOUR
checkpoint | LOCATION/COMPLIANCE WET AREAS, HAZARDS ETC. MOUNTING HEIGHTS,
checkpoint | FIT OFF AND FIX SWITCHES, WHERE MULTI GANG SWITCHES WITH MULTI CIRCUITS ARE INVOLVED USE SHROUDS ON EACH SWITCH. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
checkpoint | FITOFF DYNALITE AS PER SPECS WITH CORRECT LABELING/QR CODE ON PLANS
checkpoint | FIT OFF AND FIX GPO’S, WHERE A GPO IS LOCATED WITHIN 150mm OF A METAL STUD, USE SHROUD. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
checkpoint | FIT OFF FINAL APPLIANCES
checkpoint | COVER PLATES (IF REQUIRED)
checkpoint | INSTALL LABEL (IF A SPECIFIED REQUIREMENT)
checklist | ITR No.18 Hallway - Fit Off Electrical
section | Details
checkpoint | Area clear, tidy and accessible
checkpoint | Fit off all Lights
checkpoint | Fit off all Sensors and SET TIME TO MINIMUM
checkpoint | Fit off all EX/EMG’s
checkpoint | Label all EX/EMG’s as per plan number
checkpoint | Fit off all Cleaners GPOs
checkpoint | Fit off all Comms Riser GPOs
checkpoint | Fit off water meter GPOs
checkpoint | Ensure area is left clean
checklist | ITR No.19 Apartment - Electrical Fit Off
section | Details
checkpoint | Area clear, tidy and accessible
checkpoint | Fit Off Wall Lights
checkpoint | Fit off joinery GPO's & install cover plates.
checkpoint | Fit off all GPOs - Install cover plates & switches where required
checkpoint | Fit off light switches
checkpoint | Fit Off Data Points
checkpoint | Fit off Tstat
checkpoint | Fit Off Kitchen LED Strip
checkpoint | Fire caulk sub main into DB and all cable entries
checkpoint | Install and fitoff DB
checkpoint | Install Cooktop
checkpoint | Ensure area is left clean
checklist | ITR No.25 Commissioning
section | Details
checkpoint | Prior to energising all personnel involved to be inducted into energisation procedure and all steps undertaken to ensure compliance with this procedure
label | Obtain fresh copies of current light and power drawings and mark up any changes from the working drawings
label | Obtain copy of distribution board schedule to mark up any additions or deletions found whilst commissioning
label | Visually Check all items
checkpoint | Dead Testing
checkpoint | Live Test
text | Record Metrel Results and log
checkpoint | Check operation of all sensors (individually on minimum time setting )
checkpoint | Check sensors are set to specified time and lux
checkpoint | Fit Cover Plates to GPOs & Switches (take photos)
checkpoint | Install switchboard cover / label (take photos)
checkpoint | Ensure area is left clean
checklist | ITR No.29 Decommission Temporary Power Board
section | Details
checkpoint | Determine what the temporary board is controlling and confirm what action is required before board can be decommissioned.
label | De-commission form issued to builder, 48 hours notice to be given
checkpoint | Sign off builders checklist
checkpoint | Safety Committee Inspection
checkpoint | Final approval to be given by builder
checkpoint | Perform voltage test to ensure power supply has been isolated
checkpoint | Disconnect supply cables
checkpoint | Fire sealing of penetrations
checkpoint | Remove temporary board
checkpoint | Update temporary power board register