## Insitu Concrete
|  |  |  | Inpesction Test Plan |  | FHIMS-QA-6006 | Approved |  | Signature
|  |  |  | Contract Name: | Richmond South Low-Level Reservoir |  | FH Engineer
|  |  |  | Procedure: | Insitu Concrete |  | FH Quality Manager
Inspection & Test Plan / Checklist
Lot No: |  |  |  | Corresponding Work Instruction: |  | (insert contract suffix here)-CS-7006 |  | Compliance with Work Instructions and Specifications
Detailed Location:
Chainage:
No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | FH Initials | Design Engineer Initials (Grey if not required) | Date(s)
1 | Permits | H | Obtain Permits | As required | Document Review | Control Checklist - Fall Prevention (if applicable). Notify Worksafe NZ if required. Ensure all necessary Permit to Works & Controlled Checklists are in place | Permit attached or permit number noted | Site Engineer
3 | Design | H | Ensure that Design is approved and Drawings are of the latest revision | Prior to commencement | Document Review |  | Check Drawing Register | Site Engineer
4 | Survey Setout | H | Set out design features as per Issued For Construction drawings (Cast in items, Ducting, Penetrations) | Prior to commencement | Survey | Consistency with Construction Drawing | Survey receipt | Site Engineer
5 | Material Compliance (1) | H | Concrete mix design(s) shall be submitted to the Design Engineer in writing at least 2 weeks prior to placing concrete and approved before | Prior to commencement | Document review | Engineer approval | Design Engineer Approval | Site Engineer | Design Engineer
5 | Material Compliance (2) | H | All concrete delivered to site shall be produced strictly in accordance with the approved mix design | Prior to pouring concrete | Concrete Delivery Dockets |  | Concrete Delivery Dockets | Site Engineer
5 | Material Compliance (3) | H | Steel Reinforcement shall comply with AS/NZS 4671 & NZS3109 and shall be the grade called up on the drawings | Prior to ordering steel | Document review | AS/NZS4671&NZS3109 | Detail Sheets and Mill Certificates | Site Engineer
5 | Material Compliance (4) | H | Any welding or mechanical splicing to be approved in writing by the Design Engineer | Prior to welding or splicing | Document review |  | Mark Up As Built Drawings | Site Engineer | Design Engineer
5 | Material Compliance (5) | H | Any reinforcement requiring cutting or bending on site to be approved in writing by the Design Engineer | Prior to cutting or bending on site | Document review |  | Mark Up As Built Drawings | Site Engineer | Design Engineer
6 | Foundation Acceptance by Engineer's Rep | H | Approval given by engineer's Rep and Signed off Subgrade Approval Checksheet | Prior to commencement | Inspection by Engineer | Inspection and Acceptance of Structure Foundations | FHIMS - CS-4100 | Site Engineer | Design Engineer
7 | Blinding Concrete | H | Once blinding concrete layer has been completed the Engineer's Rep to inspect and give approval for the rest of the works to commence | Prior to commencement | Inspection by Engineer | Engineer approval | Sign off this document | Site Engineer | Design Engineer
8 | Temporary Works (Formwork) (1) | W | Formwork to be constructed to design and set to correct line and level as set out by the surveyor | Daily Visual Inspection | Visual inspection | Concrete Inspection Record | FHIMS-CS-4008 | Site Engineer
8 | Temporary Works (Formwork) (2) | H | The Site Engineer and MSQA Engineer must sign off the formwork prior to concrete being poured | Prior to concrete pour | Visual inspection | Concrete Inspection Record | FHIMS-CS-4008 | Site Engineer | Design Engineer
9 | Reinforcing (1) | W | Reinforcing steel shall be handled, placed and fixed as per NZS 3109 | Daily Visual Inspection | Document review | Concrete Inspection Record | FHIMS-CS-4008 | Site Engineer
9 | Reinforcing (2) | H | Check for any cast in items and ensure they are fixed correctly | Prior to concrete pour | Visual inspection | Concrete Inspection Record | FHIMS-CS-4008 | Site Engineer
10 | Concrete Pumping Operations | W | Ensure the Permit to Concrete Pump Checksheet has been completed before concrete pumping commences | Prior to commencement | Document review | Permit to Pump Checkseet | FHIMS-CS-4029 | Site Engineer
11 | Concreting (1) | H | The MSQA Engineer shall be advised at least 48 working hours before the proposed time for concreting that a pre-pour inspection is required | Prior to concrete pour | Visual inspection |  | FHIMS-CS-4008 | Site Engineer | Design Engineer
11 | Concreting (2) | H | Concrete dockets checked for correct mix and concrete site testing undertaken i.e. Slump test | Prior to concrete pour | Test Results | NZS 3112, Concrete Inspection Record | FHIMS-CS-4090 | Site Engineer
11 | Concreting (3) | H | Concrete surface finishes shall be Concealed Form Surfaces: F1 Exposed Formed Surfaces: F4 Exposed Uniformed Surfaces: U2 Concealed Uniformed Surfaces: U1 | At completion of pour | Visual inspection | Concrete Inspection Record | FHIMS-CS-4008 | Site Engineer
12 | Remove formwork | W | Remove formwork as per the approved work method | At completion of pour | Visual inspection | Concrete Inspection Record | FHIMS-CS-4008 | Site Engineer
13 | As-builts | H | Red pen mark up drawings to be included in QA file | At the completion of the Lot of work | Drawings | Ensure all Asbuilts uploaded into CONQA | Asbuilt Drawing | Site Engineer
14 | Lot Number QA File | W | Ensure all OFIs are closed and included within QA file, Delivery Dockets and Lab Testing Spreadsheet and Test Reports to be included in QA File | At completion of Lot | Document Review | Ensure all QA is uploaded into CONQA | Delivery Dockets, Test Reports, Lab Testing Register | Site Engineer
Comments:
IFC Drawings used for Construction incl. Rev numbers:
Reference Documentation (Notices/OFIs etc.):
QA Compiled By : |  |  |  |  | Signature: |  |  | Date:
QA checked By Discipline Manager: |  |  |  |  | Signature: |  |  | Date:
QA checked By Quality Manager: |  |  |  |  | Signature: |  |  | Date:
Accepted By Design Engineer: |  |  |  |  | Signature: |  |  | Date: