## Network Drainage
|  |  |  | Inpesction Test Plan |  | FHIMS-QA-6007 | Approved |  | Signature
|  |  |  | Contract Name: | Richmond South Low-Level Reservoir |  | FH Engineer
|  |  |  | Procedure: | Drainage Installation |  | FH Quality Manager
Inspection & Test Plan / Checklist
Lot No: |  |  |  | Corresponding Work Instruction: |  | (insert contract name suffix)-CS-7007 |  | Compliance with Work Instructions and Specifications
Detailed Location:
Chainage:
No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | FH Initials | Design Engineer Initials (Grey if not required) | Date(s)
1 | Permits | H | Obtain Permits | As required | Document Review | Digging & Excavation Permit, (incl. marking out & potholing existing services), Confined Space Permit if rquired. Notify Worksafe NZ if required. | Permit attached or permit number noted | Site Engineer
2 | Pre-construction sign offs | H | Ensure that Sub-Contract and Supplier Agreements are signed, TMP is approved all Sub-Contractors and Suppliers are inducted to site | Prior to commencement | Document Review | Signed Subcontract and Supplier Agreements, TMP approved | Subbie/Supplier Agreements, Approved TMP, Induction register | Site Engineer
3 | Design | H | Ensure that Design is approved and Drawings are of the latest revision | Prior to commencement | Document Review |  | Check Drawing Register | Site Engineer
4 | Survey Setout | H | Setout inlet & outlet points with inverts as required by Contractor to construct to design | Prior to commencement | Survey |  | Survey receipt | Site Engineer
5 | Locate existing services by hand digging or hydrovac | H | Ensure all services conflicting with the line of trench has been exposed by hand digging or hydrovac | Prior to commencement | Potholing | All conflicts have been located. New services and/or conflicts to be advised to Project Engineer. Asbuilt all services | As-built Drawings Doc. Review | Site Engineer
6 | Trenching and Excavation (1) | W | Inspect trench profile and ensure it is correct to lines and levels to design | Daily | Visual/Inspection | Line and level is correct | FHIMS-CS-4025 | Site Engineer
6 | Trenching and Excavation (2) | W | Ensure trench width is sufficient to provide enough space on either side of the pipe for compaction | Daily | Visual/Inspection | 300mm either side of the pipe | FHIMS-CS-4025 | Site Engineer
7 | Foundation Compliance (1) | H | Test formation level on completion of excavation to check if undercut required | One test per 15m linear metres | Scala Penetrometer, Visual Inspection by designer | If CBR is less than 2.5 or 50kPa undercut may be required. Seek engineer guidance for undercut depth | FHIMS-LA-4003, FHIMS-CS-4025 | Site Engineer | Design Engineer
7 | Foundation Compliance (2) | H | If water is in the trench backfill with Drainage 40/20 material ensuring Bidium cloth is pinned to the bottom of the trench. 40/20 material to extend to the mid point on the pipe or to the water table (whichever is highest). | Visual | Compaction | Ensure material is whacked every 150mm lift | FHIMS-CS-4025 | Site Engineer | Design Engineer
8 | Undercut BackFill Material Compliance Testing (1) | H | Material to meet specifications dependant on material type selected | Each material used | Document Review | Compliance with requirements from Specifications | Lab Test Report | Site Engineer
8 | Undercut BackFill Material Compliance Testing (2) | W | Geotextile or Geogrid that is used in the undercut is to be documented on FHIMS-CS-4025 | Each material used | Certification |  | FHIMS-CS-4025 | Site Engineer | Design Engineer
8 | Undercut BackFill Material Compliance Testing (3) | H | Backfill Construction Material | 1 test per 15m | Lab Testing |  | FHIMS-CS-4025 | Site Engineer
9 | Pipe Bedding Material Compliance (1) | H | Material to meet specifications dependant on material type selected | Each material used | Document Review | Compliance with requirements from Specifications | Lab Test Report | Site Engineer
9 | Pipe Bedding Material Compliance (2) | H | Backfill Construction Material | 1 test per 15m | Lab Testing |  | FHIMS-CS-4025 | Site Engineer
10 | Bedding (1) | W | Bedding - Ensure correct thickness of bedding is placed and compacted | Daily | Visual/Inspection | 100mm thick bedding for <450mm dia pipe | FHIMS-CS-4025 | Site Engineer
10 | Bedding (2) | W | Ensure bedding material is compacted | Prior to laying pipe | Testing |  | Lab test results | Site Engineer
11 | Pipes and Precast Units | H | Confirm pipes diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Each delivery to site | Certification | Pipe - Diameter & Class, Wingwalls, Manholes, Cesspits etc. | Delivery Dockets | Site Engineer
12 | Cast Insitu Drainage Components | H | If any cast insitu component i.e. Headwalls is to be completed on a separate ITP - FHIMS-QA-6006 Insitu Concrete | Every Cast Insitu Component | Document Review |  | FHIMS-QA-6006 | Site Engineer
13 | Pipe Laying (1) | W | Pipe Laying -Variation between design invert level to as-laid invert level must be less than 5mm. Variation of grade of one pipe to the next shall be less than 3mm | Daily | Visual/Inspection | Invert level <= 5mm and grade <= 3mm from design levels | FHIMS-CS-4025 | Site Engineer
13 | Pipe Laying (2) | W | Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness | Prior to backfilling | Visual/Inspection | No defects/ gaps / pipes are aligned correctly | Photos | Site Engineer
13 | Pipe Laying (3) | W | As-built survey of pipes installed | Once line is completed between 2 structures | Survey | Invert level <= 5mm and grade <= 3mm from design levels | Survey Receipt | Site Engineer
14 | Design Engineer Pre backfill Inspection (1) | W | Inspection of pipes prior to backfilling to ensure they have been installed correctly and that the joints are sealed. Check for any gaps. | Daily | Visual Inspection | Compliance with the Specification | FHIMS-CS-4025 | Site Engineer | Design Engineer
14 | Design Engineer Pre backfill Inspection (2) | W | The pipes shall be laid with the variation between the specified invert level and invert level laid shall not exceed 5mm | Prior to backfilling | Survey | Vertical tolerance +/- 5mm | FHIMS-CS-4025 | Site Engineer
14 | Design Engineer Pre backfill Inspection (3) | W | Pipe invert checks shall be carried out at least once per day with a maximum of 20m between checks. | Prior to backfilling | Survey | Vertical tolerance +/- 5mm | FHIMS-CS-4025 | Site Engineer
15 | Pipe Backfill Compliance (1) | H | Material to meet specifications dependant on material type selected | Each material used | Document Review | Compliance with requirements from Specifications | FHIMS-CS-4025 | Site Engineer
15 | Pipe Backfill Compliance (2) | H | Backfill Construction Material | 1 NDM test per 15m | Lab Testing |  | Lab Test Report | Site Engineer
16 | Backfilling | W | Backfill 150mm lifts with (material) and test every 300mm lift to underside of Subgrade. Remainder of backfill to be done with excavated material. | 1 test per 20 m length of trench per 300mm lift | Testing |  | Lab test results | Site Engineer
17 | Structure installation (Manhole, Catchpit, Wingwall) (1) | W | Base of structure to be tested. Scala's to be minimum of 3 blows per 100mm | 1 test per structure | Testing | Scala minimum 3 blows/100mm | FHIMS-LA-4003 | Site Engineer
17 | Structure installation (Manhole, Catchpit, Wingwall) (2) | W | Structures to be installed to the design survey location and level | During structure construction | Visual/Inspection | As Built Survey | FHIMS-CS-4006 and Survey receipt | Site Engineer
17 | Structure installation (Manhole, Catchpit, Wingwall) (3) | W | All joints are to be sealed including rungs and lids | During structure construction | Visual/Inspection | Pipe joint to structure shall be encased in 200mm (min.) thick 20MPa concrete | FHIMS-CS-4006 | Site Engineer
17 | Structure installation (Manhole, Catchpit, Wingwall) (4) | W | Arrange as-built survey of the structure and all invert levels | Once installed | Survey | As Built Survey | Survey Receipt | Site Engineer
18 | Post Backfill Inspection | H | On completion of backfilling all lines to be inspected | One per line | Internal Visual Inspection with camera (compliant with Confined Spaces working) | Lines must be straight, free from dirt and obstructions, with no ponding. | FHIMS-CS-4025 | Site Engineer
19 | CCTV | H | For pipes <900mm a CCTV inspection must be completed. Pipes >900mm must be visually inspected | At completion of the works | Visual Inspection/ CCTV inspection | No Defects | Inspection Report CCTV DVD | Site Engineer | Design Engineer
20 | Testing of Manholes & Pipelines | H | If called for in the specifications then test results for water tightness in the structures and low pressure air testing of the pipelines is to be carried out - test sheets to be filling in where required | One per line/structure | Measurement | Drainage Structure Water Tightness Test Record & Low Pressure Air Test Record | FHIMS-CS-4073 & FHIMS-CS-4074 | Site Engineer | Design Engineer
21 | Survey As Built | H | Ensure all drainage lines comply with design prior to carrying on with next construction process | At completion of drainage line | Measurement |  | Survey receipt | Site Engineer
22 | As-builts | H | Red pen mark up drawings to be included in QA file | At the completion of the Lot of work | Drawings | Ensure all Asbuilts uploaded into CONQA | Asbuilt Drawing | Site Engineer
23 | Lot Number QA File | W | Ensure all OFIs are closed and included within QA file, Delivery Dockets and Lab Testing Spreadsheet and Test Reports to be included in QA File | At completion of Lot | Document Review | Ensure all QA is uploaded into CONQA | Delivery Dockets, Test Reports, Lab Testing Register | Site Engineer
Comments:
IFC Drawings used for Construction incl. Rev numbers:
Reference Documentation (Notices/OFIs etc.):
QA Compiled By : |  |  |  |  | Signature: |  |  | Date:
QA checked By Discipline Manager: |  |  |  |  | Signature: |  |  | Date:
QA checked By Quality Manager: |  |  |  |  | Signature: |  |  | Date:
Accepted By Design Engineer: |  |  |  |  | Signature: |  |  | Date: