## Project Structure
Folder Structure |  |  |  |  | Checklists
Storage King Mascot
Structure
Excavation (Compacted Fill)
|  |  | North |  | Excavation - GPL-QSE-ITP-STRUC-003 (Rev 00)
|  |  | South |  | Excavation - GPL-QSE-ITP-STRUC-003 (Rev 00)
Piling
|  |  | North |  | Piling - GPL-QSE-ITP-STRUC-001 (Rev 00)
|  |  | South |  | Piling - GPL-QSE-ITP-STRUC-001 (Rev 00)
Footings
|  |  | Stair Base (South Stair 2) |  | Footings & Bases - GPL-QSE-ITP-STRUC-004 (Rev 00)
|  |  | Stair Base (West Stair 1) |  | Footings & Bases - GPL-QSE-ITP-STRUC-004 (Rev 00)
|  |  | Lift Base |  | Footings & Bases - GPL-QSE-ITP-STRUC-004 (Rev 00)
|  |  | Crane Base |  | Footings & Bases - GPL-QSE-ITP-STRUC-004 (Rev 00)
|  |  | Lift Kicker Walls (Lift 4) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Lift Kicker Walls (Lift 2,3) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Stair Kicker Walls (South) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Stair & Lift Kicker Walls (Lift 1, Stair 1) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
Ground Floor
|  |  | SOG (A) |  | Slab on Ground - GPL-QSE-ITP-STRUC-005 (Rev 00)
|  |  | SOG (B) |  | Slab on Ground - GPL-QSE-ITP-STRUC-005 (Rev 00)
|  |  | SOG (C) |  | Slab on Ground - GPL-QSE-ITP-STRUC-005 (Rev 00)
|  |  | SOG (D) |  | Slab on Ground - GPL-QSE-ITP-STRUC-005 (Rev 00)
|  |  | Suspended Slab over OSD |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Structure Handover |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
Level 1
|  |  | Suspended Slab (A) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Suspended Slab (B) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Lift, Stair Walls & Columns (A) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Lift, Stair Walls & Columns (B) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Structure Handover |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
Level 2
|  |  | Suspended Slab (A) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Suspended Slab (B) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Lift, Stair Walls & Columns (A) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Lift, Stair Walls & Columns (B) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Structure Handover |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
Level 3
|  |  | Suspended Slab (A) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Suspended Slab (B) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Lift, Stair Walls & Columns (A) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Lift, Stair Walls & Columns (B) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Structure Handover |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
Level 4
|  |  | Suspended Slab (A) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Suspended Slab (B) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Lift, Stair Walls & Columns (A) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Lift, Stair Walls & Columns (B) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Structure Handover |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
Level 5
|  |  | Suspended Slab (A) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Suspended Slab (B) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Lift, Stair Walls & Columns (A) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Lift, Stair Walls & Columns (B) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Structure Handover |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
Level 6
|  |  | Suspended Slab (A) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Suspended Slab (B) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Lift, Stair Walls & Columns (A) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Lift, Stair Walls & Columns (B) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Structure Handover |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
Level 7
|  |  | Suspended Slab (A) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Suspended Slab (B) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Lift, Stair Walls & Columns (A) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Lift, Stair Walls & Columns (B) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Structure Handover |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
Level 8
|  |  | Suspended Slab (A) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Suspended Slab (B) |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Lift, Stair Walls & Columns (A) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Lift, Stair Walls & Columns (B) |  | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
|  |  | Structure Handover |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
Level 9 (Roof)
|  |  | Lift & Stair Core Lids |  | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
|  |  | Structural Steel |  | Structural Steel - GPL-QSE-ITP-STRUC-011 (REV 00)
|  |  | Structure Handover |  | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
Façade
Ground Floor
|  |  | Shopfront Glazing |  | Windows - GPL-QSE-ITP-FAC-001 (Rev 00)
|  |  | Façade Cladding |  | Façade Cladding - GPL-QSE-ITP-FAC---- (Rev 00)
Level 1
|  |  | Louvres Installation |  | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00)
|  |  | Windows Installation |  | Windows - GPL-QSE-ITP-FAC-001 (Rev 00)
|  |  | Façade Cladding |  | Façade Cladding - GPL-QSE-ITP-FAC---- (Rev 00)
Level 2
|  |  | Louvres Installation |  | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00)
|  |  | Windows Installation |  | Windows - GPL-QSE-ITP-FAC-001 (Rev 00)
|  |  | Façade Cladding |  | Façade Cladding - GPL-QSE-ITP-FAC---- (Rev 00)
Level 3
|  |  | Louvres Installation |  | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00)
|  |  | Windows Installation |  | Windows - GPL-QSE-ITP-FAC-001 (Rev 00)
|  |  | Façade Cladding & Signage |  | Façade Cladding - GPL-QSE-ITP-FAC---- (Rev 00)
Level 4
|  |  | Louvres Installation |  | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00)
|  |  | Windows Installation |  | Windows - GPL-QSE-ITP-FAC-001 (Rev 00)
|  |  | Façade Cladding & Signage |  | Façade Cladding - GPL-QSE-ITP-FAC---- (Rev 00)
Level 5
|  |  | Louvres Installation |  | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00)
|  |  | Windows Installation |  | Windows - GPL-QSE-ITP-FAC-001 (Rev 00)
|  |  | Façade Cladding & Signage |  | Façade Cladding - GPL-QSE-ITP-FAC---- (Rev 00)
Level 6
|  |  | Louvres Installation |  | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00)
|  |  | Windows Installation |  | Windows - GPL-QSE-ITP-FAC-001 (Rev 00)
|  |  | Façade Cladding & Signage |  | Façade Cladding - GPL-QSE-ITP-FAC---- (Rev 00)
Level 7
|  |  | Louvres Installation |  | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00)
|  |  | Windows Installation |  | Windows - GPL-QSE-ITP-FAC-001 (Rev 00)
|  |  | Façade Cladding & Signage |  | Façade Cladding - GPL-QSE-ITP-FAC---- (Rev 00)
Level 8
|  |  | Louvres Installation |  | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00)
|  |  | Windows Installation |  | Windows - GPL-QSE-ITP-FAC-001 (Rev 00)
|  |  | Façade Cladding & Signage |  | Façade Cladding - GPL-QSE-ITP-FAC---- (Rev 00)
Level 9 (Roof)
|  |  | Laneway Awning Glazing & Box Gutter |  | Awnings & Roofing - GPL-QSE-ITP-FAC 006 (Rev 00)
|  |  | Façade Cladding |  | Façade Cladding - GPL-QSE-ITP-FAC---- (Rev 00)
Fit Out
Ground Floor
|  |  | Masonry Walls |  | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00)
|  |  | Plasterboard Walls |  | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00)
Services
|  |  |  | Hydraulic | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00)
|  |  |  | Mechanical | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00)
|  |  |  | Electrical | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00)
|  |  |  | Fire Services | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00)
Wet Areas
|  |  |  | Waterproofing | Internal Waterproofing - GPL-QSE-ITP-FIT-009 (Rev00)
|  |  |  | Tiling | Tiling Internal - GPL-QSE-ITP-FIT-010 (Rev 00)
|  |  | Plasterboard Ceilings |  | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00)
Mezzanine
|  |  | Waterproofing OSD & Sprinkler Tank |  | Internal Waterproofing - GPL-QSE-ITP-FIT-009 (Rev00)
Level 1
|  |  | Masonry Walls |  | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00)
|  |  | Plasterboard Walls |  | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00)
Services
|  |  |  | Hydraulic | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00)
|  |  |  | Mechanical | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00)
|  |  |  | Electrical | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00)
|  |  |  | Fire Services | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00)
|  |  | Plasterboard Ceilings |  | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00)
|  |  | Storage Cages (Including display area) |  | Storage Cages - GPL-QSE-ITP-FIT-012 (Rev00)
Level 2
|  |  | Masonry Walls |  | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00)
|  |  | Plasterboard Walls |  | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00)
Services
|  |  |  | Hydraulic | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00)
|  |  |  | Mechanical | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00)
|  |  |  | Electrical | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00)
|  |  |  | Fire Services | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00)
|  |  | Plasterboard Ceilings |  | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00)
|  |  | Storage Cages (Including display area) |  | Storage Cages - GPL-QSE-ITP-FIT-012 (Rev00)
Level 3
|  |  | Masonry Walls |  | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00)
|  |  | Plasterboard Walls |  | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00)
Services
|  |  |  | Hydraulic | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00)
|  |  |  | Mechanical | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00)
|  |  |  | Electrical | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00)
|  |  |  | Fire Services | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00)
|  |  | Plasterboard Ceilings |  | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00)
|  |  | Storage Cages (Including display area) |  | Storage Cages - GPL-QSE-ITP-FIT-012 (Rev00)
Level 4
|  |  | Masonry Walls |  | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00)
|  |  | Plasterboard Walls |  | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00)
Services
|  |  |  | Hydraulic | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00)
|  |  |  | Mechanical | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00)
|  |  |  | Electrical | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00)
|  |  |  | Fire Services | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00)
|  |  | Plasterboard Ceilings |  | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00)
|  |  | Storage Cages (Including display area) |  | Storage Cages - GPL-QSE-ITP-FIT-012 (Rev00)
Level 5
|  |  | Masonry Walls |  | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00)
|  |  | Plasterboard Walls |  | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00)
Services
|  |  |  | Hydraulic | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00)
|  |  |  | Mechanical | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00)
|  |  |  | Electrical | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00)
|  |  |  | Fire Services | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00)
|  |  | Plasterboard Ceilings |  | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00)
|  |  | Storage Cages (Including display area) |  | Storage Cages - GPL-QSE-ITP-FIT-012 (Rev00)
Level 6
|  |  | Masonry Walls |  | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00)
|  |  | Plasterboard Walls |  | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00)
Services
|  |  |  | Hydraulic | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00)
|  |  |  | Mechanical | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00)
|  |  |  | Electrical | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00)
|  |  |  | Fire Services | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00)
|  |  | Plasterboard Ceilings |  | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00)
|  |  | Storage Cages |  | Storage Cages - GPL-QSE-ITP-FIT-012 (Rev00)
Level 7
|  |  | Masonry Walls |  | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00)
|  |  | Plasterboard Walls |  | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00)
Services
|  |  |  | Hydraulic | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00)
|  |  |  | Mechanical | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00)
|  |  |  | Electrical | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00)
|  |  |  | Fire Services | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00)
|  |  | Plasterboard Ceilings |  | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00)
|  |  | Storage Cages |  | Storage Cages - GPL-QSE-ITP-FIT-012 (Rev00)
Level 8
|  |  | Masonry Walls |  | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00)
|  |  | Plasterboard Walls |  | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00)
Services
|  |  |  | Hydraulic | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00)
|  |  |  | Mechanical | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00)
|  |  |  | Electrical | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00)
|  |  |  | Fire Services | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00)
Wet Areas
|  |  |  | Waterproofing | Internal Waterproofing - GPL-QSE-ITP-FIT-009 (Rev00)
|  |  |  | Tiling | Tiling Internal - GPL-QSE-ITP-FIT-010 (Rev 00)
|  |  | Plasterboard Ceilings |  | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00)
|  |  | Storage Cages |  | Storage Cages - GPL-QSE-ITP-FIT-012 (Rev00)

## Checklists
type | name | values
checklist | Piling - GPL-QSE-ITP-STRUC-001 (Rev 00)
section | Prior to Works
checkpoint | Attach markup plan of piles covered by this ITP
checkpoint | Confirm Dial-Before-You-Dig has been received (attach plans)
label | Any services in close proximity to be sprayed/pegged out
checkpoint | Confirm existing service scan has been completed (attach survey report)
checkpoint | Obtain certification for the piling mat from Geotech (attach certificate)
checkpoint | Confirm vibration limits and monitoring requirements
checkpoint | Confirm RL’s of top of piles
checkpoint | Confirm set-out of piles and/or recovery marks has been completed (attach survey plan)
label | Refer Architectural footing plan
checkpoint | Confirm MPa, slump and agg size of concrete
text | MPa:
text | Slump:
text | Agg:
checkpoint | Ensure that adequate exclusion zones are setup during piling operations as per SWMS
section | During Works
checkpoint | Confirm pile diameters are correct as per plan
label | Refer Structural Engineer footing plan
checkpoint | Confirm pile cages installed are correct as per design
label | Refer Structural Engineer pile details
checkpoint | Confirm correct concrete supplied (attach docket)
checkpoint | Confirm concrete tester onsite to take samples
checkpoint | Ensure reo cage has sufficient cover and starter bars are of sufficient length
label | Refer Structural Engineer pile details
section | After Works
checkpoint | Obtain as-built survey of piling positions and top of piles RL (attach survey)
checkpoint | Confirm tolerance of piles are as follows:
bool | 10mm +/- from design RL
bool | 25mm +/- from design position
checkpoint | Obtain 7 day concrete crush tests results (attach)
text | Test Strength MPa
checkpoint | Obtain 28 day concrete crush tests results (attach)
text | Test Strength MPa
checkpoint | Attach Piling Subcontractor ITP
section | Sign-Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Capping Beam - GPL-QSE-ITP-STRUC-002 (Rev 00)
section | Prior to Works
checkpoint | Attach markup plan of capping beam covered by this ITP
checkpoint | Confirm excavation for capping beam has been complete
checkpoint | Confirm top of piles are clean and free of debris and starter bar detail correct
checkpoint | Confirm set-out and RL of capping beam has been completed (attached survey plan)
label | Refer Architectural concrete outline
checkpoint | Confirm MPa, slump and agg size of concrete
text | MPa:
text | Slump:
text | Agg:
checkpoint | Check quantity of concrete required prior to ordering
text | m3:
section | During Works
checkpoint | Confirm formwork shutters are clean and will provide required class finish
checkpoint | Attach Formworkers ITP
checkpoint | Attach Formwork Engineer sign off certificate confirming compliance with design & AS3610
checkpoint | Check top RL for all reinforcement to ensuring adequate cover. Confirm with Concreter
checkpoint | Confirm starter bars to columns/walls/stair are installed in correct location
checkpoint | Attach Reo Fixers ITP
checkpoint | Attach Principal Structural Engineer Inspection Report and confirm all actions are closed out
checkpoint | Confirm correct concrete supplied (attach docket)
checkpoint | Confirm concrete tester onsite to take samples
checkpoint | Confirm vibrating is occurring evenly
checkpoint | Attach Concreter ITP
section | After Works
checkpoint | Confirm stripping is complete and all exposed faces are clear of formwork
checkpoint | Confirm vibration was adequate – no air pockets, agg evenly distributed.
label | If not undertake rectification works
checkpoint | Obtain as-built survey (attach survey)
checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
bool | 6mm +/- from design RL
bool | 10mm +/- from design position
checkpoint | Obtain all concrete tests at 7 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 28 days, and attach test results
text | Test Strength MPa
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Excavation - GPL-QSE-ITP-STRUC-003 (Rev 00)
section | Prior to Works
checkpoint | Attach markup plan of extent of excavation covered by this ITP
checkpoint | Confirm Dial-Before-You-Dig has been received (attach plans)
label | Any services in close proximity to be sprayed/pegged out
checkpoint | Confirm existing service scan has been completed (attach survey report)
checkpoint | Confirm if any hand digging excavation is required close to underground services
checkpoint | Confirm set-out of site boundary, excavation line and RL datum (attach survey plan)
checkpoint | Confirm existing water table RL
checkpoint | Confirm dewatering requirements & methodology (if required)
checkpoint | Obtain approval for temporary anchors outside the site boundary (if required)
label | Refer Architectural set out drawings
checkpoint | Confirm vibration limits and monitoring requirements
checkpoint | Confirm noise limits and monitoring requirements
checkpoint | Confirm working hours and equipment limitations
checkpoint | Confirm soil testing has been undertaken and tipping classification report received (attach report)
section | During Works
checkpoint | Collection of tip dockets if required
checkpoint | Confirm progressive set out of basement line (typically at 3m drops - attach survey plans)
checkpoint | Confirm progressive Geotech inspections (typically at 3m drops - attach report and associated closeouts)
checkpoint | Confirm anchor set out and type (if required)
checkpoint | Confirm anchor depth and angle (if required)
checkpoint | Confirm anchor grout strength prior to stressing (if required)
checkpoint | Confirm dowel and reo detail to shotcrete (if required)
checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
checkpoint | Confirm correct concrete supplied (attach docket)
checkpoint | Confirm thickness and finish to shotcrete is as per design
checkpoint | Confirm RL at bulk excavation level
checkpoint | Geotech inspection and bearing capacity at bulk excavation level
checkpoint | Confirm subbase is compliant with engineers requirements
checkpoint | Civil/Structural Engineer inspection
section | After Works
checkpoint | Attach Subcontractor ITP
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Footings & Bases - GPL-QSE-ITP-STRUC-004 (Rev 00)
section | Prior to Works
checkpoint | Attach markup plan of footings & bases covered by this ITP
checkpoint | Confirm set-out of footings & bases has been completed (attach survey plan)
label | Refer Architectural footing plan
checkpoint | Confirm RL of underside of footing & bases
checkpoint | Geotech inspection and bearing capacity of base
checkpoint | Confirm MPa, slump and agg size of concrete
text | MPa:
text | Slump:
text | Agg:
checkpoint | Check quantity of concrete required prior to ordering
text | m3:
section | During Works
checkpoint | Confirm waterproofing product and detail is installed as per design (if required)
label | Refer Architectural waterproofing drawing
checkpoint | Attach Waterproofers ITP
checkpoint | Confirm lightning protection installed to footings as per Electricians requirements
checkpoint | Check top RL for all reinforcement to ensuring adequate cover. Confirm with Concreter
checkpoint | Confirm starter bars to columns/walls/stair are installed in correct location
checkpoint | Attach Formworkers ITP
checkpoint | Attach Reo Fixers ITP
checkpoint | Attach Principal Structural Engineer Inspection Report and confirm all actions are closed out
checkpoint | Confirm Private Certifier inspection of building foundations completed
checkpoint | Confirm correct concrete supplied (attach docket)
checkpoint | Confirm correct concrete supplied (attach docket)
checkpoint | Confirm concrete tester onsite to take samples
checkpoint | Confirm vibrating is occurring evenly
checkpoint | Attach Concreter ITP
section | After Works
checkpoint | Confirm stripping is complete and all exposed faces are clear of formwork
checkpoint | Confirm vibration was adequate – no air pockets, agg evenly distributed.
label | If not undertake rectification works
checkpoint | Obtain as-built survey (attach survey)
checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
bool | 6mm +/- from design RL
bool | 10mm +/- from design position
checkpoint | Obtain all concrete tests at 4 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 7 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 28 days, and attach test results
text | Test Strength MPa
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Slab on Ground - GPL-QSE-ITP-STRUC-005 (Rev 00)
section | Prior to Works
checkpoint | Confirm RL of bulk excavation
checkpoint | Confirm RL of bulk slab thickenings
checkpoint | Confirm set-out of edge boards/set-downs/drains/pits etc (attach survey plan)
label | Refer Architectural concrete outline
checkpoint | Confirm MPa, slump and agg size of concrete
text | MPa:
text | Slump:
text | Agg:
checkpoint | Check quantity of concrete required prior to ordering
text | m3:
section | During Works
checkpoint | Confirm hydraulic pits and line installed
checkpoint | Attach Hydraulic ITP
checkpoint | Confirm vapour barrier installed over correct subbase
checkpoint | Confirm formwork edge boards is adequately braced and square
checkpoint | Confirm set down heights are correct
checkpoint | Confirm all cast in elements to construction joints are installed (key joints, construction joints, expansion joints etc)
checkpoint | Confirm bond breaker has been applied to key joints
checkpoint | Attach Formworkers ITP
checkpoint | Confirm starter bars to columns/walls/stair are installed in correct location
checkpoint | Check top RL for all reinforcement to ensuring adequate cover. Confirm with Concreter
checkpoint | Attach Reo Fixers ITP
checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
checkpoint | Confirm correct concrete supplied (attach docket)
checkpoint | Confirm concrete tester onsite to take samples
checkpoint | Confirm vibrating is occurring evenly
checkpoint | Confirm falls to drainage points in slab
checkpoint | Attach Concreter ITP
section | After Works
checkpoint | Confirm saw joints installed
checkpoint | Confirm stripping is complete and all set-downs/strip drains are clear of formwork
checkpoint | Obtain as-built survey (attached survey)
checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
bool | 6mm +/- from design RL
bool | 10mm +/- from design position
checkpoint | Obtain all concrete tests at 4 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 7 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 28 days, and attach test results
text | Test Strength MPa
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Verticals - GPL-QSE-ITP-STRUC-006 (Rev 00)
section | Prior to Works
checkpoint | Confirm set-out of verticals (attach survey plan)
label | Refer Architectural concrete outline
checkpoint | Confirm cast-in starter bars are in correct location
checkpoint | Confirm MPa, slump and agg size of concrete
text | MPa:
text | Slump:
text | Agg:
checkpoint | Check quantity of concrete required prior to ordering
text | m3:
section | During Works
checkpoint | Check reinforcement to ensuring adequate cover
checkpoint | Confirm vertical and horizontal starter bars are installed in correct location
checkpoint | Attach Reo Fixers ITP
checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
checkpoint | Confirm all hydraulic cast-in services are installed (i.e. downpipes)
checkpoint | Attach Hydraulic ITP
checkpoint | Confirm position of block outs, penetrations etc are installed, as noted on:
bool | Architectural Drawings
bool | Structural Drawings
bool | Lift Drawings
bool | Mechanical Drawings
bool | Electrical Drawings
bool | Fire Drawings
bool | Hydraulic Drawings
checkpoint | Confirm formwork shutters are clean and will provide required class finish
bool | Formwork is clean and free of debris
bool | Lipping of formwork between sheets
bool | Fillets installed at all corners
bool | Ties are installed at even spacing
bool | Bottom of wall/column is clean, free from debris, rubbish or sawdust
checkpoint | Attach Formworkers ITP
checkpoint | Attach Formwork Engineer sign off certificate confirming compliance with design & AS3610
checkpoint | Confirm RL to top of vertical is acknowledged by Formworkers and Concrete Placer
checkpoint | Confirm correct concrete supplied (attach docket)
checkpoint | Confirm concrete tester onsite to take samples
checkpoint | Confirm vibrating is occurring evenly
checkpoint | Attach Concreter ITP
checkpoint | Ensure a representative from each of the following is on site and witnessing the pour:
bool | Formworkers
bool | Plumber
checkpoint | Ensure Formworkers clean any slurry runs at bottom of walls immediately after pour
section | After Works
checkpoint | Confirm stripping is complete and all exposed faces are clear of formwork
checkpoint | Confirm vibration was adequate – no air pockets, agg evenly distributed.
label | If not undertake rectification works
checkpoint | Obtain as-built survey (attach survey)
checkpoint | Obtain all concrete tests at 1 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 4 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 7 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 28 days, and attach test results
text | Test Strength MPa
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Suspended Slab - GPL-QSE-ITP-STRUC-007 (Rev 00)
section | Prior to Works
checkpoint | Confirm set-out of grids, verticals, RL on slab below (attach survey plan)
label | Refer Architectural Concrete Outline
checkpoint | Confirm formwork shop drawings and certificate has been received
checkpoint | Confirm scaffold top-up complete
checkpoint | Confirm safe means of access to new deck
checkpoint | Confirm MPa, slump and agg size of concrete
text | MPa:
text | Slump:
text | Agg:
checkpoint | Check quantity of concrete required prior to ordering
text | m3:
section | During Works
checkpoint | Confirm deck is safe, handrails installed and edge protection is provided to full perimeter of deck
checkpoint | Confirm formwork deck is suitable to achieve required finish to concrete.
bool | Formwork is clean and free of debris, rubbish or sawdust
bool | No lipping of formwork between sheets
bool | Fillets, drip grooves installed at all corners
checkpoint | Confirm as-built survey of deck is complete (attach survey plan)
checkpoint | Confirm tolerance of deck, edgeboard, setdown, penos etc are as follows:
bool | 6mm +/- from design RL
bool | 10mm +/- from design position
checkpoint | Attach Formworkers ITP
holdpoint | Attach Formworkers Deck Handover Certificate
checkpoint | Attach Formwork Engineer sign off certificate, Confirm that certificate references props, braces and compliance with design & AS3610
checkpoint | Install slip joints to all load bearing walls and corbels where required
checkpoint | Attach Hydraulic ITP (for cast-in elements), include relevant mark-ups
checkpoint | Attach Electricians ITP (for cast-in elements), include relevant mark-ups
checkpoint | Attach Fire Services ITP (for cast-in elements), include relevant mark-ups
checkpoint | Attach Mechanical ITP (for cast-in elements), include relevant mark-ups
checkpoint | Confirm that sufficient plastic bar chairs are used everywhere
checkpoint | Confirm starter bars to columns/walls/stair are installed in correct location
checkpoint | Check top RLs for all reinforcement, ensuring adequate concrete cover confirm with Concreter
checkpoint | Attach Reo Fixers ITP
checkpoint | Confirm that PT end condition (pan/edge stress) are correct and as per design
checkpoint | Confirm that correct size chairs are used under PT
checkpoint | Attach Post Tensioner ITP
checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
checkpoint | Attach Post Tensioning Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
checkpoint | Confirm correct concrete supplied (attach docket)
checkpoint | Confirm concrete tester onsite to take samples
checkpoint | Confirm vibrating is occurring evenly
checkpoint | Confirm falls to drainage points in slab
checkpoint | Attach Concreter ITP
checkpoint | Ensure a representative from each of the following is on site and witnessing the pour:
bool | Form Worker
bool | Electrician
bool | Plumber
bool | Post Tensioner
checkpoint | Confirm Form Worker has labour below deck inspecting all joints (particularly at columns & walls) and is immediately cleaning any slurry
section | After Works
checkpoint | Confirm finish of concrete is adequate for application (broom/trowel/helicopter finish), refer to AS3610
checkpoint | Confirm stripping is complete and all edgeboard, setdowns etc are clear of formwork
checkpoint | Obtain as-built survey and set-out for next level (attach survey plan)
checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
bool | 6mm +/- from design RL
bool | 10mm +/- from design position
checkpoint | Confirm initial stress is conducted, after concrete has reached 9 MPa
checkpoint | Confirm final stress is conducted, after concrete has reached 22 MPa
checkpoint | Obtain all concrete tests at 1 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 4 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 7 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 28 days, and attach test results
text | Test Strength MPa
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Stairs - GPL-QSE-ITP-STRUC-08 (Rev 00)
section | Prior to Works
checkpoint | Confirm bottom of stair RL's on Architectural Concrete Outlines
text | Bottom of Stair SSL:
text | Bottom of Stair FFL:
checkpoint | Confirm top of stair RL's on Architectural Concrete Outlines
text | Top of Stair SSL:
text | Top of Stair FFL:
checkpoint | Confirm mid landing RL's on Architectural Concrete Outlines
text | Mid Landing SSL:
text | Mid Landing FFL:
checkpoint | Check quantity of concrete required prior to ordering
text | Total m3:
checkpoint | Confirm MPa, slump and agg size of concrete prior to ordering
text | MPa:
text | Slump:
text | Agg:
section | During Works
checkpoint | Confirm all formwork is clean and free of debris
checkpoint | Confirm all cast in elements installed (i.e stair handrails), cross-check with stair shop drawings
checkpoint | Attach Formworkers ITP
checkpoint | Confirm position of block outs or penetrations installed for services (eg; fire hydrant, lighting, etc…)
checkpoint | Confirm cast-in and/or post fix starter bars are installed as per design at landings
checkpoint | Check for reinforcement lapping from landing into throat of stair as per Structural Details
checkpoint | Check top RLs for all reinforcement, ensuring adequate concrete cover confirm with Concreter
checkpoint | Attach Reo Fixers ITP
checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
checkpoint | Confirm correct concrete supplied (attach docket)
checkpoint | Confirm concrete tester onsite to take samples
checkpoint | Confirm vibrating is occurring evenly
checkpoint | Confirm cast-in of anti-slip items (eg, carborundum powder, stair nosings, etc…);
checkpoint | Attach Concreter ITP
checkpoint | Confirm Form Worker labour is available to clean up any slurry runs at bottom of walls, immediately after pour
section | After Works
checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
bool | 6mm +/- from design RL
bool | 6mm +/- from 3m straight edges
checkpoint | Obtain all concrete tests at 7 days, and attach test results
text | Test Strength MPa
checkpoint | Obtain all concrete tests at 28 days, and attach test results
text | Test Strength MPa
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Precast GPL-QSE-ITP-STRUC-09(Rev00)
section | Prior to Works
checkpoint | Confirm set-out of grids, verticals, RL on slab below (attach survey plan)
label | Refer Architectural Concrete Outline
checkpoint | Attach manufacturer ITP for panels
checkpoint | Attach Principal Structural Engineer review and acceptance of ITP
checkpoint | Confirm cast-in dowel & starter bars are correct & verified against structural drawings
checkpoint | Confirm that minimum concrete slab strength (typically 20mPa) has been reached for temporary bracing install
checkpoint | Attach manufacturer Design Certificate for panels
checkpoint | Confirm that exclusion zones are set up prior to lifting
checkpoint | Confirm all precast panels have been inspected for damage prior to lifting off truck
section | During Works
checkpoint | Confirm panels are installed in correct & final position. Check alignment with adjacent elements
checkpoint | Confirm bracing installed as per design
label | Refer Precast shop drawing
checkpoint | Attach Precast installation certificate
section | After Works
checkpoint | Confirm tolerance of finished concrete surfaces are as follows:
bool | 6mm +/- from design RL
bool | 6mm +/- from 3m straight edges
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Structure Handover to Fitout - GPL-QSE-ITP-STRUC-010 (REV 00)
checkpoint | Confirm all materials have been removed from level
checkpoint | Confirm that all slabs have been swept and cleaned of debris.
checkpoint | Confirm all fillets and nails have been removed from slab soffits
checkpoint | Confirm that all formwork has been removed from penetrations
checkpoint | Confirm that all structural defects are rectified and signed off by Principal Structural Engineer
checkpoint | Confirm that surveyor benchmark and grid lines are visible on slab
checkpoint | Confirm that all set downs have been reviewed and rectified due to incorrect setouts or issues of depth
checkpoint | Confirm grouting of PT ducts are completed and grout tubes cut flush
checkpoint | Confirm all pans have been filled and/or edge stress pockets filled
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Windows - GPL-QSE-ITP-FAC-001 (Rev 00)
section | Prior to Works
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Surveyor 1m mark and gridlines installed
checkpoint | Confirm rebate/hob RL and position correct
label | Refer Architectural Concrete Outline drawings
checkpoint | Waterproof membrane laid and dry prior to install
checkpoint | All site measures for opening sizes complete prior to manufacture
label | Refer Architectural Window Clear Opening drawing
checkpoint | All windows and doors delivered to site are correct type (colour, glass type & thickness, frame dimensions, function etc)
label | Refer Architectural/Façade Spec and Shop drawing
section | During Works
checkpoint | All windows and doors fixed plumb and level
checkpoint | All windows and door are in alignment with adj windows, and heads align
checkpoint | All relevant windows and doors align with windows on the floor below
checkpoint | Confirm RL of window sill against surveyor 1m mark
checkpoint | All sills flashings installed
checkpoint | Flyscreens installed where required
checkpoint | All gaps caulked not in excess of 25mm
section | After Works
checkpoint | Review windows to ensure no visible damage to glass or aluminium components, and protection installed
checkpoint | All window and door hardware and locks installed and keyed alike
checkpoint | All glass and sliding tracks clean and clear
checkpoint | Plywood ramps installed for access where required
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | External Masonry - GPL-QSE-ITP-FAC-002 (Rev 00)
section | Prior to Works Commencing
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Surveyor 1m mark and gridlines installed
checkpoint | Confirm wall set-out as per Architectural Drawings
checkpoint | Confirm that all penetrations as required for services are identified and marked (i.e. mechanical, electrical, fire, hydraulic, etc)
checkpoint | Confirm requirement for core filling and/or stiffeners
label | Refer Architectural Wall Set-out drawings and Structural Engineer Masonry Details
checkpoint | Confirm vermin/insect/ fire protection requirements are compiled to for all masonry sundries (i.e. stainless steel weep hole cassettes, cavity mesh, brick ties, etc)
checkpoint | Confirm FRL’s and that bricks/blocks will achieve requirements as per specs and relevant fire reports
label | Refer Architectural Fire Line drawings
checkpoint | Confirm bricks/blocks are correct manufacturer, colour and size as per drawings, specs and finishes schedules
checkpoint | Confirm brick laying pattern (i.e. stretcher bond, stack bond etc) is as per drawings, specs and finishes schedules
checkpoint | Confirm face brick set out point and RL is as per architectural drawings
checkpoint | Confirm any specific architectural details (capping's, header courses, etc) are as per architectural drawings
checkpoint | Confirm mortar and caulking colours are as per specs and finishes schedules
section | During Works
checkpoint | Confirm shelf angles are installed as per installation guideline (i.e. spacing, size and embedment of fixing)
checkpoint | Confirm shelf angle RL’s is correct relative to brick gauge requirement
checkpoint | All damp proof course and flashings built in
checkpoint | Ensure weep holes are installed at correct centres
checkpoint | Confirm that ties and stiffeners are installed at correct centres
label | Refer Structural Engineer Masonry Details
checkpoint | All cavities clean and clear
label | Ensure all damp proof courses/flashings are free of damage and clean and weep holes unblocked (photo evidence)
checkpoint | Ensure all courses are laid level, all joint sizes are consistent and ironed correctly
checkpoint | Check verticality between panels and that no steps in face work are present
checkpoint | Inspect all joints are caulked where required and colour is correct as spec’d
section | After Works
checkpoint | Check no chips in bricks/blocks are visible
checkpoint | Final brick/block clean
label | Confirm cleaning method complies to manufacturers specs
checkpoint | Attach subcontractor ITP
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Louvres & Screens - GPL-QSE-ITP-FAC 003 (Rev 00)
section | Prior to Works
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Surveyor 1m mark and gridlines installed
checkpoint | Confirm structural opening for louvres is as per design
label | Refer Architectural Elevation and Shop drawing
checkpoint | All louvers delivered to site are correct type (colour, blade angle/dimensions, function etc)
label | Refer Architectural/Façade Spec and Shop drawing
checkpoint | Confirm fixing detail back to main structure (i.e. any additional structural framing required)
label | Refer Architectural and Shop drawing
section | During Works
checkpoint | Confirm louvre fixings are correct centres and type (i.e. material, diameter and embedment)
label | Refer Shop drawing
checkpoint | Confirm louvres in correct location on façade, installed true and plumb
checkpoint | Confirm any caulking and sealing completed on louvres/brackets
section | After Works
checkpoint | Review louvers to ensure no visible damage or scratches
checkpoint | All louvers clean and protection removed
checkpoint | Attach subcontractor ITP
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Stone Cladding - GPL-QSE-ITP-FAC 004 (Rev 00)
section | Prior to work
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Surveyor 1m mark and gridlines installed
checkpoint | Confirm structure and openings are as per design
label | Refer Architectural Plans, Elevation and Shop drawing
checkpoint | Confirm all required waterproofing to substrate has been completed
checkpoint | All material delivered to site are correct (size, thickness, edge detail/mitre, as per approved sample etc)
section | During to work
checkpoint | Confirm cavity set out as per design
label | Refer Shop drawing
checkpoint | Confirm pin fixings have been installed to specified (i.e. spacing, size and embedment of fixing)
checkpoint | Confirm pin fixings have been pull tested
checkpoint | Attach test results
checkpoint | Confirm joints are consistent, as per design and at correct RL
label | Refer Shop drawing
checkpoint | All cavities clean and clear
section | After works
checkpoint | Review sandstone to ensure no visible damage or scratches
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Balustrades - GPL-QSE-ITP-FAC 005 (Rev 00)
section | Prior to work
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Surveyor 1m mark and gridlines installed
checkpoint | Waterproof membrane laid and dry prior to install
checkpoint | All site measures for opening sizes complete prior to manufacture
label | Refer Architectural Clear Opening drawing
checkpoint | Confirm rebate/hob RL and position correct if required.
checkpoint | Confirm all balustrades delivered to site are correct type (colour, glass thickness, frame dimensions etc)
checkpoint | Confirm revised access strategy to/from balcony/scaffold prior to commencing works
section | During to work
checkpoint | Confirm base channel fixings have been installed to specified (i.e. spacing, size and embedment of fixing)
checkpoint | Confirm that adjoining balustrades have common level or line.
checkpoint | Confirm height of balustrade 1000mm minimum from FFL
checkpoint | Confirm 125mm maximum distance between end posts and adj walls
checkpoint | Confirm no foot hold between 150mm and 760mm from FFL
section | After Work
checkpoint | Review balustrades to ensure no visible damage or scratches
checkpoint | All balustrades clean and protection removed
checkpoint | Attach subcontractor ITP.
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Awnings & Roofing - GPL-QSE-ITP-FAC 006 (Rev 00)
section | Prior to work
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | All material delivered to site are correct type (colour, thickness, dimensions etc)
checkpoint | Exclusion zone setup below (if required)
section | During Works
checkpoint | Confirm all sub framing as per approved design (spacing, pitch etc)
checkpoint | Confirm insulation installed as per specification
checkpoint | All set out and opening sizes for skylights etc correct
checkpoint | Confirm sheet fixings as per design (i.e. spacing, size, type etc)
checkpoint | All over flashings and under flashings installed
checkpoint | All box gutters, sumps and overflows correct size and location
label | Refer Architectural Plans, Elevation, Hydraulic Plans and Shop drawing
checkpoint | Remove metal filing, off-cuts, dust and other materials which could cause corrosion or blockages
section | After Works
checkpoint | Water Test – Hose test entire area for 4hr minimum
label | If failure occurs, rectify issue and retest
checkpoint | Review to ensure no visible damage or scratches
checkpoint | Attach subcontractor ITP.
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | External Waterproofing - GPL-QSE-ITP-FAC 007 (Rev 00)
section | Prior to Works Commencing
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Floor wastes are flush, free of waste material and in correct location
checkpoint | Water Test - Confirm concrete has structurally fall to floor wastes
label | If ponding occurs, top area and retest
checkpoint | Confirm no ponding of water by completing water testing to slab
checkpoint | Confirm all concrete defects have been actioned and surface inspected/accepted by subcontractor
section | During Works
checkpoint | Confirm product used is as per design
label | Refer Architectural Waterproofing drawing
checkpoint | Confirm minimum lap (150mm min typical), upturn (150mm min typical) etc dimensions are achieved
checkpoint | Base membrane inspected for imperfections
checkpoint | Top membrane inspected for imperfections
checkpoint | Confirm all penetrations through planter box walls are sealed
section | After Works
checkpoint | Spark Test - Subcontractor undertake spark test after minimum drying time
label | If pinholes failure occurs, rectify issue and retest
checkpoint | Flood Test - Subcontractor block floors waste and fill water to height of overflow for min 24 hours
label | If failure occurs, rectify issue and retest
checkpoint | Attach subcontractor ITP
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Tiling External - GPL-QSE-ITP-FAC 007 (Rev 00)
section | Prior to Works
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Surveyor 1m mark installed
checkpoint | Waterproof membrane laid and dry prior to install
checkpoint | Confirm tile type, size and thickness and grout colour is correct
label | Refer approved sample & apartment finishes matrix
checkpoint | Confirm tile set-out point
label | Refer Architectural Plans, Finishes Schedule
checkpoint | Confirm if acoustic mat or similar is required
label | Refer Architectural RCP, Acoustic Report
checkpoint | Confirm drainage is installed as per design.
label | Refer to Architectural & Hydraulic Plan
section | During Works
checkpoint | Confirm that all floor wastes are plugged during tiling works
checkpoint | Confirm minimum bedding thickness is achieved
checkpoint | Confirm installation of floor wastes is flush with or 1mm below floor tile level
checkpoint | Floor tiles laid to falls – minimum 1:100 or as documented
checkpoint | Grouting checked for uniformity and quality
checkpoint | Ensure quality of tile installation is maintained, i.e. alignment of joints, joint thickness
section | After Works
checkpoint | Review to ensure no visible damage or scratches
checkpoint | Attach subcontractor ITP
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Hebel - GPL-QSE-ITP-FIT-001 (Rev00)
section | Prior to Works
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Surveyor 1m mark and gridlines installed
checkpoint | Confirm safe Hebel cutting area and control measures are in place
section | During Works
checkpoint | Confirm correct head track used (Slotted angle top track to be used when < 3200mm, standard U deflection top track to be used when > 3200mm)
checkpoint | Confirm base angle has been fixed to slab at a maximum of 600mm spacings
checkpoint | Confirm panels do not straddle
checkpoint | Confirm that Hebel Mortar has been used at base of panels
checkpoint | Confirm Hebel Panel has been fixed to base angle with hex head screw 50mm from each corner
checkpoint | Confirm Hebel Panel has been fixed to head track at 900mm spacing and middle of slotted hole where applicable
checkpoint | Confirm that a maximum of 15mm spacing have been left between top of panel and concrete soffit
checkpoint | Confirm head has been caulked at junction with concrete soffit with Intumescent & Acoustic Sealant on both sides, ore one side where slotted angle track used
checkpoint | Ensure that backing rod is used behind Intumescent & Acoustic Sealant.
checkpoint | Confirm that Hebel Power Panels are glued edge to edge with Hebel adhesive.
checkpoint | Confirm all fire door frames fixed to Hebel wall panels are filled with TRCO FYREFLEX.
checkpoint | Confirm that any panel to panel junction detail must be fastened together by thread screw at 900mm maximum centres and be a maximum of 100mm from the panel end.
checkpoint | Ensure that any exposed cut reinforcement has been coated with the Hebel anti-corrosion protection paint.
checkpoint | Attach CSR Inspection Report, and confirm that all actions are closed out
section | After Works
checkpoint | Review panels to ensure no visible damage/cracks/peons
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Internal Masonry - GPL-QSE-ITP-FIT-02 (Rev00)
section | Prior to Works
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Confirm surveyor 1m mark and gridlines installed
checkpoint | Confirm wall set-out correct
label | Refer Architectural Wall Partition Set-Out drawing
checkpoint | Confirm that all penetrations as required for services are identified and marked (i.e. mechanical, electrical, fire, hydraulic, etc)
checkpoint | Confirm requirement for core filling and/or stiffeners
label | Refer Architectural Wall Set-out drawings and Structural Engineer Masonry Details
checkpoint | Confirm FRL’s and that bricks/blocks will achieve requirements as per specs and relevant fire reports
label | Refer Architectural Fire Line drawings
checkpoint | Confirm bricks/blocks are correct manufacturer, colour and size as per drawings, specs and finishes schedules
checkpoint | Confirm brick laying pattern (i.e. stretcher bond, stack bond etc) is as per drawings, specs and finishes schedules
checkpoint | Confirm mortar and caulking colours are as per specs and finishes schedules
section | During Works
checkpoint | Confirm that ties and stiffeners are installed at correct centres
label | Refer Structural Engineer Masonry Details
checkpoint | All cavities clean and clear
checkpoint | Ensure all courses are laid level, all joint sizes are consistent and ironed correctly
checkpoint | Check verticality between panels and that no steps in face work are present
checkpoint | Inspect all joints are caulked where required and colour is correct as spec’d
section | After Works
checkpoint | Check no chips in bricks/blocks are visible
checkpoint | Final brick/block clean
label | Confirm cleaning method complies to manufacturers specs
checkpoint | Attach subcontractor ITP
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Plasterboard Walls - GPL-QSE-ITP-FIT-003 (Rev 00)
section | Prior to Works
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Confirm surveyor 1m mark and gridlines installed
section | During Framing Works
checkpoint | Confirm wall set-out correct
label | Refer Architectural Wall Partition and Wall Type drawing
checkpoint | Confirm framing gauge and stud spacing to external walls as per design
label | Refer CSR or similar facade stud design
checkpoint | Confirm framing is straight and plumb
checkpoint | Confirm door frames are correct RL, plumb and installed at correct orientation
checkpoint | Confirm corners are square (notably wet areas)
checkpoint | Confirm minimum cavities achieved between Hebel and stud
label | Refer Acoustic reports
checkpoint | Confirm that joinery openings are correct
checkpoint | Confirm all noggins are installed
bool | Bathroom Accessories and Grab Rails
bool | Bathroom Vanities and Shavers
bool | Kitchen Joinery
bool | Laundry Washer/Dryers
bool | Wall-fixed Joinery etc
section | During Sheeting Works
checkpoint | Confirm all service ITPs have been received
checkpoint | Attach Fire Penetration Inspection Report, and confirm that all actions are closed out
checkpoint | Confirm acoustic and thermal insulation installed
label | Refer Acoustic and Section J reports
checkpoint | Confirm correct board type has been used (FC, Blue Board, Aqua check etc)
checkpoint | Confirm sheeting to intertenancy and wet areas are full height and sealed to concrete soffit on both sides of wall (or as required)
label | Refer Acoustic reports
checkpoint | Confirm all penetrations through wet area walls adjacent to habitable rooms are sealed and caulked
checkpoint | Confirm skirting fixed level and at correct RL at joinery/window interfaces
section | After Works
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Plasterboard Ceilings - GPL-QSE-ITP-FIT-004 (Rev 00)
section | Prior to Works
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Confirm surveyor 1m mark and gridlines installed
checkpoint | Attach Acoustic Consultant Inspection Report, and confirm that all actions are closed out
checkpoint | Attach Fire Penetration Inspection Report, and confirm that all actions are closed out
section | During Works
checkpoint | Confirm ceiling framing flat and at correct RL to achieve FTC height
checkpoint | Confirm ceiling framing bulkheads are square and level
checkpoint | Confirm ceiling interface with door frames correct
checkpoint | Confirm access panel set-out correct and AC equipment, fire dampers etc are accessible
label | Refer Architectural RCP drawing
checkpoint | Confirm all noggins are installed
bool | Blind Pelmets
bool | Ceiling Fans
bool | Pivot Doors
checkpoint | Confirm all grill inserts are installed to bulkhead framing (where applicable)
checkpoint | Confirm ceiling insulation complete (where applicable)
checkpoint | Confirm ceiling framing do not clash with other services (e.g. downlights, access panels, mechanical exhaust, sprinkler heads)
section | After Works
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Hydraulic Rough-in - GPL-QSE-ITP-FIT-005 (Rev 00)
section | Prior to Works
checkpoint | Attach markup plan of area/unit covered by this ITP
section | Stacks and Underslung
checkpoint | Fire collars inspected prior to works. If cast-in, all grout removed, no honeycombing etc. If retrofit, correct number of screws used etc.
checkpoint | No part of fire collar covered (i.e. painted or Hebel head track etc)
checkpoint | Underslung PVC pipe installed as per design location. If not, mark up sent to record 'as-built'
label | Refer Hydraulic drainage plan
checkpoint | Underslung PVC pipes and traps invert level all contained inside ceiling void
label | Refer Architectural RCP
checkpoint | IO's installed as per design and at change of directions
checkpoint | All PVC pipe work acoustically lagged and wrapped as required
label | Refer Acoustic Report
checkpoint | Confirm PVC pipes are not bridging against metal studs (Minimum 5mm clearance is required after lagging)
section | Rough-in
checkpoint | Confirm rough-in location to kitchen water and gas as per kitchen shop drawing
checkpoint | Confirm rough-in location of wet area as per design
checkpoint | Confirm rough-in heights of wet area as per design
text | Shower head, mixer, diverter
text | Bath spout, mixer
text | Basin spout, mixer, waste
checkpoint | Confirm inbuilt cistern location and framing
checkpoint | Confirm A/C tundish location
checkpoint | PEX pipes clipped at required centres (horizontal 600mm, vertical 1200mm) and rubber grommets fitted where running through studs.
checkpoint | Confirm following test been undertaken (attached sign off)
bool | Pressure test for water and gas
bool | Drainage pipework
checkpoint | Confirm all penetrations through fire walls/slabs are treated and signed off by Fire Peno consultant
section | After Works
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Electrical Rough In - GPL-QSE-ITP-FIT-006 (Rev 00)
section | Prior to Works
checkpoint | Attach markup plan of area/unit covered by this ITP
section | During Works
checkpoint | Confirm light layout and switching as per the design
label | Refer Architectural RCP NOT Electrical Plan
checkpoint | Confirm height and location of the following
text | Internal GPOs, TV & data
text | Fridge/Freezer GPO
text | Kitchen GPOs
text | Bathroom GPO
text | Security Intercom
text | External GPO
label | Refer Architectural Set-out NOT Electrical Plan
checkpoint | Confirm GPO locations for OTHER (i.e. fans, FCUs, blinds, etc)
checkpoint | Confirm NBN conduit and draw wire
checkpoint | Confirm all penetrations through fire walls/slabs are treated and signed off by Fire Peno consultant
section | After Works
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Mechanical Rough In - GPL-QSE-ITP-FIT-007 (Rev 00)
section | Prior to Works
checkpoint | Attach markup plan of area/unit covered by this ITP
section | During Works
checkpoint | Confirm FCU and Fan location as per the design and ceiling access panel will work for servicing (i.e. back left hand side of FCU, directly under fan)
label | Refer Architectural RCP for Access Panel location
checkpoint | Confirm FCUs and Fans are vibration isolated from soffit with in shear rubber mounts
checkpoint | Confirm minimum 100mm clearance behind FCU for return air path
checkpoint | Confirm all flexible and sheet metal ducting has been installed as per drawings
checkpoint | Confirm sealing of flexible connections between kitchen/ toilet exhaust fan and metal ducting (mechanically fixed required)
checkpoint | Confirm flexible ductwork is not crushed, torn or damaged at any point
checkpoint | Confirm wiring of AC controls are located as per architectural set-out
checkpoint | Confirm all refrigerant pipes have been installed, pressure tested and insulated
checkpoint | Confirm all condensate drains have been installed back to tundish and tested for falls
checkpoint | Confirm all above ceiling air paths are maintained as per design
checkpoint | Confirm all penetrations through fire walls/slabs are treated and signed off by Fire Peno consultant
section | After Works
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Fire Services Rough In - GPL-QSE-ITP-FIT-008 (Rev 00)
section | Prior to Works
checkpoint | Attach markup plan of area/unit covered by this ITP
section | During Works
checkpoint | Confirm sprinkler pipework installed as per drawings
checkpoint | Confirm sprinkler heads have been installed as per architectural RCP layout
checkpoint | Confirm any drenchers required have been installed
checkpoint | Confirm red cabling installed for fire electrical speakers and detectors
checkpoint | Confirm all penetrations through fire walls/slabs are treated and signed off by Fire Peno consultant
checkpoint | Confirm pipework pressure test has been undertaken
section | After Works
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Internal Waterproofing - GPL-QSE-ITP-FIT-009 (Rev00)
section | Prior to Works Commencing
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Floor wastes are flush, free of waste material and in correct location
checkpoint | Water Test - Confirm concrete has structurally fall to floor wastes
label | If ponding occurs, top area and retest
checkpoint | Confirm no ponding of water by completing water testing to slab
checkpoint | Confirm all concrete defects have been actioned and surface inspected/accepted by subcontractor
checkpoint | Confirm position and RL of waterproofing angles
section | During Works
checkpoint | Confirm product used is as per design
label | Refer Architectural Waterproofing drawing
checkpoint | Sealant at wall/floor junction and wall/wall junction inspected for imperfections
checkpoint | Confirm minimum lap (150mm min typical), upturn (150mm min typical) etc dimensions are achieved
checkpoint | Base membrane inspected for imperfections
checkpoint | Top membrane inspected for imperfections
checkpoint | Confirm exposed aluminium angles are not membrane over
checkpoint | Confirm waterproofing complete around all PC penetrations (i.e. mixer, spouts, shower head etc.)
section | After Works
checkpoint | Confirm no pinholes with detector after minimum drying time 24 hours
checkpoint | Flood Test - Subcontractor block floors waste and fill water to height of overflow for min 24 hours
label | If failure occurs, rectify issue and retest
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Tiling Internal - GPL-QSE-ITP-FIT-010 (Rev 00)
section | Prior to Works
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Surveyor 1m mark installed
checkpoint | Waterproof membrane laid and dry prior to install
checkpoint | Confirm tile type, size and thickness and grout colour is correct
label | Refer approved sample & apartment finishes matrix
checkpoint | Confirm tile set-out point
label | Refer Architectural Plans, Finishes Schedule
checkpoint | Confirm if acoustic mat or similar is required
label | Refer Architectural RCP, Acoustic Report
checkpoint | Confirm drainage is installed as per design.
label | Refer to Architectural & Hydraulic Plan
checkpoint | Confirm aluminium angle is not damaged or misaligned
checkpoint | Confirm top of aluminium angle is at the correct RL, and check against external floor finished level
section | During Works
checkpoint | Confirm that all floor wastes are plugged during tiling works
checkpoint | Confirm minimum bedding thickness is achieved
checkpoint | Confirm installation of floor wastes is flush with or 1mm below floor tile level
checkpoint | Floor tiles laid to falls – minimum 1:100 or 1:80 inside showers
checkpoint | Stop wall and floor tiles 2-3mm short of edges and fill with resilient caulking compound
checkpoint | Grouting checked for uniformity and quality
checkpoint | Ensure quality of tile installation is maintained, i.e. alignment of joints, joint thickness
section | After Tiling
checkpoint | Review to ensure no visible damage or scratches
checkpoint | Confirm all excess silicon is removed from tiles and adjoining surfaces
checkpoint | Attach subcontractor ITP
section | Sign Off
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: FM
label | Issue Date: 21.09.2022
checklist | Structural Steel - GPL-QSE-ITP-STRUC-011 (REV 00)
section | Prior to Works
checkpoint | Confirm set-out of grids, and benchmark RL on slab below. Attach survey plan.
label | Refer Architectural Concrete Outline
label | Refer Structural Steel Marking Plan
checkpoint | Attach structural steel manufacturer ITP
bool | Steel assembly and material certification from supplier
bool | Welding certification from supplier as per AS1554.1
bool | Paint certification from supplier
checkpoint | Attach Principal Structural Engineer review and acceptance of structural steel manufacture
checkpoint | Confirm cast-in and/or base plate details are correct & verified against structural drawings
checkpoint | Confirm exclusion zones are set up prior to lifting
checkpoint | Confirm all steel members have been inspected for damage prior to lifting off truck
section | During Works
checkpoint | Confirm Steel members are correct size.
label | Refer Structural Steel Marking Plan
checkpoint | Confirm Steel columns are installed in correct & final position. Check plumbness. Check RL. Check alignment with adjacent elements.
checkpoint | Check Flange / Web direction in correct position.
checkpoint | Confirm Steel beams are installed as per design.
label | Refer Structural Steel assembly drawing
text | Bolt type & quantity:
text | Bolt direction:
checkpoint | Confirm connection detail installed as per design
checkpoint | Confirm on-site welding completed as per design, attach ITP
label | Welds require 10% mag testing, 100% visual testing
checkpoint | Attach Structural Steel installation certificate
section | After Works
checkpoint | Attach Surveyor As-Built & Verticality Check.
checkpoint | Confirm tolerance of structural steel elements are as follows:
bool | 10mm +/- from design RL
bool | 6mm +/- from position
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: DL
label | Issue Date: 24.04.2023
checklist | Façade Cladding - GPL-QSE-ITP-FAC 008 (Rev 00)
section | Prior to work
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Confirm structural supports and openings are as per design
label | Refer Architectural Plans, Elevation and Shop drawing
checkpoint | Confirm all required waterproofing to substrate has been completed
checkpoint | All material delivered to site are correct (size, thickness, fixing detail, as per approved sample etc)
Text | Confirming fixing methodology (exposed/internal/recessed):
section | During to work
checkpoint | Confirm cavity set out as per design
label | Refer Shop drawing
checkpoint | Confirm sarking has been installed correctly (i.e. overlap, taping of edges)
checkpoint | Confirm fixings have been installed to specified (i.e. spacing, size)
checkpoint | Confirm joints are consistent, as per design and at correct RL & spacing
label | Refer Shop drawing
section | After works
checkpoint | Review cladding to ensure no visible damage or scratches
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: DL
label | Issue Date: 12.05.2023
checklist | Sandwich Panels - GPL-QSE-ITP-FIT-011 (Rev00)
section | Prior to Works
checkpoint | Attach sandwich panel manufacturer ITP
checkpoint | Sandwich panel material certification from supplier
checkpoint | Collate individual dockets for facility validation
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Surveyor 1m mark and gridlines installed
text | Confirm joint direction (horizontal/vertical):
text | Confirm installation methodology (panel lifting tool/craneage/etc):
checkpoint | All panels delivered to site are correct (size, thickness, openings)
label | Refer Shop Drawings
section | During Works
checkpoint | Confirm correct head track and bottom plinth
checkpoint | Confirming spacing of fixings
checkpoint | Confirm bottom U channel and horizontal insulation installed
checkpoint | Confirm sealing tape and/or flashing installed
checkpoint | Check for panel alignment, joints, interfaces, sealing
checkpoint | Confirm perimeter ceiling track installed
checkpoint | Confirm insulation installed at perimeter
checkpoint | Confirm ceiling panel supports & spacing
bool | Confirm ceiling panels are complete & OK for foot traffic
checkpoint | Confirm sealing works are completed correctly
checkpoint | Attach Cleanroom Consultant Inspection Report, and confirm all actions are closed out
section | After Works
checkpoint | Review panels to ensure no visible damage/cracks/misalignments
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: DL
label | Issue Date: 12.05.2023
checklist | Cleanroom Checklist - GPL-QSE-ITP-FIT-012 (Rev00)
section | Prior to Works
checkpoint | Cleanroom material delivered clean, protected, and undamaged (plastic wrap)
bool | Confirm sandwich panels
bool | Confirm mechanical ductwork
bool | Confirm pipework
label | Refer Structural Steel assembly drawing
text | Bolt type & quantity:
text | Bolt direction:
checkpoint | Surveyor 1m mark and gridlines installed
text | Confirm joint direction (horizontal/vertical):
text | Confirm installation methodology (panel lifting tool/craneage/etc):
checkpoint | All panels delivered to site are correct (size, thickness, openings)
label | Refer Shop Drawings
section | During Works
checkpoint | Confirm correct head track and bottom plinth
checkpoint | Confirming spacing of fixings
checkpoint | Confirm bottom U channel and horizontal insulation installed
checkpoint | Confirm sealing tape and/or flashing installed
checkpoint | Check for panel alignment, joints, interfaces, sealing
checkpoint | Confirm perimeter ceiling track installed
checkpoint | Confirm insulation installed at perimeter
checkpoint | Confirm ceiling panel supports & spacing
bool | Confirm ceiling panels are complete & OK for foot traffic
checkpoint | Confirm sealing works are completed correctly
checkpoint | Attach Cleanroom Consultant Inspection Report, and confirm all actions are closed out
section | After Works
checkpoint | Review panels to ensure no visible damage/cracks/misalignments
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: DL
label | Issue Date: 24.06.2023
checklist | Storage Cages - GPL-QSE-ITP-FIT-012 (Rev00)
section | Prior to Works
checkpoint | Work area and surfaces clean and clear ready to commence work
checkpoint | Confirm correct colour has been delivered
label | Refer Architectural Specification
checkpoint | Confirm surveyor 1m mark and gridlines installed
section | During Installation Works
checkpoint | Confirm wall set-out is correct
label | Refer Architectural Wall Partition and Wall Type drawing
checkpoint | Confirm framing is straight and plumb
checkpoint | Confirm door openings are correct position, RL, plumb and installed at correct orientation
checkpoint | Confirm corners are square
checkpoint | Confirm corner guards and rails are fixed level and at correct RL
section | After Works
checkpoint | Attach subcontractor ITP
section | Sign Offs
checkpoint | Orwell Sign Off
holdpoint | Request Sign Off
label | Authorised By: DL
label | Issue Date: 07.02.2025