## Table 1
Appendix A: Inspection Test Plan A1 – Earthworks A2 – Concrete Works A3 – Piling Works A4 – Pipeworks A5 – Mechanical Works A6 – Electrical Works
.
Appendix A1- Earthworks
ITEM | DESCRIPTION OF WORKS |  |  | POINT OF INSPECTION / TEST | [6 empty] | STANDARD / REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT | [7 empty] | STAGE / FREQUENCY | [5 empty] | RESPONSIBILITY |  |  |  |  | EVIDENCE |  | REMARKS
EARTH WORKS
1 | Site clearing |  |  | Area to be cleared Depth of grubbing Removal of topsoil | [6 empty] | - Refer to construction drawings - Approved method statement | [5 empty] | Survey equipment Tools to measure depth | [7 empty] | Entire site | [5 empty] | Contractor |  |  |  |  | Setting out plan Survey plan
2 | Excavation |  |  | Dimensional tolerance (depth) | [6 empty] | Width < 300mm than the dimensions shown on the drawings | [5 empty] | Tools to measure depth | [7 empty] | When required | [5 empty] | Contractor/ Project Manager |  |  |  |  | Survey plan
|  |  |  | Unsuitable material (If any) | [6 empty] | JKR/SPJ/2013-S2: Clause 2.2.1 (d) or JKR 20800-0183-14 Section B Cl. 5.2.3 | [5 empty] | Trial pit | [7 empty] | When required | [5 empty] | Contractor/ Project Manager |  |  |  |  | Material laboratory test
|  |  |  | Grading of replacement materials | [6 empty] | JKR/SPJ/2013-S2: Table 2.1 or JKR 20800-0183-14 Section B Cl. 5.7, Table B1 | [5 empty] | Particle Size Distribution (Gradation analysis) | [7 empty] | When required | [5 empty] | Contractor/ Project Manager |  |  |  |  | Material laboratory test
|  |  |  | Excavation of hard materials/ rock | [6 empty] | JKR/SPJ/2013-S2: Clause 2.2.1 (f) and (g) or JKR 20800-0183-14 Section B Cl. 5.2.5, | [5 empty] | Trial excavation | [7 empty] | When required | [5 empty] | Contractor/ Project Manager |  |  |  |  | Trial excavation record
|  |  |  | Rock blasting | [6 empty] | JKR/SPJ/2013-S2: Clause 2.2.3.8 or JKR 20800-0183-14 Section B Cl. 5.1.2 | [5 empty] | Trial blasting | [7 empty] | When required | [5 empty] | Contractor/ Project Manager |  |  |  |  | Trial blasting record
3 | Fill materials |  |  | Suitability of materials (1) | [6 empty] | JKR/SPJ/2013 - Cl. 2.2.4.1 and 2.2.4.2 or JKR 20800-0183-14 Section B Cl. 5.2.4 or Federal Aviation Administration (FAA) AC 150/5320-6E CI 205 | [5 empty] | Atterberg limit test | [7 empty] | One test/ 1500 m3 of the material to be used | [5 empty] | Contractor/ Project Manager |  |  |  |  | Material laboratory test
|  |  |  | Suitability of materials (2) | [6 empty] | JKR/SPJ/2013 - Cl. 2.2.4.1 and 2.2.4.2 or JKR 20800-0183-14 Section B Cl. 5.2.4 or Federal Aviation Administration (FAA) AC 150/5320-6E CI 205 | [5 empty] | Gradation analysis | [7 empty] | One test/ 1500 m3 of the material to be used | [5 empty] | Contractor/ Project Manager |  |  |  |  | Material laboratory test
|  |  |  | Suitability of materials (3) | [6 empty] | JKR/SPJ/2013 - Cl. 2.2.4.1 and 2.2.4.2 or JKR 20800-0183-14 Section B Cl. 5.2.4 or Federal Aviation Administration (FAA) AC 150/5320-6E CI 205 | [5 empty] | Compaction test (MS 1056) | [7 empty] | One test/ 1500 m3 of the material to be used | [5 empty] | Contractor/ Project Manager |  |  |  |  | Material laboratory test
|  |  |  | Suitability of materials (4) | [6 empty] | JKR/SPJ/2013 - Cl. 2.2.4.1 and 2.2.4.2 or JKR 20800-0183-14 Section B Cl. 5.2.4 or Federal Aviation Administration (FAA) AC 150/5320-6E CI 205 | [5 empty] | Soaked CBR test | [7 empty] | One test/ 1500 m3 of the material to be used | [5 empty] | Contractor/ Project Manager |  |  |  |  | Material laboratory test
|  |  |  | Suitability of materials (5) | [6 empty] | Federal Aviation Administration (FAA) AC 150/5320-6E CI 205 & ICAO A. Manual Part | [5 empty] | Plate Bearing Test | [13 empty] | Contractor/ Project Manager |  |  |  |  | Material laboratory test
4 | Slope Cutting |  |  | Area to be cut and trim | [6 empty] | Refer to construction drawing | [5 empty] | Survey equipment Measuring tape | [7 empty] | Before slope cutting | [5 empty] | Surveyor / Contractor |  |  |  |  | Setting out plan Surveyor peg point
|  |  |  | Safety Precaution | [6 empty] | JKR specification for occupational safety & Health in engineering construction | [5 empty] | Visual checking | [7 empty] | Before slope cutting | [5 empty] | Contractor | [6 empty] | Ensure nobody or property at the downstream of slope cutting
|  |  |  | Excavation - Dimension - Level - Line - Profile | [6 empty] | Refer to construction drawing | [5 empty] | Survey equipment Measuring devices | [7 empty] | Once slope cutting completed | [5 empty] | Contrator / Surveyor Consultant |  |  |  |  | Request for Inspection Form
|  |  |  | Compaction | [6 empty] | Refer to construction drawing Visual inspection | [5 empty] | Excavator | [7 empty] | Once after work completed | [5 empty] | Contractor / Consultant |  |  |  |  | Request for Inspection Form Compaction record
5 | Drainage |  |  | Drainage route Drain excavation and Slope alignment | [6 empty] | Refer to construction drawing Refer to construction drawing | [5 empty] | survey equipment Measuring tape | [7 empty] | Before start work | [5 empty] | Surveyor / Contractor |  |  |  |  | Setting our plan
|  |  |  | Drain invet level | [6 empty] | Refer to construction drawing Site Layout plan | [5 empty] | Survey equipment Level measuring devices | [18 empty] | Request for Inspection Form
|  |  |  | Belian pile | [6 empty] | Refer to construction drawing | [5 empty] | Excavator Measuring tape | [7 empty] | once during piling work | [5 empty] | Contractor Consultant |  |  |  |  | Pile Material inspection form Request for Inspection Form for piling work
|  |  |  | Cutting and bending of steel reinforcement | [6 empty] | Refer to construction drawing BS4449 | [13 empty] | Before fixing concreting | [5 empty] | Contractor
|  |  |  | Fixing of steel reinforcement to formwork | [6 empty] | Refer to construction drawing Comply design concrete cover Comply design drain width and depth | [5 empty] | Measuring tape | [13 empty] | Contractor / Consultant |  |  |  |  | Request for Inspection Form
6 | Slope Protection |  |  | Preparation of site Compaction | [6 empty] | Refer to construction drawing MS1056 SO approval | [5 empty] | Compaction and CBR test equipment | [7 empty] | once upon work done | [10 empty] | Request for inspection form
|  |  |  | Placement of Gabions Material | [6 empty] | BS1052:1980 JKR/SPJ/1988 sub-Section 3.6.2.1 | [19 empty] | Contractor / Consultant |  |  |  |  | Material inspection form
|  |  |  | Installation of Gabion Stone | [6 empty] | refer to construction drawing refer to construction drawing | [19 empty] | Contractor / Consultant Consultant |  |  |  |  | Request for inspection form
Appendix A2- Concrete Works
ITEM |  | DESCRIPTION OF WORKS |  |  | POINT OF INSPECTION/TEST |  |  |  |  | STANDARD/REQUIREMENT | [5 empty] | TOOLS/ EQUIPMENT |  |  |  | STAGE/ FREQUENCY |  |  |  |  | RESPONSIBILITY |  |  |  |  | EVIDENCE |  |  |  |  | REMARKS
CONCRETE WORKS
1 |  | CONCRETE MATERIALS |  |  | Manufacturers certificate of test. (types & composition of cement) |  |  |  |  | SIRIM approved cement | [9 empty] | Before mixing concrete and at change of supplier |  |  |  |  | Contractors/ Supplier |  |  |  |  | certificate
|  | Cement |  |  | Storage |  |  |  |  | Protected againt water
|  | Aggregates ( Fine and Course) |  |  | Approved Source., Aggregate test results |  |  |  |  | - Granite for water retaining structure - Limestone for non water retaining structure | [9 empty] | Before mixing concrete and at change of source/ supplier |  |  |  |  | Contractors/ Supplier |  |  |  |  | Aggregates test report
[5 empty] | Aggregates test results |  |  |  |  | Elongation, flakiness, clay slit content, soundness etc.
[5 empty] | Grading or Sieve Anaysis test results |  |  |  |  | Within Grading envelope
|  | Water |  |  | Source of water. |  |  |  |  | Approved source -clean, free chloride and sulphate | [9 empty] | Before mixing concrete and at change of soured/ producer/ supplier |  |  |  |  | Contractors/ Supplier |  |  |  |  | Sampling test
2 |  | STEEL REINFORCEMENT |  |  | Steel characteristic strength fy N/mm2 |  |  |  |  | As design for use in the construction drawings | [9 empty] | Before delivery to site / Initial, Ramdom testing |  |  |  |  | Contractors/ Supplier |  |  |  |  | Mill certificates, tensile test results
MS 146, BS 4461, MS 144, MS 145
[5 empty] | Storage |  |  |  |  | In clean and dry conditions | [9 empty] | Initial stage/ throughout. |  |  |  |  | Contractors/ Supplier
[5 empty] | Condition of steel reinforcement |  |  |  |  | Clean , free from rust, scalling, oil, grease, paint, dirt etc | [9 empty] | Before fixing and concreting. |  |  |  |  | Contractors/ Consultant |  |  |  |  | Request for inspection form
[5 empty] | Cutting and bending of steel reinforcement |  |  |  |  | As per construction drawings. and BS 4449 | [9 empty] | Before fixing and concreting. |  |  |  |  | Contractors
[5 empty] | Fixing of steel reinforcement to formwork |  |  |  |  | As per construction drawings | [9 empty] | Before concreting |  |  |  |  | Contractors/ consultant |  |  |  |  | Request for inspection form
Comply design concrete cover
BS 1052
[5 empty] | Welding of reinforcement |  |  |  |  | Welding carried out by certified welder | [14 empty] | Contractors
BS EN 1011 and BS EN 60974
3 |  | APPROVAL AND PRODUCTION OF CONCRETE MISTURE (Prescribed or designed concrete) |  |  | Concrete grade /strength or mixture |  |  |  |  | As required in construction drawing or Approved by consultant | [9 empty] | Initial stage or Regularly on production |  |  |  |  | Contractors/ supplier |  |  |  |  | - Consultant approval - Concrete testing from - Initial test results or comformity test or identity test, and /or Delivery order
[5 empty] | Cement content |  |  |  |  | JKR Building Specs
[5 empty] | Consistency / watercement ratio |  |  |  |  | Slump test / compacting test/ Vebe test/ flow test
[5 empty] | Admixtures |  |  |  |  | Prescribed concrete : CEM 1 only . No admixture
Designed concrete : All cement type + Admixture
4 |  | APPROVAL OF READY MIXED. |  |  | Supplier Information / Manufacturer certificate |  |  |  |  | Supplier name, Plant location, transportation duration, Plant's capacity production | [9 empty] | Initial Stage |  |  |  |  | Consultant |  |  |  |  | Manufacturers certificates and licencing.
[5 empty] | Mixing |  |  |  |  | All concrete materials mixed at plant (NO extra water/ admixtures added after leaving the plant) | [9 empty] | Regularly on production |  |  |  |  | Supplier
[5 empty] | Delivery |  |  |  |  | Delivery ticket and manufacturer's batching record
Check for grade, slump, temperature, Time < 2 hrs.
ITEM |  | DESCRIPTION OF WORKS |  |  | POINT OF INSPECTION/TEST |  |  |  |  | STANDARD/REQUIREMENT | [5 empty] | TOOLS/ EQUIPMENT |  |  |  | STAGE/ FREQUENCY |  |  |  |  | RESPONSIBILITY |  |  |  |  | EVIDENCE |  |  |  |  | REMARKS
CONCRETE WORKS
5 |  | CONCRETE TESTING (Compressive Strength : CUBES OR CYLINDER) |  |  | Initial test results |  |  |  |  | Samples: At least 3 specimens from each of 3 batches. (Average strength is used) | [9 empty] | Initial stage /change in material or specified requirement |  |  |  |  | Contractor/ Supplier |  |  |  |  | Record form |  |  |  |  | 1. EN 12390-2 (Curing) 2. Test result - average of 2 or more specimens made from 1 sample tested at same age. 3. Cube strength at 7 days 28-days compressive strength.
Average Compressive strength > fck of Table D8, D9 by adequate margin (2 x SD): (At least 6-12 N/mm2)
Historical data of batching plant can be used ( exceed target mean strength at 28 days)
[5 empty] | Conformity test results |  |  |  |  | Rate of sampling for accessing comformity : (Table D10), 35 test results for initial roduction or 35 test results ( within 12 months) for continuous production. | [9 empty] | Initial stage /change in material or specified requirement |  |  |  |  | Contractor
Test result from individual specimen or; average of 2 or more specimens made from 1 sample tested at 28 days.
Criteria Acceptance : Table D11
[5 empty] | Identity test |  |  |  |  | Rate of sampling and testing to EN 12350- 1 | [5 empty] | JKR/QC/B05/04 |  |  |  | Random on production. |  |  |  |  | Contractor
· critical structure : 1 sample per 10m3 or 10 batches
· slab/beam :1sample per 20m3 or 20 batches
· raft foundation/ mass concrete :1 sample per 50m3 or 50 batches
· minimum 2 samples each concreting day per grade/structure
· for designed mix : 4 samples (12 cubes) on first concreting day per grade and subsequently minimum 1 sample per source per day per grade
[5 empty] | Identity test for Slump and Flow test |  |  |  |  | Sampling and testing plan to comply with MS 26-1-1 (sampling),MS 26-1-2 (slump measurement),MS 26-1-5 (flow measurement) | [5 empty] | JKR/QC/B05/04 |  |  |  | Initial stage / ramdom on production. |  |  |  |  | Contractor |  |  |  |  | Record form
Slump measurement - Table D14, D15 , and MS 523:Part 1
Flow measurement - Annex B of MS 523- 2
ITEM |  | DESCRIPTION OF WORKS |  |  | POINT OF INSPECTION/TEST |  |  |  |  | STANDARD/REQUIREMENT | [5 empty] | TOOLS/ EQUIPMENT |  |  |  | STAGE/ FREQUENCY |  |  |  |  | RESPONSIBILITY |  |  |  |  | EVIDENCE |  |  |  |  | REMARKS
CONCRETE WORKS
6 |  | PLACEMENT OF CONCRETE |  |  | Site condition |  |  |  |  | Dry condition. No concreting in flowing water and underwater. | [9 empty] | Throughout |  |  |  |  | Contractor |  |  |  |  | Record form
[5 empty] | Placement and compaction |  |  |  |  | Time mixing and placement within 2 hrs., Temperature not exceed 36 deg C
Concrete dropped no exceed 1.5m high.
Compacting in layer 300 mm to 450 mm.only.
7 |  | FORMWORK AND SCALFOLDING |  |  | Design Drawings and method statement |  |  |  |  | Certified by Professional Engineer. If scaffolding is necessary, appoint competent scaffolder | [5 empty] | Design/shop drawings |  |  |  | Before installation. |  |  |  |  | Contractor/ Consultant |  |  |  |  | Drawings, calculation certificate
[5 empty] | Construction stage |  |  |  |  | Formwork and scalfolding in correct position, shape, profile and dimension (verticality, alignment and level), rigid and tight, clean. | [5 empty] | visual |  |  |  | Before and during concreting |  |  |  |  | Contractor
Finishes: Formed and unformed surface finish to various classes.
[5 empty] | Removal of formworks |  |  |  |  | When approval by consultant granted | [9 empty] | After min strength achieved. |  |  |  |  | Contractor
8 |  | SUPPORTING AND SPACER BLOCKS |  |  | size |  |  |  |  | NOT more than 50mm x50mm | [9 empty] | Throughout |  |  |  |  | Contractor
[5 empty] | strength |  |  |  |  | At least the same strength and material source's as the concrete to be poured (with nominal aggregates size = 10 mm) | [9 empty] | Throughout |  |  |  |  | Contractor
9 |  | CONSTRUCTION JOINTS |  |  | Location |  |  |  |  | As per drawings; or if not indicated in the drawings, Contractor may proposed with consultant approval | [9 empty] | Throughout |  |  |  |  | Contractor
[10 empty] | NOT allowed at toilet/wet area | [9 empty] | Throughout |  |  |  |  | Contractor
[5 empty] | Horizontal constructions joint |  |  |  |  | Placed 25mm gauge strip inside the forms along all exposed surface to ensure straight joint | [9 empty] | Throughout |  |  |  |  | Contractor
[5 empty] | Constructions joint for wall/column |  |  |  |  | Construct 75mm height of kicker (starter stub) monolithically with the base concrete | [9 empty] | Throughout |  |  |  |  | Contractor
Appendix A3- Piling Works
ITEM |  | DESCRIPTION OF WORKS |  | POINT OF INSPECTION / TEST |  |  |  | STANDARD / REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT |  |  |  |  | STAGE / FREQUENCY |  |  |  |  | RESPONSIBILITY |  |  |  |  | EVIDENCE |  |  |  |  | REMARKS
PILING WORKS - PRE CAST (DRIVEN/ JACKED - IN PILE)
1 |  | Piling equipments (Type/ hammer weight/ pressure requirement) |  | - Approval of piling equipments - Approved method statement |  |  |  | Refer to construction drawings & Method statement | [5 empty] | Visual inspection |  |  |  |  | Prior to pile installation |  |  |  |  | Contractor/ Consultant |  |  |  |  | Equipment specification & calibration records
2 |  | Set criteria (End bearing piles) |  | Set criteria calculation submitted by contractor and approval from consultant |  |  |  | Refer approved set criteria calculation | [5 empty] | Hiley's formulae (Driven pile) or equivalent approved by consultant/ Correlation chart (Jacked-in) |  |  |  |  | Prior to pile installation |  |  |  |  | Contractor/ Consultantr |  |  |  |  | Approved Set calculation |  |  |  |  | Hiley set calculation
3 |  | Piles |  | Physical condition of piles (Type/dimension/ shoes/ defects) |  |  |  | Refer to construction drawings & approved pile catalogue/drawing | [5 empty] | Visual inspection |  |  |  |  | 3 specimens for each batch of delivery or every 40 piles whichever is larger |  |  |  |  | Contractor/ Consultant |  |  |  |  | Record and defects marking |  |  |  |  | To submit pile concrete cube test result
4 |  | Installation of piles |  | Number of preliminary pile |  |  |  | Refer to construction drawings | [5 empty] | Contract document |  |  |  |  | Prior to installation of preliminary pile |  |  |  |  | Contractor/ surveyor/ Consultant |  |  |  |  | As built drawing & piling records
|  |  |  | Pile deviation |  |  |  | < 75mm | [5 empty] | Survey equipments |  |  |  |  | Every pile | [9 empty] | As built drawing/Survey record/ pins/ pegs/ markers
|  |  |  | Verticality of pile |  |  |  | < 1:75 | [5 empty] | Survey equipments/plumb bob | [14 empty] | As built drawing
|  |  |  | Pile extension | [9 empty] | Visual inspection |  |  |  |  | Every extension of pile | [9 empty] | Welding records
|  |  |  | Termination of pile |  |  |  | Set criteria (end bearing pile)/penetration depth as specified in the drawings (friction pile) | [5 empty] | Visual inspection |  |  |  |  | Every pile | [9 empty] | Pile driving record
5 |  | Pile testing (Static load test) |  | Test method |  |  |  | Refer to construction drawings, Method Statement | [5 empty] | Document review |  |  |  |  | Prior to commencement of testing |  |  |  |  | Contractor/ Consultant |  |  |  |  | Method statement
|  |  |  | Number of test |  |  |  | Refer to construction drawings | [5 empty] | Contract document & Method Statement |  |  |  |  | Prior to commencement of testing | [9 empty] | Load test report
|  |  |  | Testing procedures |  |  |  | Approved method statements | [5 empty] | Document review |  |  |  |  | Every test pile | [9 empty] | Method statement
|  |  |  | Allowable capacity of pile (Acceptance of piles) |  |  |  | Residual settlement after removal of test load < (D/120+4)mm or 6.5mm, whichever the lowest - Refer calculation method | [5 empty] | Load Settlement Graph |  |  |  |  | Every test pipe | [9 empty] | Load test report
Total settlement under design load < 12.5mm - Refer calculation method
Total settlement under 2xWL < 38mm Or 10% x pile diameter; whichever is the lower value. - Refer calculation method
ITP/Pil‐1
Appendix A4- Pipe Works
ITEM | DESCRIPTION OF WORKS |  |  | POINT OF INSPECTION / TEST |  |  |  |  | STANDARD/REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT | [5 empty] | STAGE/ FREQUENCY |  |  |  |  | RESPONSIBILITY | [5 empty] | EVIDENCE |  |  |  |  | REMARKS
Pipeworks/Waterworks
1 | HDPE Pipe Laying Work |  |  | Material & Production Acceptance Test |  |  |  |  | Manufacturer standard / MS1058 Malaysia Standard for portable water HDPE pipes | [5 empty] | Factory QC test ort / Production certificate | [5 empty] | Before product dispatch out from factory |  |  |  |  | Contractor | [5 empty] | Certificate of Approval from SWA
|  |  |  | Material Delivery Acceptance |  |  |  |  | Specification / Contract construction drawing | [5 empty] | Delivery order/ Catalogue | [5 empty] | Upon receiving material |  |  |  |  | Consultant Contractor | [5 empty] | Delivery order
|  |  |  | Storage |  |  |  |  | General in clean, flat and away from Heat / Flaming | [5 empty] | Physical inspection | [5 empty] | Upon each bath of material receiveing |  |  |  |  | Contractor | [5 empty] | Material Inspection Form Deivery order
|  |  |  | Pipe Laying work |  |  |  |  | Contract construction drawing / Pipeline profile drawing | [5 empty] | Measuring tape / Vernier Caliper | [5 empty] | Before pipe Jointing |  |  |  |  | Consultant Contractor | [5 empty] | Request for Inspection Form, Delivery order, surveyor indentified route
|  |  |  | Pipe Jointing and Laying |  |  |  |  | Specificaton / Manufacturer recomendation / Approved Method statement / Pipeline profile drawing | [5 empty] | Automatic / Semi auto HDPE butt welding machine | [5 empty] | Every joint |  |  |  |  | Consultant Contractor | [5 empty] | Welding / pipe layer certificate
|  |  |  | Trenching and backfilling |  |  |  |  | Constract construction drawing / JKR General specification for water main construction | [5 empty] | Visual Visual, measuring tape | [5 empty] | Every 200-300 meter interval |  |  |  |  | Consultant Contractor | [5 empty] | Request for Inspection Form
|  |  |  | Isolation Valve, Washour and Air valve installation |  |  |  |  | Contract construction drawing / Pipeline profile drawing | [5 empty] | Visual, measuring tape | [5 empty] | Before installation |  |  |  |  | Contractor | [5 empty] | Request for Inspection Form
|  |  |  | Sectional Pressure Test |  |  |  |  | Specificaton / Contract requirement / Approved Mehod statement - 1.5 x working pressure | [5 empty] | pressure pump, pressure gauge, timer | [5 empty] | Sectional / Test once upon pipework completed |  |  |  |  | Consultant Contractor | [5 empty] | Form-CS-W-3 (water main pressure and leakage test form)
|  |  |  | General System Test for Water Work |  |  |  |  | General in clean / Manufacturer Specification (Control valve setting) | [5 empty] | Physical inspection, pressure gauge | [5 empty] | Overall test prior water supply to WTP |  |  |  |  | Contractor | [5 empty] | Request for Inspection Form and Approval Chit
ITP/pipeworks-1
Appendix A5- Mechanical Works
ITEM |  | DESCRIPTION OF WORKS |  | POINT OF INSPECTION / TEST |  |  | STANDARD/REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT |  |  |  |  | STAGE/ FREQUENCY |  |  |  |  | RESPONSIBILITY |  |  |  |  | EVIDENCE | [5 empty] | REMARKS
HORIZONTAL SPLIT CASING PUMP / VERTICAL MULTI STAGE PUMP INSTALLATION
1 |  | Horizontal Split Casing / Vertical Multistage Pump |  | Submission of material for approval |  |  | 1. Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 3. Contract Document. | [10 empty] | Before manufacturing |  |  |  |  | Consultant/ Contractor/ S.O |  |  |  |  | Material approval
|  |  |  | Factory acceptance test |  |  | Refer contract specification | [10 empty] | Prior of delivery to the site. |  |  |  |  | Consultant/ Manufacturer/ S.O |  |  |  |  | Testing report | [5 empty] | For motor >100kW
|  |  |  | Material on site inspection. |  |  | To conform as per approved material. | [5 empty] | Visual |  |  |  |  | Upon delivery at site. Once for each delivery. |  |  |  |  | Consultant / Contractor |  |  |  |  | Material Inspection Form
|  |  |  | Pump installation |  |  | 1. Manufacturer installation manual 2. Approved method statement / Shop drawing | [5 empty] | - Measuring tape & spirit level - visual |  |  |  |  | Upon installation |  |  |  |  | Consultant/ Contractor |  |  |  |  | Request for inspection form
|  |  |  | Non-shrink grouting |  |  | Manufacturer specification | [5 empty] | spirit level |  |  |  |  | Upon installation of QDC |  |  |  |  | Contractor | [10 empty] | Stud-bolt with lock nut
|  |  |  | Pump allignment |  |  | Manufacturer specification | [5 empty] | Feeler gauge, Dial gauge and shim plate |  |  |  |  | Upon base frame grouting |  |  |  |  | Contractor |  |  |  |  | - M&E pump allignment form - To be done by skilled personnel
|  |  |  | Discharge pipe & bracket installation |  |  | Approved method statement / Shop drawing | [5 empty] | Plumb bob/ spirit level |  |  |  |  | Upon installation |  |  |  |  | Consultant/ Contractor |  |  |  |  | Request for inspection form
|  |  |  | LCP installation |  |  | Approved method statement / Shop drawing | [10 empty] | Upon installation |  |  |  |  | Consultant/ Contractor |  |  |  |  | Request for inspection form
|  |  |  | Pump cable insulation resistance test | [8 empty] | Insulation Tester |  |  |  |  | Upon completion of cable laying |  |  |  |  | Contractor / consultant |  |  |  |  | M&E Cable Insulation Test Form
|  |  |  | Setting of pump protection parameters and value |  |  | Manufacturer recommendation | [5 empty] | Computer / Instrument manual |  |  |  |  | Upon energized of control panle |  |  |  |  | contractor |  |  |  |  | M&E testing and commissioning form
|  |  |  | Functioning test during testing & commissioning |  |  | 1. Design Requirement. 2. Specification 3. Functioning. | [10 empty] | Upon completion of other test above. Once for each board. |  |  |  |  | Contractor / Consultant / S.O'R |  |  |  |  | M&E pre- Commissioning & T&C Test Form
ITEM |  | DESCRIPTION OF WORKS |  | POINT OF INSPECTION / TEST |  |  | STANDARD/REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT |  |  |  |  | STAGE/ FREQUENCY |  |  |  |  | RESPONSIBILITY |  |  |  |  | EVIDENCE | [5 empty] | REMARKS
PIPE AND FITTINGS INSTALLATION
1 |  | Piping |  | Material Aceptance |  |  | Specification / Approved shop drawing/ Malaysia Standard / British Standard / Specifcation: i.e Flange, welding & joint method subject to pipe size. | [5 empty] | Delivery Order |  |  |  |  | Upon receiving material |  |  |  |  | Consultant/ Contractor/ S.O |  |  |  |  | - Material approval -Delivery Order
|  |  |  | Installation (above ground and underground) |  |  | Approved shop drawing | [5 empty] | Visual, measuring tape | [9 empty] | Consultant/ Contractor | [10 empty] | i. Above ground application - Pipe coated with zinc chromate coating ii. Underground application - Pipe coated with bituminous with lime coating
|  |  |  | Pressure Testing |  |  | Pressure test 1.5 working pressure for 48 hrs and pressure drop shall not below 10% from the pressure test | [5 empty] | Pressure gauge & pressure pump |  |  |  |  | Section by section Every section |  |  |  |  | Consultant/ Contractor
2 |  | Valve and fittings |  | Material Aceptance Installation |  |  | Specification / Approved shop drawing/ Malaysia Standard / British Standard / Specifcation: i.e Pressure rating | [5 empty] | Visual |  |  |  |  | Before manufacturing |  |  |  |  | Consultant/ Contractor/ S.O
|  |  |  | Material on site inspection. |  |  | To conform as per approved material. | [5 empty] | Visual |  |  |  |  | Upon delivery at site. Once for each delivery. |  |  |  |  | Consultant / Contractor |  |  |  |  | Material Inspection Form
|  |  |  | Installation |  |  | Approved shop drawing | [10 empty] | Upon installation |  |  |  |  | Consultant/ Contractor |  |  |  |  | Request for inspection form | [5 empty] | to check all bolt and nuts shall be HDG high
3 |  | Pipe Collar weld / Spigot weld |  | Welding joint inspection |  |  | - Approved method statement / Shop drawing - Welding to be performed by skilled welder | [5 empty] | Visual |  |  |  |  | Randomly check for every 10 welding joints |  |  |  |  | Contractor/ Consultant |  |  |  |  | Request for inspection form | [5 empty] | Physical chek on welding joint
|  |  |  | Pressure test |  |  | - Approved method statement - Pressure test for > 16 bars for 15 minutes | [5 empty] | Pressure gauge & Nitrogen gas |  |  |  |  | every joint |  |  |  |  | Contractor/ Consultant |  |  |  |  | M&E pressure testing form
Appendix A6- Electrical Works
ITEM | DESCRIPTION OF WORKS |  | POINT OF INSPECTION / TEST |  |  | STANDARD / REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT |  |  |  | STAGE/ FREQUENCY | [5 empty] | RESPONSIBILITY |  |  |  |  | EVIDENCE | [5 empty] | REMARKS
LOW VOLTAGE : ELECTRICAL BOARDS
1 | MSB / SSB / DB / AMF Board / LCP/CP |  | Submission for Circuit diagram for approval. |  |  | 1. Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 3. Contract Document. | [9 empty] | Before manufacturing of the boards. | [5 empty] | Contractor/ Consultant |  |  |  |  | Panel approval from consultant
|  |  | Factory Acceptance Test a) Functional test. b) Pressure Test / Injection Test - Exclude control panel, DB c) Insulation Resistance Test 1000 VDC. - Exclude control panel, DB |  |  | Refer contract specification 1. Approved Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 1. Approved Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 3. Contract Document. 1. Approved Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 3. Contract Document. | [5 empty] | LV Pressure Test Set Insulation Resistance Test |  |  |  | Prior of delivery to the site. After completion of installation work Prior of delivery to the site. Prior of delivery to the site. Once for each board. | [5 empty] | Contractor/ Consultant / S.O'R |  |  |  |  | Manufacturer Test Report Manufacturer Test Report Manufacturer Test Report | [5 empty] | For MSB only For MSB and Sub- switchboard For MSB and Sub- switchboard
|  |  | Material on site inspection |  |  | 1. Approved Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 3. Contract Document. | [5 empty] | Measuring Devices (Caliper, Measuring Tape, etc.). |  |  |  | Every Panel delivered to site | [5 empty] | Contractor/ Consultant |  |  |  |  | Material Inspection Form
|  |  | Installation of MSB / SSB / DB / AMF / PFC |  |  | 1. Approved Shop Drawing. 2. Approved Method Statement. | [9 empty] | In-progress and upon completion of installation. Once for each board. | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Installation of Earthing System for LV Board. |  |  | 1. Approved Shop Drawing. 2. Specification | [5 empty] | Earth Tester. |  |  |  | Upon completion of installation. Once for each installation. | [5 empty] | Contractor/ Consultant |  |  |  |  | M&E Pre- Commissioning Test
|  |  | Setting of Protection Relay - For MSB, AMF and SSB only |  |  | Setting value from designer for O/C, E/F | [5 empty] | Secondary Relay Test Set. |  |  |  | Upon completion of installation for all works at the board. Once for each relay. | [5 empty] | Contractor/ Tester/ SESCO |  |  |  |  | TEST REPORT | [5 empty] | Done by third party tester
|  |  | Functional test during Testing & Commissioning Session. |  |  | 1. Design Requirement. 2. Specification 3. Functioning. | [9 empty] | Upon completion of other test above. Once for each board. | [5 empty] | Contractor/ Consultant / S.O'R |  |  |  |  | M&E pre- Commissioning & T&C Test Form
ITEM | DESCRIPTION OF WORKS |  | POINT OF INSPECTION / TEST |  |  | STANDARD / REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT |  |  |  | STAGE/ FREQUENCY | [5 empty] | RESPONSIBILITY |  |  |  |  | EVIDENCE | [5 empty] | REMARKS
2 | Variable Speed Drive (VFD) |  | Submission for material approval |  |  | 1. Technical specification 2. Contract documents | [9 empty] | Before manufacturing/ Once for each material. | [5 empty] | Contractor/ Consultant/ S.O
|  |  | Material on site inspection. |  |  | To conform as per approved material. | [5 empty] | Visual |  |  |  | Upon delivery at site. Once for each delivery. | [5 empty] | Consultant/ Contractor |  |  |  |  | Material Inspection Form
|  |  | VFD installation - Mounting method - Air ventilation - accessible for trouble shooting |  |  | 1. Manufacturer installation manual 2. Approved method statement / Shop drawing | [5 empty] | Visual, measuring tape, spirit level |  |  |  | During and after installation | [5 empty] | Contractor |  |  |  |  | Request for inspection Form
|  |  | Cable termination and insulation resistance test |  |  | Manufacturer installation manual | [5 empty] | Insulation & Continuity Tester |  |  |  | Upon completion of cable Termination | [5 empty] | Contractor/ Consultant |  |  |  |  | M&E Cable Insulation Test Form
|  |  | Motor ID & information and drive parameters setting - To be done by trained and competant personnel |  |  | Manufacturer recommendation | [5 empty] | Computer /Drive firmware manual |  |  |  | Upon energized of control panle | [5 empty] | Contractor | [10 empty] | Including Pump ID run
|  |  | Functioning test during testing & commissioning session |  |  | 1. Design Requirement. 2. Specification 3. Functioning. | [9 empty] | Upon completion of other test above. Once for each board. | [5 empty] | Contractor/ Consultant / S.O'R |  |  |  |  | M&E pre- Commissioning & T&C Test Form
ITEM | DESCRIPTION OF WORKS |  | POINT OF INSPECTION / TEST |  |  | STANDARD / REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT |  |  |  | STAGE/ FREQUENCY | [5 empty] | RESPONSIBILITY |  |  |  |  | EVIDENCE | [5 empty] | REMARKS
LOW VOLTAGE : WIRING SYSTEM & UNDERGROUND CABLE
1 | Light Fittings/Fan |  | Submission of material for approval |  |  | Technical specification | [9 empty] | Before material delivery at site. Once for each material. | [5 empty] | Contractor/ Consultant
|  |  | Material on site inspection. |  |  | To conform as per approved material. | [9 empty] | Upon delivery at site. Once for each delivery. | [5 empty] | Contractor/ Consultant |  |  |  |  | Material Inspection Form
|  |  | Installation of conduit, trunking and accessories. |  |  | Approved Shop Drawing | [9 empty] | - In-progress and upon completion of installation. - Once for each zone/ section/ | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Installation of final circuit wiring. |  |  | Specification (L-S1). | [9 empty] | In-progress and upon completion of installation. Once for each zone / section / floor. | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspeciton Form
|  |  | Insulation resistance test | [8 empty] | Insulation Tester |  |  |  | Upon completion of cable laying | [5 empty] | Contractor/ Consultant |  |  |  |  | M&E Cable Insulation Test Form
|  |  | Polarity test. |  |  | Load connected correctly. | [5 empty] | Insulation & Continuity Tester, polarity tester |  |  |  | Upon completion of wiring work. Once for each circuit. | [5 empty] | Contractor/ Consultant
|  |  | Installation of fittings. |  |  | - Approved method Statement - Specifications (L-S1) | [5 empty] | Measuring devices. |  |  |  | Upon completion of fitting installations. Once for each building | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Functional test. |  |  | Functional. | [5 empty] | Measuring devices. |  |  |  | Upon completion of other test above. | [5 empty] | Contractor/ Consultant |  |  |  |  | M&E T&C Form
2 | Switch Socket Outlet (SSO) |  | Submission of material for approval |  |  | Technical specification | [5 empty] | Measuring devices. |  |  |  | Before material delivery at site. Once for each material. | [5 empty] | Contractor/ Consultant
|  |  | Material on site inspection |  |  | To conform as per approved material | [5 empty] | Measuring devices. |  |  |  | Upon delivery at site. Once for each delivery. | [5 empty] | Contractor/ Consultant |  |  |  |  | Material Inspection Form
|  |  | Installation of conduit, trunking and accessories. |  |  | - Approved shop drawing - Specification (L-S1). | [5 empty] | Measuring devices. |  |  |  | In-progress and upon completion of installation. Once for each zone / section / floor. | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Installation of final circuit wiring. |  |  | Specification (L-S1). | [5 empty] | continuity meter |  |  |  | In-progress and upon completion of installation. Once for each zone / section / floor. | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Insulation resistance test | [8 empty] | Insulation Tester |  |  |  | Upon completion of cable laying | [5 empty] | Contractor/ Consultant |  |  |  |  | M&E Cable Insulation Test Form
|  |  | Polarity test. |  |  | Load connected correctly. | [5 empty] | Insulation,Continui ty Tester, polarity |  |  |  | Upon completion of wiring work. Once for each circuit. | [5 empty] | Contractor/ Consultant
|  |  | Installation of fittings. |  |  | - Approved method Statement - Specifications | [5 empty] | Measuring devices. |  |  |  | Upon completion of fitting installations. Once for each zone / section / floor. | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Functional test. |  |  | Functional. | [5 empty] | Measuring devices. |  |  |  | Upon completion of other test above. Once for each zone / section / floor. | [5 empty] | Contractor/ Consultant |  |  |  |  | M&E testing & commissioning Form
3 | Three Phase Point / Submain Cables |  | Submission of material for approval |  |  | Technical specification | [5 empty] | Measuring devices. |  |  |  | Before material delivery at site. Once for each material. | [5 empty] | Contractor/ Consultant |  |  |  |  | Material Approval
ITEM | DESCRIPTION OF WORKS |  | POINT OF INSPECTION / TEST |  |  | STANDARD / REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT |  |  |  | STAGE/ FREQUENCY | [5 empty] | RESPONSIBILITY |  |  |  |  | EVIDENCE | [5 empty] | REMARKS
|  |  | Material on site inspection. |  |  | To conform as per approved material. | [5 empty] | Measuring devices. |  |  |  | Upon delivery at site. Once for each delivery. | [5 empty] | Contractor/ Consultant |  |  |  |  | Material Inspection Form
|  |  | Installation of conduit, trunking and accessories. |  |  | As per approve shop drawings | [5 empty] | Measuring devices. |  |  |  | In-progress and upon completion of installation. Once for each zone / section / floor. | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Installation of cables. |  |  | - Specification (L-S1). - Approved method statement. | [5 empty] | Visual |  |  |  | In-progress and upon completion of installation. Once for each zone / section / floor. | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Insulation resistance test | [8 empty] | - Insulation & Continuity Tester. - Insulation Tester. |  |  |  | Upon completion of continuity test. Once for each circuit. | [5 empty] | Contractor/ Consultant |  |  |  |  | M&E Cable Insulation Test Form
|  |  | Phase sequence test. |  |  | Check phase sequence terminated correctly. | [5 empty] | Phase sequence tester, continuity tester |  |  |  | Upon completion of cable insulation test. Once for each circuit. | [5 empty] | Contractor/ Consultant | [10 empty] | Marking on cable to identify each cable identity
4 | Underground Cable |  | Submission of material for approval |  |  | Technical specification | [5 empty] | Measuring devices. |  |  |  | Before material delivery at site. Once for each material. | [5 empty] | Contractor/ Consultant |  |  |  |  | Material Approval
|  |  | Material on site inspection. |  |  | To conform as per approved material. | [5 empty] | Measuring devices. |  |  |  | Upon delivery at site. Once for each delivery. | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Installation of cables. |  |  | - Specification (L-S3). - Approved method statement. | [5 empty] | Visual |  |  |  | In-progress and upon completion of installation. Once for each zone / section. | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Continuity test. | [8 empty] | Insulation & Continuity Tester. |  |  |  | Upon completion of cable installation. Once for each cable. | [5 empty] | Contractor/ Consultant
|  |  | Insulation resistance test | [8 empty] | Insulation & Continuity Tester. |  |  |  | Upon completion of cable continuity test. Once for each | [5 empty] | Contractor/ Consultant |  |  |  |  | M&E Cable Insulation Test Form
|  |  | Phase sequence test. |  |  | Check phase sequence terminated correctly. | [5 empty] | Phase sequence tester / Continuity test |  |  |  | Upon completion of continuity test. Once for each circuit. | [5 empty] | Contractor/ Consultant | [10 empty] | Marking on cable to identify each cable identity
ITEM | DESCRIPTION OF WORKS |  | POINT OF INSPECTION / TEST |  |  | STANDARD / REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT |  |  |  | STAGE/ FREQUENCY | [5 empty] | RESPONSIBILITY |  |  |  |  | EVIDENCE | [5 empty] | REMARKS
LOW VOLTAGE : LIGHTNING PROTECTION SYSTEM
1 | Lightning Protection System |  | Submission of material approval |  |  | - Technical specification - M&E drawing | [9 empty] | Before material delivery at site / Once for each material | [5 empty] | Contractor/ Consultant |  |  |  |  | Material Approval
|  |  | Material on site inspection |  |  | As per material approval | [9 empty] | Upon delivery at site / Once for each delivery | [5 empty] | Contractor/ Consultant |  |  |  |  | Material Inspection Form
|  |  | Inspection on air termination system installation |  |  | - Air terminals or vertical finials of annealed copper tape 25mm x 3mm or other approved material. - Fixing bracket intervals < 500mm (metallic / non-metallic roof). - Air termination rods min. 300mm (L), 16mm dia. with | [5 empty] | Measuring Equipment |  |  |  | In-progress and upon completion of installation / Once for each block | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Inspection on down conductor system installation |  |  | - Annealed copper tape 25mm x 3mm or other approved material. - Properly clamped down conductor to structural reinforcing bar at 1m intervals. | [5 empty] | Measuring Equipment |  |  |  | In-progress and upon completion of installation / Once for each down conductor | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Inspection on test joint installation |  |  | - Joints and bonds by copper clamps or exothermic welding or brazing. - Height at 2.5m from finished floor level. - Copper clamp overlapping >20mm. - PVC casing for exposed down conductor between test joint and ground. - Flash counter height at 2.0m from floor finished level. | [5 empty] | Measuring Equipment |  |  |  | In-progress and upon completion of installation / Once for each test joint | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Resistance test : 1. Earth Electrode 2. Earth Termination |  |  | Entire system combine resistance < 5 Ω | [5 empty] | Earth Tester |  |  |  | Upon completion of installation / Once for each block | [5 empty] | Contractor/ Consultant |  |  |  |  | - M&E Pre- Commissioning Test Form - T&C Test Form
ITEM | DESCRIPTION OF WORKS |  | POINT OF INSPECTION / TEST |  |  | STANDARD / REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT |  |  |  | STAGE/ FREQUENCY | [5 empty] | RESPONSIBILITY |  |  |  |  | EVIDENCE | [5 empty] | REMARKS
LOW VOLTAGE : STANDBY GENERATOR SET
1 | Standby Generator Set. |  | Submission for material approval |  |  | Technical specification | [9 empty] | Before manufacturing/ Once for each material. | [5 empty] | Contractor/ Consultant/ S.O |  |  |  |  | Material Approval
|  |  | Factory Acceptance Test (Routine Test) : a) Visual Inspection b) Cranking Test |  |  | - Manufacturers Specification. - Design requirement. a) Works test. b) Fulfilling to conditioning of Engine Protective Devices. c) Sudden power increase/decrease. - Approved shop drawing for generator set. - To confirm as per material approved. | [5 empty] | - Inductive Load- bank at pf 0.8 lagging. |  |  |  | Before material delivery at site / Once for each material. During testing and commissioning. | [5 empty] | Contractor/ Consultant/ S.O'R/ Manufacturer |  |  |  |  | Manufacturer Test Report | [5 empty] | For generator >100kW
|  |  | Material on site inspection |  |  | To comform as per approved material | [5 empty] | Visual Inspection |  |  |  | Upon delivery at site. Each delivery. | [5 empty] | Contractor/ Consultant |  |  |  |  | Material Inspection Form
|  |  | Generator set room requirement. |  |  | 1. Shop drawing 2. Specification | [9 empty] | By the end of construction or after generator installation | [5 empty] | Contractor/ Consultant |  |  |  |  | - Subject to consultant approval - Shop drawing approval
|  |  | Inspection on installation works. |  |  | 1. Manufacturers specification manual. 2. Approved Shop drawing. 3. Specification (L-S5). | [5 empty] | measuring tape , spirit level |  |  |  | - During installation and completion of installation. - Throughout the installation. | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for Inspection Form
|  |  | Noise level measurement |  |  | - Jabatan Alam Sekitar (JAS). - <80 dBA Sound Pressure Level. Measured 1 meter away from the generator room. | [5 empty] | Sound Meter. |  |  |  | Upon completion of acoustic treatment. During testing and commissioning. | [5 empty] | Contractor/ Consultant |  |  |  |  | M&E pre- Commissioning & T&C Test Form
|  |  | Battery installation and connection |  |  | 1. Manufacturer installation manual 2. Connection shall done by competent personnel | [5 empty] | Ampere meter / DC volt etre |  |  |  | Upon installation | [5 empty] | Contractor/ Consultant |  |  |  |  | Request for inspection form
|  |  | Setting of Generator set's protection parameters and value |  |  | Manufacturer recommendation | [5 empty] | Computer / Equipment manual |  |  |  | Upon energized of control panel | [5 empty] | Contractor/ Consultant |  |  |  |  | Manufacturer service/ test report
|  |  | Generator start up |  |  | 1. Design Requirement. 2. Specification 3. Manufacturer guidline | [5 empty] | Voltmeter, sound meter and ampere meter |  |  |  | Upon parameter setting done | [5 empty] | Contractor/ Manufacturer |  |  |  |  | Manufacturer service/ test report
|  |  | Functioning test during testing & commissioning session |  |  | 1. Design Requirement. 2. Specification 3. Functioning. | [5 empty] | Voltmeter, sound meter and ampere meter |  |  |  | - Upon completion of other test above. - Once for each board. | [5 empty] | Contractor/ Consultant / S.O'R |  |  |  |  | M&E pre- Commissioning & T&C Test Form
ITEM | DESCRIPTION OF WORKS |  | POINT OF INSPECTION / TEST |  |  | STANDARD / REQUIREMENT | [5 empty] | TOOLS / EQUIPMENT |  |  |  | STAGE/ FREQUENCY | [5 empty] | RESPONSIBILITY |  |  |  |  | EVIDENCE | [5 empty] | REMARKS
2 | Acoustic |  | Acoustic treatment system installation |  |  | 1. Manufacturer installation manual 2. Approved method statement / Shop drawing | [5 empty] | Measuring tape & spirit level |  |  |  | Upon installation | [5 empty] | Contractor |  |  |  |  | Request for inspection form | [5 empty] | To check air inlet and outlet arrow / rotation
3 | LV Cabling |  | Material submission approval |  |  | - Contract Document. - Technical Submittal (i.e : catalogue, brand & model). | [9 empty] | Prior to delivery to site. / Once for each type of material | [5 empty] | Contractor/ Consultant |  |  |  |  | Material approval
|  |  | Material on site inspection |  |  | - Manufacturer's Specification. - Design Requirement. - Technical Specification | [9 empty] | Upon delivery at site. / Once for each material / delivery | [5 empty] | Contractor/Consultant |  |  |  |  | Material Inspection Form
|  |  | Cable installation |  |  | - Approved Method Statement - Approve shop drawing - Technical Specification | [9 empty] | In-progress and upon completion of installation. / Once for each installation | [5 empty] | Contractor/Consultant |  |  |  |  | Request for Inspection Form
|  |  | Continuity Test |  |  | - Approved Method Statement - Specification | [9 empty] | Upon Completion of cable installation / Once for each cable | [5 empty] | Contractor/Consultant |  |  |  |  | M&E Cable Insulation Test Form
|  |  | Insulation Resistance Test |  |  | Ohm > 5 M ohms. | [5 empty] | 1. Insulation & Continuity Tester. 2. Insulation |  |  |  | Upon Completion of continuity test / Once for each cable | [5 empty] | Contractor |  |  |  |  | M&E Cable Insulation Test Form