## Table 1
Appendix A: Inspection Test Plan
A1 – Earthworks A2 – Concrete Works A3 – Piling Works A4 – Pipeworks A5 – Mechanical Works A6 – Electrical Works
.
Appendix A1- Earthworks
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD / REQUIREMENT | TOOLS / EQUIPMENT | STAGE / FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
EARTH WORKS
1 | Site clearing | Area to be cleared Depth of grubbing Removal of topsoil | - Refer to construction drawings - Approved method statement | Survey equipment Tools to measure depth | Entire site | Contractor | Setting out plan Survey plan
2 | Excavation | Dimensional tolerance (depth) | Width < 300mm than the dimensions shown on the drawings | Tools to measure depth | When required | Contractor/ Project Manager | Survey plan
|  | Unsuitable material (If any) | JKR/SPJ/2013-S2: Clause 2.2.1 (d) or JKR 20800-0183-14 Section B Cl. 5.2.3 | Trial pit | When required |  | Material laboratory test
|  | Grading of replacement materials | JKR/SPJ/2013-S2: Table 2.1 or JKR 20800-0183-14 Section B Cl. 5.7, Table B1 | Particle Size Distribution (Gradation analysis) | When required |  | Material laboratory test
|  | Excavation of hard materials/ rock | JKR/SPJ/2013-S2: Clause 2.2.1 (f) and (g) or JKR 20800-0183-14 Section B Cl. 5.2.5, | Trial excavation | When required |  | Trial excavation record
|  | Rock blasting | JKR/SPJ/2013-S2: Clause 2.2.3.8 or JKR 20800-0183-14 Section B Cl. 5.1.2 | Trial blasting | When required |  | Trial blasting record
3 | Fill materials | Suitability of materials | JKR/SPJ/2013 - Cl. 2.2.4.1 and 2.2.4.2 or JKR 20800-0183-14 Section B Cl. 5.2.4 or Federal Aviation Administration (FAA) AC 150/5320-6E CI 205 | Atterberg limit test | One test/ 1500 m3 of the material to be used | Contractor/ Project Manager | Material laboratory test
Gradation analysis
Compaction test (MS 1056)
Soaked CBR test
|  |  | Federal Aviation Administration (FAA) AC 150/5320-6E CI 205 & ICAO A. Manual Part | Plate Bearing Test
4 | Slope Cutting | Area to be cut and trim | Refer to construction drawing | Survey equipment Measuring tape | Before slope cutting | Surveyor / Contractor | Setting out plan Surveyor peg point
|  | Safety Precaution | JKR specification for occupational safety & Health in engineering construction | Visual checking | Before slope cutting | Contractor |  | Ensure nobody or property at the downstream of slope cutting
|  | Excavation | Refer to construction drawing | Survey equipment | Once slope cutting completed | Contrator / Surveyor | Request for Inspection Form
|  | - Dimension - Level - Line - Profile |  | Measuring devices |  | Consultant
|  | Compaction | Refer to construction drawing Visual inspection | Excavator | Once after work completed | Contractor / Consultant | Request for Inspection Form Compaction record

## Table 2
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD / REQUIREMENT | TOOLS / EQUIPMENT | STAGE / FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
EARTH WORKS
5 | Drainage | Drainage route Drain excavation and Slope alignment | Refer to construction drawing Refer to construction drawing | survey equipment Measuring tape | Before start work | Surveyor / Contractor | Setting our plan
|  | Drain invet level | Refer to construction drawing Site Layout plan | Survey equipment Level measuring devices |  |  | Request for Inspection Form
|  | Belian pile | Refer to construction drawing | Excavator Measuring tape | once during piling work | Contractor Consultant | Pile Material inspection form Request for Inspection Form for piling work
|  | Cutting and bending of steel reinforcement | Refer to construction drawing BS4449 |  | Before fixing concreting | Contractor
|  | Fixing of steel reinforcement to formwork | Refer to construction drawing Comply design concrete cover Comply design drain width and depth | Measuring tape |  | Contractor / Consultant | Request for Inspection Form
6 | Slope Protection | Preparation of site Compaction | Refer to construction drawing MS1056 SO approval | Compaction and CBR test equipment | once upon work done |  | Request for inspection form
|  | Placement of Gabions Material | BS1052:1980 JKR/SPJ/1988 sub-Section 3.6.2.1 |  |  | Contractor / Consultant | Material inspection form
|  | Installation of Gabion Stone | refer to construction drawing refer to construction drawing |  |  | Contractor / Consultant Consultant | Request for inspection form
Appendix A2- Concrete Works

## Table 3
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION/TEST | STANDARD/REQUIREMENT | TOOLS/ EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
CONCRETE WORKS
1 | CONCRETE MATERIALS | Manufacturers certificate of test. (types & composition of cement) | SIRIM approved cement |  | Before mixing concrete and at change of supplier | Contractors/ Supplier | certificate
| Cement | Storage | Protected againt water
| Aggregates ( Fine and Course) | Approved Source., Aggregate test results | - Granite for water retaining structure - Limestone for non water retaining structure |  | Before mixing concrete and at change of source/ supplier | Contractors/ Supplier | Aggregates test report
|  | Aggregates test results | Elongation, flakiness, clay slit content, soundness etc.
|  | Grading or Sieve Anaysis test results | Within Grading envelope
| Water | Source of water. | Approved source -clean, free chloride and sulphate |  | Before mixing concrete and at change of soured/ producer/ supplier | Contractors/ Supplier | Sampling test
2 | STEEL REINFORCEMENT | Steel characteristic strength fy N/mm2 | As design for use in the construction drawings |  | Before delivery to site / Initial, Ramdom testing | Contractors/ Supplier | Mill certificates, tensile test results
MS 146, BS 4461, MS 144, MS 145
|  | Storage | In clean and dry conditions |  | Initial stage/ throughout. | Contractors/ Supplier
|  | Condition of steel reinforcement | Clean , free from rust, scalling, oil, grease, paint, dirt etc |  | Before fixing and concreting. | Contractors/ Consultant | Request for inspection form
|  | Cutting and bending of steel reinforcement | As per construction drawings. and BS 4449 |  | Before fixing and concreting. | Contractors
|  | Fixing of steel reinforcement to formwork | As per construction drawings |  | Before concreting | Contractors/ consultant | Request for inspection form
Comply design concrete cover
BS 1052
|  | Welding of reinforcement | Welding carried out by certified welder |  |  | Contractors
BS EN 1011 and BS EN 60974
3 | APPROVAL AND PRODUCTION OF CONCRETE MISTURE (Prescribed or designed concrete) | Concrete grade /strength or mixture | As required in construction drawing or Approved by consultant |  | Initial stage or Regularly on production | Contractors/ supplier | - Consultant approval - Concrete testing from - Initial test results or comformity test or identity test, and /or Delivery order
|  | Cement content | JKR Building Specs
|  | Consistency / watercement ratio | Slump test / compacting test/ Vebe test/ flow test
|  | Admixtures | Prescribed concrete : CEM 1 only . No admixture
Designed concrete : All cement type + Admixture
4 | APPROVAL OF READY MIXED. | Supplier Information / Manufacturer certificate | Supplier name, Plant location, transportation duration, Plant's capacity production |  | Initial Stage | Consultant | Manufacturers certificates and licencing.
|  | Mixing | All concrete materials mixed at plant (NO extra water/ admixtures added after leaving the plant) |  | Regularly on production | Supplier
|  | Delivery | Delivery ticket and manufacturer's batching record
Check for grade, slump, temperature, Time < 2 hrs.
CONCRETE WORKS
5 | CONCRETE TESTING (Compressive Strength : CUBES OR CYLINDER) | Initial test results | Samples: At least 3 specimens from each of 3 batches. (Average strength is used) |  | Initial stage /change in material or specified requirement | Contractor/ Supplier | Record form | 1. EN 12390-2 (Curing) 2. Test result - average of 2 or more specimens made from 1 sample tested at same age. 3. Cube strength at 7 days 28-days compressive strength.
Average Compressive strength > fck of Table D8, D9 by adequate margin (2 x SD): (At least 6-12 N/mm2)
Historical data of batching plant can be used ( exceed target mean strength at 28 days)
|  | Conformity test results | Rate of sampling for accessing comformity : (Table D10), 35 test results for initial roduction or 35 test results ( within 12 months) for continuous production. |  | Initial stage /change in material or specified requirement | Contractor
Test result from individual specimen or; average of 2 or more specimens made from 1 sample tested at 28 days.
Criteria Acceptance : Table D11
|  | Identity test | Rate of sampling and testing to EN 12350- 1 | JKR/QC/B05/04 | Random on production. | Contractor
· critical structure : 1 sample per 10m3 or 10 batches
· slab/beam :1sample per 20m3 or 20 batches
· raft foundation/ mass concrete :1 sample per 50m3 or 50 batches
· minimum 2 samples each concreting day per grade/structure
· for designed mix : 4 samples (12 cubes) on first concreting day per grade and subsequently minimum 1 sample per source per day per grade
|  | Identity test for Slump and Flow test | Sampling and testing plan to comply with MS 26-1-1 (sampling),MS 26-1-2 (slump measurement),MS 26-1-5 (flow measurement) | JKR/QC/B05/04 | Initial stage / ramdom on production. | Contractor | Record form
Slump measurement - Table D14, D15 , and MS 523:Part 1
Flow measurement - Annex B of MS 523- 2

## Table 4
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION/TEST | STANDARD/REQUIREMENT | TOOLS/ EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
CONCRETE WORKS
6 | PLACEMENT OF CONCRETE | Site condition | Dry condition. No concreting in flowing water and underwater. |  | Throughout | Contractor | Record form
|  | Placement and compaction | Time mixing and placement within 2 hrs., Temperature not exceed 36 deg C
Concrete dropped no exceed 1.5m high.
Compacting in layer 300 mm to 450 mm.only.
7 | FORMWORK AND SCALFOLDING | Design Drawings and method statement | Certified by Professional Engineer. If scaffolding is necessary, appoint competent scaffolder | Design/shop drawings | Before installation. | Contractor/ Consultant | Drawings, calculation certificate
|  | Construction stage | Formwork and scalfolding in correct position, shape, profile and dimension (verticality, alignment and level), rigid and tight, clean. | visual | Before and during concreting | Contractor
Finishes: Formed and unformed surface finish to various classes.
|  | Removal of formworks | When approval by consultant granted |  | After min strength achieved. | Contractor
8 | SUPPORTING AND SPACER BLOCKS | size | NOT more than 50mm x50mm |  | Throughout | Contractor
|  | strength | At least the same strength and material source's as the concrete to be poured (with nominal aggregates size = 10 mm) |  | Throughout | Contractor
9 | CONSTRUCTION JOINTS | Location | As per drawings; or if not indicated in the drawings, Contractor may proposed with consultant approval |  | Throughout | Contractor
|  |  | NOT allowed at toilet/wet area |  | Throughout | Contractor
|  | Horizontal constructions joint | Placed 25mm gauge strip inside the forms along all exposed surface to ensure straight joint |  | Throughout | Contractor
|  | Constructions joint for wall/column | Construct 75mm height of kicker (starter stub) monolithically with the base concrete |  | Throughout | Contractor
Appendix A3- Piling Works

## Table 5
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD / REQUIREMENT | TOOLS / EQUIPMENT | STAGE / FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
PILING WORKS - PRE CAST (DRIVEN/ JACKED - IN PILE)
1 | Piling equipments (Type/ hammer weight/ pressure requirement) | - Approval of piling equipments - Approved method statement | Refer to construction drawings & Method statement | Visual inspection | Prior to pile installation | Contractor/ Consultant | Equipment specification & calibration records
2 | Set criteria (End bearing piles) | Set criteria calculation submitted by contractor and approval from consultant | Refer approved set criteria calculation | Hiley's formulae (Driven pile) or equivalent approved by consultant/ Correlation chart (Jacked-in) | Prior to pile installation | Contractor/ Consultantr | Approved Set calculation | Hiley set calculation
3 | Piles | Physical condition of piles (Type/dimension/ shoes/ defects) | Refer to construction drawings & approved pile catalogue/drawing | Visual inspection | 3 specimens for each batch of delivery or every 40 piles whichever is larger | Contractor/ Consultant | Record and defects marking | To submit pile concrete cube test result
4 | Installation of piles | Number of preliminary pile | Refer to construction drawings | Contract document | Prior to installation of preliminary pile | Contractor/ surveyor/ Consultant | As built drawing & piling records
|  | Pile deviation | < 75mm | Survey equipments | Every pile |  | As built drawing/Survey record/ pins/ pegs/ markers
|  | Verticality of pile | < 1:75 | Survey equipments/plumb bob |  |  | As built drawing
|  | Pile extension |  | Visual inspection | Every extension of pile |  | Welding records
|  | Termination of pile | Set criteria (end bearing pile)/penetration depth as specified in the drawings (friction pile) | Visual inspection | Every pile |  | Pile driving record
5 | Pile testing (Static load test) | Test method | Refer to construction drawings, Method Statement | Document review | Prior to commencement of testing | Contractor/ Consultant | Method statement
|  | Number of test | Refer to construction drawings | Contract document & Method Statement | Prior to commencement of testing |  | Load test report
|  | Testing procedures | Approved method statements | Document review | Every test pile |  | Method statement
|  | Allowable capacity of pile (Acceptance of piles) | Residual settlement after removal of test load < (D/120+4)mm or 6.5mm, whichever the lowest - Refer calculation method | Load Settlement Graph | Every test pipe |  | Load test report
Total settlement under design load < 12.5mm - Refer calculation method
Total settlement under 2xWL < 38mm Or 10% x pile diameter; whichever is the lower value. - Refer calculation method
ITP/Pil‐1
Appendix A4- Pipe Works

## Table 6
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD/REQUIREMENT | TOOLS / EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
Pipeworks/Waterworks
1 | HDPE Pipe Laying Work | Material & Production Acceptance Test | Manufacturer standard / MS1058 Malaysia Standard for portable water HDPE pipes | Factory QC test ort / Production certificate | Before product dispatch out from factory | Contractor | Certificate of Approval from SWA
|  | Material Delivery Acceptance | Specification / Contract construction drawing | Delivery order/ Catalogue | Upon receiving material | Consultant Contractor | Delivery order
|  | Storage | General in clean, flat and away from Heat / Flaming | Physical inspection | Upon each bath of material receiveing | Contractor | Material Inspection Form Deivery order
|  | Pipe Laying work | Contract construction drawing / Pipeline profile drawing | Measuring tape / Vernier Caliper | Before pipe Jointing | Consultant Contractor | Request for Inspection Form, Delivery order, surveyor indentified route
|  | Pipe Jointing and Laying | Specificaton / Manufacturer recomendation / Approved Method statement / Pipeline profile drawing | Automatic / Semi auto HDPE butt welding machine | Every joint | Consultant Contractor | Welding / pipe layer certificate
|  | Trenching and backfilling | Constract construction drawing / JKR General specification for water main construction | Visual Visual, measuring tape | Every 200-300 meter interval | Consultant Contractor | Request for Inspection Form
|  | Isolation Valve, Washour and Air valve installation | Contract construction drawing / Pipeline profile drawing | Visual, measuring tape | Before installation | Contractor | Request for Inspection Form
|  | Sectional Pressure Test | Specificaton / Contract requirement / Approved Mehod statement - 1.5 x working pressure | pressure pump, pressure gauge, timer | Sectional / Test once upon pipework completed | Consultant Contractor | Form-CS-W-3 (water main pressure and leakage test form)
|  | General System Test for Water Work | General in clean / Manufacturer Specification (Control valve setting) | Physical inspection, pressure gauge | Overall test prior water supply to WTP | Contractor | Request for Inspection Form and Approval Chit
ITP/pipeworks-1
Appendix A5- Mechanical Works

## Table 7
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD/REQUIREMENT | TOOLS / EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
HORIZONTAL SPLIT CASING PUMP / VERTICAL MULTI STAGE PUMP INSTALLATION
1 | Horizontal Split Casing / Vertical Multistage Pump | Submission of material for approval | 1. Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 3. Contract Document. |  | Before manufacturing | Consultant/ Contractor/ S.O | Material approval
|  | Factory acceptance test | Refer contract specification |  | Prior of delivery to the site. | Consultant/ Manufacturer/ S.O | Testing report | For motor >100kW
|  | Material on site inspection. | To conform as per approved material. | Visual | Upon delivery at site. Once for each delivery. | Consultant / Contractor | Material Inspection Form
|  | Pump installation | 1. Manufacturer installation manual 2. Approved method statement / Shop drawing | - Measuring tape & spirit level - visual | Upon installation | Consultant/ Contractor | Request for inspection form
|  | Non-shrink grouting | Manufacturer specification | spirit level | Upon installation of QDC | Contractor |  | Stud-bolt with lock nut
|  | Pump allignment | Manufacturer specification | Feeler gauge, Dial gauge and shim plate | Upon base frame grouting | Contractor | - M&E pump allignment form - To be done by skilled personnel
|  | Discharge pipe & bracket installation | Approved method statement / Shop drawing | Plumb bob/ spirit level | Upon installation | Consultant/ Contractor | Request for inspection form
|  | LCP installation | Approved method statement / Shop drawing |  | Upon installation | Consultant/ Contractor | Request for inspection form
|  | Pump cable insulation resistance test |  | Insulation Tester | Upon completion of cable laying | Contractor / consultant | M&E Cable Insulation Test Form
|  | Setting of pump protection parameters and value | Manufacturer recommendation | Computer / Instrument manual | Upon energized of control panle | contractor | M&E testing and commissioning form
|  | Functioning test during testing & commissioning | 1. Design Requirement. 2. Specification 3. Functioning. |  | Upon completion of other test above. Once for each board. | Contractor / Consultant / S.O'R | M&E pre- Commissioning & T&C Test Form

## Table 8
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD/REQUIREMENT | TOOLS / EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
PIPE AND FITTINGS INSTALLATION
1 | Piping | Material Aceptance | Specification / Approved shop drawing/ Malaysia Standard / British Standard / Specifcation: i.e Flange, welding & joint method subject to pipe size. | Delivery Order | Upon receiving material | Consultant/ Contractor/ S.O | - Material approval -Delivery Order
|  | Installation (above ground and underground) | Approved shop drawing | Visual, measuring tape |  | Consultant/ Contractor |  | i. Above ground application - Pipe coated with zinc chromate coating ii. Underground application - Pipe coated with bituminous with lime coating
|  | Pressure Testing | Pressure test 1.5 working pressure for 48 hrs and pressure drop shall not below 10% from the pressure test | Pressure gauge & pressure pump | Section by section Every section | Consultant/ Contractor
2 | Valve and fittings | Material Aceptance Installation | Specification / Approved shop drawing/ Malaysia Standard / British Standard / Specifcation: i.e Pressure rating | Visual | Before manufacturing | Consultant/ Contractor/ S.O
|  | Material on site inspection. | To conform as per approved material. | Visual | Upon delivery at site. Once for each delivery. | Consultant / Contractor | Material Inspection Form
|  | Installation | Approved shop drawing |  | Upon installation | Consultant/ Contractor | Request for inspection form | to check all bolt and nuts shall be HDG high
3 | Pipe Collar weld / Spigot weld | Welding joint inspection | - Approved method statement / Shop drawing - Welding to be performed by skilled welder | Visual | Randomly check for every 10 welding joints | Contractor/ Consultant | Request for inspection form | Physical chek on welding joint
|  | Pressure test | - Approved method statement - Pressure test for > 16 bars for 15 minutes | Pressure gauge & Nitrogen gas | every joint | Contractor/ Consultant | M&E pressure testing form
Appendix A6- Electrical Works

## Table 9
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD / REQUIREMENT | TOOLS / EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
LOW VOLTAGE : ELECTRICAL BOARDS
1 | MSB / SSB / DB / AMF Board / LCP/CP | Submission for Circuit diagram for approval. | 1. Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 3. Contract Document. |  | Before manufacturing of the boards. | Contractor/ Consultant | Panel approval from consultant
|  | Factory Acceptance Test a) Functional test. b) Pressure Test / Injection Test - Exclude control panel, DB c) Insulation Resistance Test 1000 VDC. - Exclude control panel, DB | Refer contract specification 1. Approved Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 1. Approved Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 3. Contract Document. 1. Approved Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 3. Contract Document. | LV Pressure Test Set Insulation Resistance Test | Prior of delivery to the site. After completion of installation work Prior of delivery to the site. Prior of delivery to the site. Once for each board. | Contractor/ Consultant / S.O'R | Manufacturer Test Report Manufacturer Test Report Manufacturer Test Report | For MSB only For MSB and Sub- switchboard For MSB and Sub- switchboard
|  | Material on site inspection | 1. Approved Shop Drawing. 2. Technical Submittal (i.e: Catalogue, Brand & Model). 3. Contract Document. | Measuring Devices (Caliper, Measuring Tape, etc.). | Every Panel delivered to site | Contractor/ Consultant | Material Inspection Form
|  | Installation of MSB / SSB / DB / AMF / PFC | 1. Approved Shop Drawing. 2. Approved Method Statement. |  | In-progress and upon completion of installation. Once for each board. | Contractor/ Consultant | Request for Inspection Form
|  | Installation of Earthing System for LV Board. | 1. Approved Shop Drawing. 2. Specification | Earth Tester. | Upon completion of installation. Once for each installation. | Contractor/ Consultant | M&E Pre- Commissioning Test
|  | Setting of Protection Relay - For MSB, AMF and SSB only | Setting value from designer for O/C, E/F | Secondary Relay Test Set. | Upon completion of installation for all works at the board. Once for each relay. | Contractor/ Tester/ SESCO | TEST REPORT | Done by third party tester
|  | Functional test during Testing & Commissioning Session. | 1. Design Requirement. 2. Specification 3. Functioning. |  | Upon completion of other test above. Once for each board. | Contractor/ Consultant / S.O'R | M&E pre- Commissioning & T&C Test Form

## Table 10
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD / REQUIREMENT | TOOLS / EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
2 | Variable Speed Drive (VFD) | Submission for material approval | 1. Technical specification 2. Contract documents |  | Before manufacturing/ Once for each material. | Contractor/ Consultant/ S.O
|  | Material on site inspection. | To conform as per approved material. | Visual | Upon delivery at site. Once for each delivery. | Consultant/ Contractor | Material Inspection Form
|  | VFD installation - Mounting method - Air ventilation - accessible for trouble shooting | 1. Manufacturer installation manual 2. Approved method statement / Shop drawing | Visual, measuring tape, spirit level | During and after installation | Contractor | Request for inspection Form
|  | Cable termination and insulation resistance test | Manufacturer installation manual | Insulation & Continuity Tester | Upon completion of cable Termination | Contractor/ Consultant | M&E Cable Insulation Test Form
|  | Motor ID & information and drive parameters setting - To be done by trained and competant personnel | Manufacturer recommendation | Computer /Drive firmware manual | Upon energized of control panle | Contractor |  | Including Pump ID run
|  | Functioning test during testing & commissioning session | 1. Design Requirement. 2. Specification 3. Functioning. |  | Upon completion of other test above. Once for each board. | Contractor/ Consultant / S.O'R | M&E pre- Commissioning & T&C Test Form

## Table 11
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD / REQUIREMENT | TOOLS / EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
LOW VOLTAGE : WIRING SYSTEM & UNDERGROUND CABLE
1 | Light Fittings/Fan | Submission of material for approval | Technical specification |  | Before material delivery at site. Once for each material. | Contractor/ Consultant
|  | Material on site inspection. | To conform as per approved material. |  | Upon delivery at site. Once for each delivery. | Contractor/ Consultant | Material Inspection Form
|  | Installation of conduit, trunking and accessories. | Approved Shop Drawing |  | - In-progress and upon completion of installation. - Once for each zone/ section/ | Contractor/ Consultant | Request for Inspection Form
|  | Installation of final circuit wiring. | Specification (L-S1). |  | In-progress and upon completion of installation. Once for each zone / section / floor. | Contractor/ Consultant | Request for Inspeciton Form
|  | Insulation resistance test |  | Insulation Tester | Upon completion of cable laying | Contractor/ Consultant | M&E Cable Insulation Test Form
|  | Polarity test. | Load connected correctly. | Insulation & Continuity Tester, polarity tester | Upon completion of wiring work. Once for each circuit. | Contractor/ Consultant
|  | Installation of fittings. | - Approved method Statement - Specifications (L-S1) | Measuring devices. | Upon completion of fitting installations. Once for each building | Contractor/ Consultant | Request for Inspection Form
|  | Functional test. | Functional. | Measuring devices. | Upon completion of other test above. | Contractor/ Consultant | M&E T&C Form
2 | Switch Socket Outlet (SSO) | Submission of material for approval | Technical specification | Measuring devices. | Before material delivery at site. Once for each material. | Contractor/ Consultant
|  | Material on site inspection | To conform as per approved material | Measuring devices. | Upon delivery at site. Once for each delivery. | Contractor/ Consultant | Material Inspection Form
|  | Installation of conduit, trunking and accessories. | - Approved shop drawing - Specification (L-S1). | Measuring devices. | In-progress and upon completion of installation. Once for each zone / section / floor. | Contractor/ Consultant | Request for Inspection Form
|  | Installation of final circuit wiring. | Specification (L-S1). | continuity meter | In-progress and upon completion of installation. Once for each zone / section / floor. | Contractor/ Consultant | Request for Inspection Form
|  | Insulation resistance test |  | Insulation Tester | Upon completion of cable laying | Contractor/ Consultant | M&E Cable Insulation Test Form
|  | Polarity test. | Load connected correctly. | Insulation,Continui ty Tester, polarity | Upon completion of wiring work. Once for each circuit. | Contractor/ Consultant
|  | Installation of fittings. | - Approved method Statement - Specifications | Measuring devices. | Upon completion of fitting installations. Once for each zone / section / floor. | Contractor/ Consultant | Request for Inspection Form
|  | Functional test. | Functional. | Measuring devices. | Upon completion of other test above. Once for each zone / section / floor. | Contractor/ Consultant | M&E testing & commissioning Form
3 | Three Phase Point / Submain Cables | Submission of material for approval | Technical specification | Measuring devices. | Before material delivery at site. Once for each material. | Contractor/ Consultant | Material Approval
|  | Material on site inspection. | To conform as per approved material. | Measuring devices. | Upon delivery at site. Once for each delivery. | Contractor/ Consultant | Material Inspection Form
|  | Installation of conduit, trunking and accessories. | As per approve shop drawings | Measuring devices. | In-progress and upon completion of installation. Once for each zone / section / floor. | Contractor/ Consultant | Request for Inspection Form
|  | Installation of cables. | - Specification (L-S1). - Approved method statement. | Visual | In-progress and upon completion of installation. Once for each zone / section / floor. | Contractor/ Consultant | Request for Inspection Form
|  | Insulation resistance test |  | - Insulation & Continuity Tester. - Insulation Tester. | Upon completion of continuity test. Once for each circuit. | Contractor/ Consultant | M&E Cable Insulation Test Form
|  | Phase sequence test. | Check phase sequence terminated correctly. | Phase sequence tester, continuity tester | Upon completion of cable insulation test. Once for each circuit. | Contractor/ Consultant |  | Marking on cable to identify each cable identity
4 | Underground Cable | Submission of material for approval | Technical specification | Measuring devices. | Before material delivery at site. Once for each material. | Contractor/ Consultant | Material Approval
|  | Material on site inspection. | To conform as per approved material. | Measuring devices. | Upon delivery at site. Once for each delivery. | Contractor/ Consultant | Request for Inspection Form
|  | Installation of cables. | - Specification (L-S3). - Approved method statement. | Visual | In-progress and upon completion of installation. Once for each zone / section. | Contractor/ Consultant | Request for Inspection Form
|  | Continuity test. |  | Insulation & Continuity Tester. | Upon completion of cable installation. Once for each cable. | Contractor/ Consultant
|  | Insulation resistance test |  | Insulation & Continuity Tester. | Upon completion of cable continuity test. Once for each | Contractor/ Consultant | M&E Cable Insulation Test Form
|  | Phase sequence test. | Check phase sequence terminated correctly. | Phase sequence tester / Continuity test | Upon completion of continuity test. Once for each circuit. | Contractor/ Consultant |  | Marking on cable to identify each cable identity

## Table 12
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD / REQUIREMENT | TOOLS / EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
LOW VOLTAGE : LIGHTNING PROTECTION SYSTEM
1 | Lightning Protection System | Submission of material approval | - Technical specification - M&E drawing |  | Before material delivery at site / Once for each material | Contractor/ Consultant | Material Approval
|  | Material on site inspection | As per material approval |  | Upon delivery at site / Once for each delivery | Contractor/ Consultant | Material Inspection Form
|  | Inspection on air termination system installation | - Air terminals or vertical finials of annealed copper tape 25mm x 3mm or other approved material. - Fixing bracket intervals < 500mm (metallic / non-metallic roof). - Air termination rods min. 300mm (L), 16mm dia. with | Measuring Equipment | In-progress and upon completion of installation / Once for each block | Contractor/ Consultant | Request for Inspection Form
|  | Inspection on down conductor system installation | - Annealed copper tape 25mm x 3mm or other approved material. - Properly clamped down conductor to structural reinforcing bar at 1m intervals. | Measuring Equipment | In-progress and upon completion of installation / Once for each down conductor | Contractor/ Consultant | Request for Inspection Form
|  | Inspection on test joint installation | - Joints and bonds by copper clamps or exothermic welding or brazing. - Height at 2.5m from finished floor level. - Copper clamp overlapping >20mm. - PVC casing for exposed down conductor between test joint and ground. - Flash counter height at 2.0m from floor finished level. | Measuring Equipment | In-progress and upon completion of installation / Once for each test joint | Contractor/ Consultant | Request for Inspection Form
|  | Resistance test : 1. Earth Electrode 2. Earth Termination | Entire system combine resistance < 5 Ω | Earth Tester | Upon completion of installation / Once for each block | Contractor/ Consultant | - M&E Pre- Commissioning Test Form - T&C Test Form

## Table 13
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD / REQUIREMENT | TOOLS / EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
LOW VOLTAGE : STANDBY GENERATOR SET
1 | Standby Generator Set. | Submission for material approval | Technical specification |  | Before manufacturing/ Once for each material. | Contractor/ Consultant/ S.O | Material Approval
|  | Factory Acceptance Test (Routine Test) : a) Visual Inspection b) Cranking Test | - Manufacturers Specification. - Design requirement. a) Works test. b) Fulfilling to conditioning of Engine Protective Devices. c) Sudden power increase/decrease. - Approved shop drawing for generator set. - To confirm as per material approved. | - Inductive Load- bank at pf 0.8 lagging. | Before material delivery at site / Once for each material. During testing and commissioning. | Contractor/ Consultant/ S.O'R/ Manufacturer | Manufacturer Test Report | For generator >100kW
|  | Material on site inspection | To comform as per approved material | Visual Inspection | Upon delivery at site. Each delivery. | Contractor/ Consultant | Material Inspection Form
|  | Generator set room requirement. | 1. Shop drawing 2. Specification |  | By the end of construction or after generator installation | Contractor/ Consultant | - Subject to consultant approval - Shop drawing approval
|  | Inspection on installation works. | 1. Manufacturers specification manual. 2. Approved Shop drawing. 3. Specification (L-S5). | measuring tape , spirit level | - During installation and completion of installation. - Throughout the installation. | Contractor/ Consultant | Request for Inspection Form
|  | Noise level measurement | - Jabatan Alam Sekitar (JAS). - <80 dBA Sound Pressure Level. Measured 1 meter away from the generator room. | Sound Meter. | Upon completion of acoustic treatment. During testing and commissioning. | Contractor/ Consultant | M&E pre- Commissioning & T&C Test Form
|  | Battery installation and connection | 1. Manufacturer installation manual 2. Connection shall done by competent personnel | Ampere meter / DC volt etre | Upon installation | Contractor/ Consultant | Request for inspection form
|  | Setting of Generator set's protection parameters and value | Manufacturer recommendation | Computer / Equipment manual | Upon energized of control panel | Contractor/ Consultant | Manufacturer service/ test report
|  | Generator start up | 1. Design Requirement. 2. Specification 3. Manufacturer guidline | Voltmeter, sound meter and ampere meter | Upon parameter setting done | Contractor/ Manufacturer | Manufacturer service/ test report
|  | Functioning test during testing & commissioning session | 1. Design Requirement. 2. Specification 3. Functioning. | Voltmeter, sound meter and ampere meter | - Upon completion of other test above. - Once for each board. | Contractor/ Consultant / S.O'R | M&E pre- Commissioning & T&C Test Form

## Table 14
ITEM | DESCRIPTION OF WORKS | POINT OF INSPECTION / TEST | STANDARD / REQUIREMENT | TOOLS / EQUIPMENT | STAGE/ FREQUENCY | RESPONSIBILITY | EVIDENCE | REMARKS
2 | Acoustic | Acoustic treatment system installation | 1. Manufacturer installation manual 2. Approved method statement / Shop drawing | Measuring tape & spirit level | Upon installation | Contractor | Request for inspection form | To check air inlet and outlet arrow / rotation
3 | LV Cabling | Material submission approval | - Contract Document. - Technical Submittal (i.e : catalogue, brand & model). |  | Prior to delivery to site. / Once for each type of material | Contractor/ Consultant | Material approval
|  | Material on site inspection | - Manufacturer's Specification. - Design Requirement. - Technical Specification |  | Upon delivery at site. / Once for each material / delivery | Contractor/Consultant | Material Inspection Form
|  | Cable installation | - Approved Method Statement - Approve shop drawing - Technical Specification |  | In-progress and upon completion of installation. / Once for each installation | Contractor/Consultant | Request for Inspection Form
|  | Continuity Test | - Approved Method Statement - Specification |  | Upon Completion of cable installation / Once for each cable | Contractor/Consultant | M&E Cable Insulation Test Form
|  | Insulation Resistance Test | Ohm > 5 M ohms. | 1. Insulation & Continuity Tester. 2. Insulation | Upon Completion of continuity test / Once for each cable | Contractor | M&E Cable Insulation Test Form