## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
86b33e55-1984-4416-84d4-063fcfd184b2 | checklist | ITP - 111 - Wastewater PE Rev C | itp | ITP - 111 - Wastewater PE |  | 679f9c4b-cf06-4096-8321-0757015ce709
3b41d634-1d3d-43ef-8adb-d3a04dbe5dd6 | section | SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
08e8669c-e5b0-46ab-a310-d0b3ff3aea44 | checkpoint | 1.1 - Extent of Line Setout
aeb8fe9d-d48e-5604-9ca5-d70c9b4597e4 | note | Acceptance / Conformance Criteria - Ensure line and level of wastewater has been marked out and agreed with Engineer in accordance with the drawings.
d21255b2-6816-50dc-b8f4-459b2151f44f | note | ○ Identify any clashes before construction.
3d3b87ed-e4cd-50fa-9e31-08f983c0d421 | note | Standard / Specification - Design Drawings
720275bd-215a-5100-a7a1-2754617f1004 | note | Verifying Document - ITP Sign Off
cc93520a-80a8-5d4d-9c7d-25a872dad2cd | note | Frequency - Prior to Construction & Every Revision of IFC Drgs / Data
ba4bbf44-cd17-5f0c-815b-8c0c65caed81 | note | Verification Activity: Activity - M
38e93665-158d-5659-b3f8-ddc3d2b316d2 | note | Verification Activity: By - PE
d25d3c93-d075-455e-9dc0-43d4af373de6 | checkpoint | 1.2 - Environmental Protection
04a63200-d53f-58f1-b0ce-2b68e546e1e8 | note | Acceptance / Conformance Criteria - Install Erosion Sediment Control measures in line with PWRBSS ESCP plans
2b2bf356-5daa-5447-b802-9aa436557030 | note | ○ Inspect, monitor, and maintain ESCP measures weekly and immediately before & after significant weather events
7eab1015-f905-59f6-959e-7b08f783c1d7 | note | Standard / Specification - Project ESCP Plans
dea900ca-7bbd-5239-8969-f85b9506a37e | note | Verifying Document - ITP Sign Off
5e08a5b5-fac3-5b35-af40-54fe54e19ac7 | note | Frequency - Prior to Construction
12705b6d-c86c-537b-9cb9-e52b92fd4ce6 | note | ○ Inspect, Monitor, and Maintain Weekly and immediately before and after significant weather events
98afff49-518c-564b-9ef6-fcb3158309de | note | Verification Activity: Activity - M
f07025db-49e3-56db-9c67-abadbe7b1e2d | note | Verification Activity: By - PE
dd01c6c2-4558-4cd7-82ad-a54f9af241fc | checkpoint | 1.3 - Stakeholder
50ea45da-5b18-55e2-aa74-02b41df97537 | note | Acceptance / Conformance Criteria - Inform stakeholders of upcoming works
3aeb4497-bcf3-54dd-8ebe-8b18d396bd14 | note | ○ Agree plans for maintaining access to properties during construction with landowners
53a1f713-9b56-5c03-9dbc-7acc224e0ae1 | note | Standard / Specification - Project Stakeholder Management Plan
b79b003f-2a38-558b-a246-4934244b3892 | note | Verifying Document - ITP Sign Off
2ee25f6b-3088-5d69-baf7-8d7e5e0b189b | note | Frequency - Prior to Construction with continue updates throughout the works
699a8c5e-1e14-5648-845c-2ed4649baa4e | note | Verification Activity: Activity - M
6cda8349-52f5-58d4-a2ef-4ee5d814d206 | note | Verification Activity: By - PE
652b07a0-288f-4b6c-83e7-b1142f207412 | checkpoint | 1.4 - Permits
a5052d35-33aa-56ec-bc23-42f7666866e6 | note | Acceptance / Conformance Criteria - Permit to Dig must be in place before any ground breaking activity commences, incl. trenching, driving waratahs or survey pegs, and topsoil strip.
d97c8b42-7d55-5a44-b0a9-19477bff931d | note | ○ Permit to Dig will be based on BBO existing Services Drawings, Before U Dig Plans , potholing by the project, CAT & Genny survey, and visual inspections.
f9ae2df0-077c-5b2a-a588-4c0829bbb1fc | note | ○ All known services must be clearly marked on site and briefed to the workforce.
ef3c7362-e75c-5927-bbe6-23d51b0e1afc | note | Standard / Specification - Section 2.2.10 Project Specification
8c79bfc5-8c9d-5ad4-9bd1-0230ac798635 | note | Verifying Document - Ground Disturbance Permit DN-ZH-FM043.1
14f7f7b3-b603-538c-ab5b-15e2c448400a | note | Frequency - Prior to Construction
82892767-4adb-53d3-b8f6-c5391a5c4c13 | note | ○ Reviewed and Reissued weekly or when site conditions change
456380ec-b30b-5f69-8ac2-1d6045db2482 | note | Verification Activity: Activity - H
232817e1-717a-5c92-8d76-943d6d8d1e40 | note | Verification Activity: By - PE
d2ce9723-f0d7-4d8f-b99c-3e030396441b | section | SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
ff08673a-8620-4836-8497-ae10c996fdd6 | checkpoint | 2.1 - Pipes/Fittings/precast Units
e9c31d34-876f-5a04-82ec-40ff2e955ae1 | note | Acceptance / Conformance Criteria - Confirm pipes diameter and class as shown on the drawings.
0c79066c-65c2-5c84-bbbc-2125ef01bbf1 | note | ○ Pipe dimensions given on the drawings are nominal outside diameters.
eba0616b-c735-5a26-a45b-9747e6217689 | note | ○ Manufacturer verification/records of compliance of PE pipe (i.e. pipe resin data)
b799c7df-4ae3-5561-bcd4-a3a4ded21ac2 | note | Standard / Specification - Project Specification
312d35af-c8fb-5b14-b287-71722f13dc43 | note | Verifying Document - Visual Check, Manufacturer's Verification
740efda2-cdaf-51e6-a66a-556b1c980c9a | note | Frequency - Each Delivery to Site
c043618c-b5d3-50b1-b1b5-c6727b4704c2 | note | Verification Activity: Activity - S
6f918756-8b98-5394-907e-7794edc81cb3 | note | Verification Activity: By - PE
276f5a4f-2bc2-4846-b718-223127fa92cd | checkpoint | 2.2 - Undercut Backfill/Bedding/Side/Haunch/Overlay/Backfill Material Compliance
9c5d5479-fe16-5b02-b29a-d0a96d4df062 | note | Acceptance / Conformance Criteria - Confirm material grading and density of pit sand
5e24e1a2-32e7-5ba0-b788-e64d3e081ec2 | note | Standard / Specification - AS/NZS2566 G1 (or otherwise)
d79dd7cb-db88-5cb7-b854-6b0aa03a87c2 | note | Verifying Document - IANZ Lab Test Reports
6d3c2d6c-667b-5a52-8b99-54aa2baf77ec | note | Frequency - 1 Test per 1000m3
6946ba1a-18c4-5e0c-8c96-b7d0ce92da87 | note | Verification Activity: Activity - H
c0a2de92-0313-576b-b56a-42ede3d1095e | note | Verification Activity: By - PE
022bc2de-c3d0-4873-bd8a-f83194ec3224 | section | SECTION 3 – CONSTRUCTION ACTIVITY
2fb04865-fa75-4b15-8eef-7bd73c7a0c90 | checkpoint | 3.1.1 - Foundation Compliance
a0208e95-b9fa-5192-a5eb-d92f0ee341a5 | note | Acceptance / Conformance Criteria - Scala 3 blows/100mm
4e3e64b4-b800-566d-97b6-f2667d7f158a | note | ○ Vane Shear Strength 70kPa
da8cb4c0-8661-5db0-aad4-6c3c4592aca2 | note | Standard / Specification - Project Specification 4.3
b02584e9-24f6-5197-bec9-916fa46ac2f9 | note | Verifying Document - Scala test result
cc7e873d-7c1b-5e1e-afaa-af8bcce0e794 | note | Frequency - Every 20m along trench
23c5c8cb-325f-554a-93ed-957220ae95c8 | note | ○ 1 test every 5m² at driveways and footpaths
9b867a40-9997-5a9f-9c5c-9ed5f70ebfd6 | note | Verification Activity: Activity - H
93bbe515-3514-54ff-9c97-8358f883f017 | note | Verification Activity: By - QE
f735f248-55f1-458a-af08-8d9bbd9ce555 | checkpoint | 3.1.2 - Undercut Backfill Compliance
54465482-3160-5c72-b2f6-ff5caa5fe869 | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm
22c93251-3c8e-5d2e-b714-6af3235fac97 | note | ○ Minimum Compaction 95%(Average98%) of MDD
407ad1e9-72f1-5f47-ac03-9407b446ad13 | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 60 or 95% of MDD
e3c5af9c-c895-5adf-93a4-d2ea077db452 | note | ○ AS/NZs 3725:2007
8d13ebf2-c851-59c4-a080-d26a23f04334 | note | Verifying Document - IANZ Lab Test Report
47c52222-03ca-5bca-9f75-1b3fe6b0c4d4 | note | Frequency - Based on Undercut Section
507d4938-94a6-502d-afe4-0bc4c2c053a5 | note | Verification Activity: Activity - H
d361f2fd-1e2f-54d4-81bf-58dd73585322 | note | Verification Activity: By - QE
7f95d084-870c-4eed-ba49-8faabc22b233 | checkpoint | 3.1.3 - Bedding Compaction Testing
0103705a-c541-5a76-808b-1f352be3bccb | note | Acceptance / Conformance Criteria - NDM Back Scatter
3f864571-6d2e-580c-98d8-77f584344954 | note | ○ Minimum Compaction 95%(Average98%) of MDD
6bd402cb-dd52-5e38-91e3-759c5f63a656 | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD
2d67a0df-5c25-5263-b410-5daed68e78d8 | note | ○ AS/NZS 2566.2/2002
cc708f24-02f4-5a47-98a4-d2152011d148 | note | Verifying Document - IANZ Lab Test Report
c82df032-4bb0-51c1-898b-356b9719048a | note | Frequency - Every 20m along trench
39cf982c-6729-577b-8b39-2395ff3818b8 | note | ○ 1 test every 5m² at driveways and footpaths
6a2671c7-77d2-51e5-b935-c36e630dacf2 | note | Verification Activity: Activity - H
e36b23fd-a61d-5a18-9fe3-158f28ca21e5 | note | Verification Activity: By - QE
393f7353-164f-4cb7-a8cd-882d4162a024 | checkpoint | 3.1.5 - Overlay Compaction Testing - Overlay zone shall extend from top of Side Zone to 600mm above the top of the pipe. 2 lifts of 300mm should be placed.
aab9ca39-5555-5a44-bb21-a6a60ddef38b | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm
df16f8f1-5605-58ea-b812-9316ab6efe51 | note | ○ Minimum Compaction 92% of MDD
0913efb7-a4af-5eaa-99c4-b5c1bf89976d | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 60 or 92% of MDD
14382105-f15f-58d7-9798-00d0df4e269a | note | ○ AS/NZS 3725:2007
3a9a59f1-d49b-5d36-9b34-ba06074f51c6 | note | Verifying Document - IANZ Lab Test Report
36a3ec45-e696-58d7-9498-e603e4ef6b97 | note | Frequency - Every 20m along trench
8f5ac71a-3883-5dae-ab7b-cd2f670a3da3 | note | ○ 1 test every 5m² at driveways and footpaths
ae60f3fb-7b7b-5434-a313-05b929eae640 | note | Verification Activity: Activity - H
a09f8926-9c98-5152-819c-c521942047c6 | note | Verification Activity: By - QE
b3f7eb01-ea80-4d95-8c01-853c65a1b69f | checkpoint | 3.1.6 - Collection of Waipa ITPs
ece1e485-b8aa-5b64-a415-e8da00091e6e | note | Acceptance / Conformance Criteria - ITP 04 Butt Welding
348a059a-f91b-58fb-9dcb-35dfefe91db8 | note | Standard / Specification - PWRBSS Quality Management Plan
94e87303-50e4-59a4-81eb-83646a768a6e | note | Verifying Document - Document Review
695c28de-20bf-5ae5-9ff1-ec56e1a0f7e1 | note | Frequency - Once
beba5da6-2bf8-516d-9e15-96c80a874365 | note | Verification Activity: Activity - HP
791fd6e9-055e-599f-a5e1-0e3eae12561d | note | Verification Activity: By - ENG
e19b7072-eec5-4898-9c84-7078bf1ebaeb | signoff | AUTHORITY HOLDPOINT
70825302-71ce-4bfc-a84c-1813935e63ae | checkpoint | 3.1.7 - Backfill Inspection
3a0d14fa-8a79-56e5-94fd-31821b94d919 | note | Acceptance / Conformance Criteria - Inspection of pipes prior to backfilling to ensure correct installation. No damages caused to the pipeline.
2be88f09-88fb-525a-b843-e11bf5e5b4a6 | note | Standard / Specification - Project Specification 4.3
9f880966-f001-5aee-a06e-4011edf20ac9 | note | Verifying Document - Photographs
a56255b4-0078-5471-9455-9297bdce341c | note | Frequency - Continous
9befc712-fd9f-51e9-b40c-90a2b163a885 | note | Verification Activity: Activity - S
698da5b0-b282-5ff4-b1cc-59542cba8ee3 | note | Verification Activity: By - PE
1f35e240-b1b0-44a0-b683-60b0a6ee7a17 | checkpoint | 3.1.8 - Survey
2debec50-321c-5c42-8397-95c742015497 | note | Acceptance / Conformance Criteria - All wastewater lines shall be laid per design layout. The deviation from approved design alignment permitted either in plan or elevation shall be:
fdbf7379-ffc8-5864-91d5-39aab890d7c1 | note | ○ Vertical tolerance ± 50mm on straight and 100mm in curves
ba4a551e-5a13-5038-a286-4f65a5e3226a | note | Standard / Specification - Vertical tolerance +/- 50mm
8390bc5b-2958-5dc5-9dda-53e74b1cbbd0 | note | ○ Horizontal +/- 100mm
ac90192f-0f95-5741-80fb-1178eccf1fac | note | Verifying Document - Survey Data
49c703b1-3194-5ddf-9216-075861e29824 | note | Frequency - Continous
0aa643da-9715-5163-aedd-78c3f45fb247 | note | Verification Activity: Activity - C
b94f483e-712d-5253-b85e-7712c898f0c7 | note | Verification Activity: By - SV
61b0e0a1-7ef9-4c0e-acf4-a4ae73ae6dc0 | checkpoint | 3.1.9 - Backfill Compaction Testing
48356dd8-47f6-51b1-9b5d-e8a408ea2db6 | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm
1869700f-9fd5-59ae-ad97-1cac0cbea2c7 | note | ○ Testing to be completed on 500mm lifts of backfill - 95% of MDD at OMC
d6af6476-67f6-58cc-925c-6ccf76e8dd03 | note | Standard / Specification - Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD
d358a8a7-33f3-5135-94cb-31ef8ff8a63b | note | ○ AS/NZS 2566.2/2002
ff24e590-5545-5ac2-9d65-6fecfe95820f | note | Verifying Document - IANZ Lab Test Report
0872ae35-4eb9-5f3c-9a83-8b8850be856c | note | Frequency - Every 20m along trench
6dd6be41-e7eb-5b41-8644-4fbfd913d250 | note | ○ 1 test every 5m² at driveways and footpaths
76f7d514-fb39-5838-a8ff-4863f1148650 | note | Verification Activity: Activity - H
067863d9-4083-50ed-839f-d6869dc7e8bc | note | Verification Activity: By - QE
4bcb429c-a0e4-490b-b99c-b15c4c212648 | checkpoint | 3.1.10 - End Caps
f9fb7bbe-e875-5ae4-827c-2da5ff5c749f | note | Acceptance / Conformance Criteria - Red-painted sealed end per RITS D5.4.
8112e8c8-3cc4-5b33-b600-28f92c4f1b7b | note | Standard / Specification - RITS D5.4
5818a72c-8d32-56b3-972b-a2a4d04604d3 | note | Verifying Document - Photographs
9e5081af-8482-59e8-9ee7-0eb55b9d20d0 | note | Frequency - Each End Cap
81fb03c3-e1d9-5dc7-a46d-abb7aaa41ee5 | note | Verification Activity: Activity - S
3d00bb91-ef7b-58db-be8b-8310abcc8db7 | note | Verification Activity: By - PE
5df501e6-968c-4e32-b92f-a44d270299a6 | checkpoint | 3.2.1 - Manhole Foundation Compliance
33f78455-9826-5840-99a1-2f666861cffb | note | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
a678d5d6-2b8a-52b1-9e96-573933e81c1a | note | ○ Cohesive Material: Vane Shear Strength 70kPa
2b713e6d-702f-514d-ad05-416c0c481ec0 | note | Standard / Specification - Project Specification 4.3
06b76edc-4705-58a2-b446-d51ef91adbb4 | note | Verifying Document - IANZ Scala test result
06c91bf0-aad0-5780-8ed4-0d0ef94f0eb9 | note | Frequency - 1 Test/Manhole
dfbffcba-aecd-5882-a046-787fc9e2c53d | note | Verification Activity: Activity - H
39101090-bb48-5e0a-9391-be3900f985a5 | note | Verification Activity: By - QE
a767cee1-7cf4-4832-b667-e5ea5d06eab1 | checkpoint | 3.2.2 - Undercut Backfill Compliance
8fb19620-71bf-5c17-888e-07e5c1faedd9 | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm
9995078e-8142-5424-954b-4e9336f5c1c4 | note | ○ Minimum Compaction 95% of MDD
13ca01c4-098a-5b62-b9ca-5d03e5f22b46 | note | Standard / Specification - HS2 backfil Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD
892cf77f-f829-53bb-9bdb-b392afa84d60 | note | ○ AS/NZS 3725:2012
dbf57eda-0d50-5535-bd4d-89faa199a8de | note | Verifying Document - IANZ Lab Test Report
da3bf3c8-7cff-54a2-ae4e-a5bd80220047 | note | Frequency - 1 Test/Manhole if Undercut required
b3e18acd-2adc-56bb-be00-7694cb7e3f66 | note | Verification Activity: Activity - H
dbc5cc49-af8f-5ebc-ad7e-2358bf683944 | note | Verification Activity: By - QE
a73f421d-933f-4ea3-9c33-cfdc1b4391bf | checkpoint | 3.2.3 - Bedding Compaction Testing
b1439eaa-7bac-59a2-adaa-0c02ebc05b47 | note | Acceptance / Conformance Criteria - NDM Back Scatter
66582e6d-4f66-5ac0-b9c1-27de19544eff | note | ○ Minimum Compaction 95% of MDD
800c0b06-e185-56ab-a397-fa1561b2045d | note | Standard / Specification - HS2 backfil Non cohesive material - Minimum Density Index (DI) of 70 or 95% of MDD
59864ed2-0b5a-5d97-bba9-b9232b6db99f | note | ○ AS/NZS 3725:2012
a7229e58-fb34-5e88-b311-8f8610059c45 | note | Verifying Document - IANZ Lab Test Report
27ece894-e1c3-5aca-ae27-30f0a3f3e4f3 | note | Frequency - 1 Test/Manhole
08f2a1e5-8c04-5a99-b995-97bcfcfb2bd0 | note | Verification Activity: Activity - H
149ffa98-f541-5bec-b44a-ca7400669c8d | note | Verification Activity: By - QE
8543d836-efca-47e0-92e9-c3423fda8213 | checkpoint | 3.2.4 - Backfill Inspection
3e941499-b26e-5d4e-92b9-979a6feb0167 | note | Acceptance / Conformance Criteria - Inspection of pipes prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the manhole
5add0c10-5e0f-507c-92fa-0d76be05f770 | note | Standard / Specification - Project Specification 4.3
f6e15a72-74e7-58a9-b5b4-9b0a4e008140 | note | Verifying Document - Photographs
6a9e809e-a582-5a60-9765-7fc462eb1711 | note | Frequency - Continous
50f7f00a-b2cc-5ee5-a549-2c2f383307bc | note | Verification Activity: Activity - S
1190d7fa-20c7-55dd-aa85-b1d0f076f630 | note | Verification Activity: By - PE
97b4c7a6-4649-43b7-a470-faa13f0ab737 | checkpoint | 3.2.5 - Backfill Testing
174079b1-ec0d-5fdb-9506-bfa703bd2275 | note | Acceptance / Conformance Criteria - NDM Direct Transmission with a probe depth of 300mm
6f8896f3-7a12-5086-9ac8-ba9d630fd18b | note | ○ Testing to be completed on 500mm lifts of backfill - 95% of MDD at OMC.
cb80232f-da07-5cdf-810a-7ee2f522ebfe | note | ○ Minimum Compaction 95% (Average 98%) of MDD
90fc0a94-09b5-5722-abdd-6de523143128 | note | Standard / Specification - MDD Average of 98% with minimum of 95%, PS 4.5
40fed417-c50b-5f36-8009-458c24f15028 | note | Verifying Document - IANZ Lab Test Report
106c26e5-9056-584c-843e-ec2d6ee04361 | note | Frequency - 4 Density tests per layer at Quarter Points Around Structure
08ed4d3b-1a3a-56dd-a6af-41cab92cf519 | note | Verification Activity: Activity - H
7675d06e-7b2a-57d6-87f9-81dd3fe64e58 | note | Verification Activity: By - QE
dc41e3c3-68e2-4502-8b41-9bcf6b862e29 | checkpoint | 3.2.6 - Concrete Load Distribution Ring
0a483c15-ee22-5408-a385-87ff3890099e | note | Acceptance / Conformance Criteria - Installed per manufacturers requirements.
ea1964b2-833e-55e5-8157-24c20c4aea99 | note | Standard / Specification - BBO Request
bca504f4-81f4-513c-b80d-61ef23956028 | note | Verifying Document - Photographs
fbb79f75-cc57-520e-8643-4ad72b0bfc2e | note | Frequency - Each romold manhole
56663a83-42d4-55f6-ad52-52ec84888101 | note | Verification Activity: Activity - S
9a28d154-ae11-51f1-ab06-a0c055ea1b08 | note | Verification Activity: By - PE
5f43b102-b3e9-4e06-9de0-1213af0030d3 | checkpoint | 3.3.1 - Pressure Testing Methodology
57990fe6-2750-54b8-98bf-2300191d6a11 | note | Acceptance / Conformance Criteria - Subcontractor to submit to method statement prior to testing.
236028ba-0c7f-5a82-a130-a71bd9a500d3 | note | Standard / Specification - PS Appendix L 3.10
20b1b1fb-55e6-5741-8624-548c00eed443 | note | Verifying Document - Engineer's confirmation of witness test
1f2efc0d-d9c7-54eb-b011-afada889d681 | note | Frequency - Notification required 2 working days prior to testing
b9da16db-e9dd-5827-9880-d7f9edb6dcdb | note | Verification Activity: Activity - H
0e7d6c37-4d98-55ff-98fc-56dc7a7b2c84 | note | Verification Activity: By - ENG
1ffae514-5118-45da-9df2-9002b9c66d64 | checkpoint | 3.3.2 - Pressure Testing Qualification
28cda046-f2e5-51d4-b815-68b761562df0 | note | Acceptance / Conformance Criteria - Confirmation of qualification of personnel supervising the test.
6834f8fb-3a63-51f4-96cd-cd73066f3345 | note | Standard / Specification - PS Appendix L 3.10.3
f94a94d1-1c5b-54f6-b9e2-7f187b30b865 | note | Verifying Document - Qualification
99ab69be-12b6-50ef-8a6d-3db481ae992a | note | Frequency - Once per supervisor
a607133b-bce4-5bff-8bf7-60b3ef2e3d58 | note | Verification Activity: Activity - S
8bab25f5-e285-586a-a9f0-16742ebe1f9f | note | Verification Activity: By - PE
7215e341-906e-4cbf-98b3-0a6340a0da23 | checkpoint | 3.3.3 - PE Pipeline Pressure Test
4113a64e-1725-54dc-b0af-7f16d5a4ca25 | note | Acceptance / Conformance Criteria - Unless otherwise specified and approved with line-specific methodolfy (i.e. Pressuremain 04 and 03).
4c70af7b-8653-5220-a5ca-cc3fccd99181 | note | ○ Testing to be undertaken on completion of invasive/major works.
bc81996c-f6e2-598b-be74-966f5c64e56b | note | ○ M5 per NZS 2566.2, test pressure 1.25x lowest rated component.
545f90cf-386e-5143-a493-beb4090fcda1 | note | Standard / Specification - PS Appendix L 3.10.10 (RFI-0268)
fb0d24c0-eb62-5ff5-897f-e49a1b5817ff | note | Verifying Document - Pressure Test Report incl. data log in .csv or .xls format
e304105a-8a37-5c42-b3dd-ee8b21a91ee5 | note | Frequency - Per methodology
7ed09bc4-9a94-57ca-a19f-a9212c3d06cf | note | Verification Activity: Activity - H
7ff35e2a-1d0e-5459-ac6a-ecc762e1dd4a | note | Verification Activity: By - ENG
270cf86d-dcf6-4ae8-86bd-eb1f109b457c | checkpoint | 3.3.4 - Romold Manhole
bb7aaf0c-55fe-41fd-93c6-b260952a9382 | section | SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
4c47f7de-04d6-4249-b634-0430ffd7d109 | checkpoint | 4.1 - Unforeseen Items
08286f57-6faf-536f-a4dd-20ca028e85be | note | Acceptance / Conformance Criteria - Upload items which may not be captured appropriately above (i.e. EF Coupler Installation)
72b6c461-1289-50b4-94a8-44efcfff8679 | note | Standard / Specification - BBO Request
df9b358e-81d7-586a-bb3b-a30745adf20e | note | Verifying Document - Misc.
34376842-6fdc-5651-a216-4058b8568c42 | note | Frequency - Once per lot
238b3c0e-9947-592e-9cac-b92cc4da692d | note | Verification Activity: Activity - C
b9db2ac7-146e-5be9-9abb-e6eeb82f2041 | note | Verification Activity: By - PE
2fae5bcd-e8a8-4c87-88b6-a1fdfd4a8042 | checkpoint | 4.2 - Survey As-Builts
cb0fc962-5c56-5094-8b47-d5dfd6ef9260 | note | Acceptance / Conformance Criteria - Quality Check on New Works
fa425e8b-beff-5205-865f-47cf9acafb9d | note | Standard / Specification - Project Specification
310fc6d8-9613-575c-af81-9d2c69ae5e65 | note | Verifying Document - Survey Data
4eb9108f-57a9-5e2a-9923-48d5dac30ff1 | note | ○ As Built Drawings
df785beb-0283-5f4e-8e1e-f9a54591768a | note | ○ Photographs
d36ba515-3810-5090-ae95-52b301e865cb | note | ○ Red Pen As-Builts including Undercuts
26b18dcc-6f81-5cf5-ae5e-994160748440 | note | Frequency - Post Works Completion
ff61c8e4-1dad-5961-8caf-27b0a93e0ca0 | note | Verification Activity: Activity - H
a87889c5-6190-5a98-84ab-ecd4614d45e2 | note | Verification Activity: By - SV
| checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
| textbox | Contractor's Rep Name:
| textbox | Engineer's Rep. Name:
| date | Date:
| signoff | Add Signature