## Master List Templates
Id | Type | Name | Values | Prompting Name
11d4612b-8e0c-4477-9d3c-2e0c1a183e33 | checklist | Cable Drum Inspection Checklist |  | Cable Drum Inspection Checklist
5e47900a-d397-42cd-9234-b4b7d3362356 | section | Cable drum details
7089a24c-3afa-4136-976a-2798caad63c9 | checkpoint | Cable drum details
fc30a98c-7f0c-5be0-80c9-479f5c18b95f | textbox | Drum number:
0e02c801-9b9b-50ed-9017-74f85547f2b9 | date | Date:
99b24b80-a43b-4a94-96dc-ceb518d42752 | section | Visual inspection
9e827754-ad94-4835-b7a8-4286cadc470b | checkpoint | Drum Condition
f45f69a8-97f4-5ad0-95e0-2dd7c0af2cbf | textbox | Drum Type
5fc4ce18-a52b-4090-a5b6-eb66398f423f | checkpoint | Signs Of Damage
227555a4-6ec2-499f-bf2c-a8fae328622e | checkpoint | Damage 1
51ad469b-0896-5936-acff-2a08ff24b20e | textbox | Damage type:
1b366580-ca14-5789-a4a7-af9c592968a0 | textbox | Severity:
233cf797-c363-55bd-a224-d2001476d0f5 | textbox | Labelled gas pressure:
37943547-d60e-5075-bd17-b44c9a750d17 | textbox | Tested pressure:
16f14d5c-270f-44ec-a6e6-8537101488bc | checkpoint | Damage 2
8679ca98-ea4e-579e-b239-627de0c55c13 | textbox | Damage type:
40bcd1da-6e93-598f-8785-b7d1cb2c1e0b | textbox | Severity:
080530c3-2694-523c-8d89-ca3ae1d5d3dc | textbox | Labelled gas pressure:
7bd5387c-6514-5d36-8227-5cc5f53c9500 | textbox | Tested pressure:
82a859b9-804e-43f0-bda6-615b91736e3c | checkpoint | Damage 3
62f8fb3b-9fd2-5cbb-99dc-38e6ca2657a8 | textbox | Damage type:
ee2c1d7d-24f1-5aac-b208-d91711e1f218 | textbox | Severity:
b7113688-e789-579c-b152-e32ee980f76c | textbox | Labelled gas pressure:
c2b9a2ca-2c86-5720-9436-d4ff96990348 | textbox | Tested pressure:
4bc37aa2-184e-40f3-b2da-2ed8652e1a5a | checklist | Cable Insulation Testing Record Checklist |  | Cable Insulation Testing Record Checklist
3a0ade55-af45-419d-a552-f7f81e0944a3 | section | Details
ff708c25-81ce-426b-b28b-25c491799aee | checkpoint-no-value | General details
4f8877a8-7411-548f-85ce-f100071d2578 | textbox | Cable ID:
d6e8f36a-13ce-588b-ac2a-50512a1eba80 | date | Test Date:
e9c34b70-8c87-5f61-af20-a2ca6b87cc69 | textbox | Test Technician:
345d31a1-d311-5cff-9497-c5b307659ac3 | textbox | From/Cct Source:
ffaad822-4e4d-5768-81e9-45a959ee227e | textbox | To/Cct Destination:
11245efc-a1cb-5260-b418-22ac9d901c7c | textbox | Rated Voltage (kV):
04021784-d48d-56ba-900a-831bc25981db | textbox | Size/Type/Cores:
848cb42b-a627-50ea-b820-0ca05d2bb840 | textbox | Cable Type:
dd411d26-531d-5354-a8cb-b51f14a70073 | textbox | Circuit/Drum Length:
980cc1a5-3921-51ee-bf41-f8a95c221ded | textbox | Identifying Notes:
7785b302-0d42-49cf-8b1b-daeea072eaf7 | section | Sheath to Earth Insulation Resistance
c71c7cb6-0402-4e32-958e-634ad3f0cd07 | checkpoint-no-value | Details
b76e8d6d-b240-5499-9ce8-ce22163c88c1 | textbox | Instrument used:
15d8d0ec-bbfe-5257-9f80-f18a3727bfef | textbox | Serial Number:
a9c81803-4597-52b2-bb86-4362c0055831 | date | Cal. Expiry Date:
c702b93a-63d5-54ca-a5b9-1319d3789725 | textbox | Test Voltage (kV):
a85ed98b-f72c-5564-80bc-44a5da41e109 | textbox | Duration (mins):
94dcb558-6d47-58f6-a5d2-0659e6f96008 | textbox | Air Temp (degrees C):
452441b1-803e-5c31-8584-70cec783f63d | textbox | Humidity (%):
30fc6186-fcdd-4b6d-a029-7b0406e5b0ac | checkpoint | Singe Core Cables
711a42e8-e44e-5836-bf41-b1c8ad2ef9c5 | textbox | L1 Screen to Earth (Ohms):
21c8fb5c-93b1-5eea-bb1c-3793b1b037d9 | textbox | L2 Screen to Earth (Ohms):
a2f4af11-f782-5df8-b432-0e6dcfe2a186 | textbox | L3 Screen to Earth (Ohms):
9c300933-4726-468b-b343-d7435f4575e3 | checkpoint | Three Core Cable
31a34e9e-02fa-53e9-868f-fb723e192f32 | textbox | Screen(s) to Earth (Ohms):
85c03ec6-7fca-4469-8b8c-689484b5870a | section | Core to Screen Insulation Resistance
186d82a5-388d-4875-97b7-e6934eac6754 | checkpoint-no-value | Details
1bc1a73d-7028-52f7-9543-e92ff3b30f43 | textbox | Instrument used:
d8bf6715-3117-5249-baf7-497949049e64 | textbox | Serial Number:
1895b13e-a2f2-5b08-ad3f-55b540314034 | date | Cal. Expiry Date:
5b72dc68-3604-550f-8e97-08b9d58a236b | textbox | Test Voltage (kV):
6d028f80-339d-53b9-bffb-cfb0c53f1a9d | textbox | Duration (mins):
b58e18f7-0f9c-54da-b895-3e0109b79a76 | textbox | Air Temp (degrees C):
e3d11fb9-fc4b-54a1-b2ad-003b798c1738 | textbox | Humidity (%):
40cf785c-c6b7-444a-a503-68df6cd776e7 | checkpoint | Singe & Three Core Cables
2071842f-24e4-55db-a9a6-3f6ea783ca5d | textbox | L1 Core to Screen (Ohms):
69316d11-4c2f-5d2e-b178-6c4704bc628c | textbox | L2 Core to Screen (Ohms):
ffd3f512-d4bb-5caa-ac3e-1ed73f37a545 | textbox | L3 Core to Screen (Ohms):
4a2ba902-1c38-4aae-b664-b37678c2aa85 | section | Core to Core Insulation Resistance
d236c055-e477-4c37-976f-02ae0ce067cf | checkpoint-no-value | Details
2b8a609b-71a9-51be-84f5-2bacfb666c33 | textbox | Instrument used:
fe63115d-4922-55b4-ba75-bf438c7f6458 | textbox | Serial Number:
31465ed5-46c1-53a1-afd2-72ab23d27c9f | date | Cal. Expiry Date:
ecfeedc0-9db3-574b-959e-ec7acbd67e23 | textbox | Test Voltage (kV):
54eaccc6-c5da-5484-a353-494952866e8a | textbox | Duration (mins):
1aaa028f-c082-5195-ab96-2f68487625b2 | textbox | Air Temp (degrees C):
a0930471-8aec-5757-ad56-c7410ca56ab8 | textbox | Humidity (%):
c16c8162-e284-40bf-b20e-32462fa7a8bf | checkpoint | Singe & Three Core Cables
d060ea8e-bfd1-51c0-bb75-71787b10cd76 | textbox | L1 to L2 (Ohms):
c59a6d88-8156-564c-8f7f-be60a7fb9972 | textbox | L1 to L3 (Ohms):
b5f0e61c-e03e-5b51-a65a-f606edbcea35 | textbox | L2 to L3 (Ohms):
33276a0a-4eaf-4d99-b8a3-58408e7941d8 | section | Signoff
c6fd424e-d5ee-4033-8660-f7ff537cf592 | checkpoint | Technician Signoff
10fd0f55-4dbd-4bc5-a4f5-261fddc8c6bd | signoff | SIGN HERE OR REQUEST SIGNOFF
82e85ce1-ace5-4a16-81f6-54e84e835784 | checklist | Cable Pulling Record Sheet |  | Cable Pulling Record Sheet
189a6247-cd51-4ef3-8ebf-468772a63e16 | section | Details
6acf0c84-0d21-4194-84ba-31234af9d10b | checkpoint-no-value | Cable Route
a4cc26a1-52b2-5d84-9b79-88ca9e4ed287 | date | Date:
c6b8284c-06e1-54ff-aa17-955826bcba3b | textbox | From:
e3c85d4a-57a5-5ac5-bd1c-dc0d7179f7d3 | textbox | To:
8d51d6c0-4dd9-5194-9133-9e89934ab96a | textbox | Length Of Run:
f45cd2b7-9b19-4a54-b49d-e28bbf7cd806 | checkpoint-no-value | Cable Description:
16943dd4-4115-5547-a3a3-6b51bd7f7bd0 | textbox | Cable Size:
9d91a8e5-6f3c-59ac-b7ba-abea741ec4f3 | textbox | Minimum Bending Radius During Installation:
1ecbe2b9-421e-4f69-97e0-fcb31873a89c | checkpoint-no-value | Cable Containment
50e7ebee-e0f2-552a-9cc6-085cec912fdf | textbox | Type:
09fcace7-b67d-5430-885b-232db79c816c | textbox | Size:
e133086e-a1e0-46c4-9f4f-e88bbfe044f3 | checkpoint | Has The Containment Been Proved?
7741d1f2-02d0-4366-a470-4dfc539e661c | checkpoint-no-value | Cable Pull
dc09fc59-2647-5d4c-a8aa-c6cad8e62cde | textbox | Method Of Pulling:
fe770a31-2dad-533c-b9b9-1b7631f0c328 | textbox | Type Of Pulling Grip:
a2f3a244-06a0-5dec-b13f-071dad2ff5e4 | textbox | Maximum Permissible Pulling Tension:
73f029f2-8ab8-5dbc-82a8-998d9153cf52 | textbox | Instal Pulling Tension:
3f84c2d7-495e-51fd-bfc2-010ae84be29f | textbox | Completion Date:
c17f0731-6763-4036-aa5f-1e69f5098cce | checklist | Cable Sheath Test (Gas) Checklist |  | Cable Sheath Test (Gas) Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8b05d9df-3ba9-48ba-9f48-a0cba08449b2 | checkpoint | Date
3229bdcc-0ef0-5ccf-ad95-49f0dbbb92a4 | date | Date:
89908541-7caa-4323-80f0-6036feab2d5e | checkpoint-no-value | Equipment details
0fa97291-b127-5e6d-927b-72fc87ed1ed2 | textbox | Equipment:
31579691-7bc3-50aa-bfd4-05e74afa1832 | textbox | Serial number:
43d83b33-d267-5674-b67f-bc8924f3ed1a | textbox | Make:
948da125-2811-47bc-a90c-2823571afee0 | checkpoint | Gas Pressure Applied (PSI)
873accde-91c7-56ae-8fbc-32cbbafbf081 | button | Please select | 10 PSI, 15 PSI
d3fed123-d1fd-46c6-92a8-51665f852a4a | checkpoint | Gas Pressure At Start Of Test (PSI)
373ffc51-afc5-5f2a-b1bd-5e0a80470e3d | textbox
339f2f8a-1477-40cd-82d1-ec185de09c5c | checkpoint | Gas Pressure After 30 Minutes (PSI)
8778f4b1-91ba-561f-9c8f-54bcb9d5341d | textbox
a26ac152-a9a8-4c3a-b0a4-f62ba0586791 | checkpoint | Gas Pressure After 60 Minutes (PSI)
821149f9-6c11-5b0f-a971-857390091b02 | textbox
3a2ecdfd-ea78-48ea-9160-4729e3ae09b0 | checkpoint-no-value | Technician Name
c8fb0201-7618-524b-b39b-79a2c6e59a35 | textbox | Tested by:
2a566ca0-e1f2-4e7e-abd5-a3b8b9a54812 | checklist | IR Testing For Single Core Cables Checklist |  | IR Testing For Single Core Cables Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
80e3d926-7e03-46ca-ad42-ab578342244b | checkpoint | Date
5c4f6b17-93cd-5122-b1c0-549b026b4cbc | date | Date:
3f91b77c-1697-4131-b4d7-9a9fdd4b56b9 | checkpoint-no-value | Equipment details
e3bfe51b-2954-5416-87f5-6bf14bef498d | textbox | Equipment:
6cb7cbaf-a801-575d-9a50-6844b0e0911b | textbox | Serial number:
7adf9dba-9c6b-55b5-afdd-92b8362e2e31 | textbox | Make:
4ed3127f-340a-4be4-a9dd-7d650501ce14 | checkpoint | Red Phase 1 - Screen
ef32a0bb-dd44-579a-b3c2-3a7dd4ba32fa | textbox | Test Voltage:
5844ad9b-5020-51ea-9470-deae4c28a8dd | textbox | Duration:
3d47d5e0-289b-5c9c-a3ed-7c1d9fa86566 | textbox | Result:
2a17ed1f-d281-469b-86a0-d05b4ed9bc54 | checkpoint | Red Phase 2 - Screen
21f49f3c-3cff-53c9-9f09-58d7fbd76985 | textbox | Test Voltage:
7dc3d24d-7cab-51f1-9ef7-c215c47df187 | textbox | Duration:
00940c93-f89c-5a4a-a1ed-761fd08f60c4 | textbox | Result:
59711cfe-69d2-4fae-8c35-851d4c684f02 | checkpoint | Red Phase 1 - Earth
c188a3a2-cfc7-565b-8128-2fa47810e5f9 | textbox | Test Voltage:
e0486d38-08f2-5ee3-9803-2dfd52e273fb | textbox | Duration:
b6aae098-1731-568f-906b-801b8b8be257 | textbox | Result:
ee238cc9-459f-4b4c-89d6-beb0b6566cba | checkpoint | Red Phase 2 - Earth
7ddf6711-b628-5a09-9a3f-81508b88dc0a | textbox | Test Voltage:
fc21d0bc-9d23-5b6d-8e13-4fbe15dce5ad | textbox | Duration:
960999c4-8925-5a10-be97-37d7dc63eb58 | textbox | Result:
3c734930-7092-41f4-9e16-960f7440d854 | checkpoint | White Phase 1 - Screen
c688229e-a92a-58d0-a622-d3b452e2e20d | textbox | Test Voltage:
78344cc0-37b9-504a-a26e-4f92226dd98e | textbox | Duration:
7c766696-30d8-59b4-839d-873370a085cc | textbox | Result:
c47b7c18-a216-4750-80e4-beb089e468fc | checkpoint | White Phase 2 - Screen
512df42a-e0e0-59b3-819e-aacb6dd1ca33 | textbox | Duration:
5124cbf7-118a-57de-9548-9b3166fb7b0c | textbox | Result:
c7c96d13-b3e1-4175-8329-6202f8df6047 | checkpoint | White Phase 1 - Earth
e6a54faa-292b-5b4a-bb67-a9a7a5729b44 | textbox | Test Voltage:
f1379882-63ec-5717-831a-2d909191c092 | textbox | Duration:
fb760d45-f0c1-548f-868b-dcdcd641ef3b | textbox | Result:
fbd0b2c7-39c3-475a-8a76-244d940bfc8f | checkpoint | White Phase 2 - Earth
86f246a6-1423-5181-a546-9db67b674908 | textbox | Test Voltage:
9de86f9a-26e3-5d45-8d1a-054b388b8014 | textbox | Duration:
bf5478ff-f69a-591a-abe8-50aadf6b900b | textbox | Result:
65e1c57c-2859-4399-be6a-4d2e10f9dcd7 | checkpoint | Blue Phase 1 - Screen
bf97d282-0618-506f-a1c4-4b5343f477c7 | textbox | Test Voltage:
2ee11a10-7546-5c33-b0c8-644407d03195 | textbox | Duration:
d7edde00-bf84-5092-bb82-53652bdae987 | textbox | Result:
450c4df5-50a6-4c17-9a0c-a4fc1da041c5 | checkpoint | Blue Phase 2 - Screen
894c3c6d-9a07-5ffe-b2b6-17ed31975249 | textbox | Test Voltage:
12f02528-1062-5448-b6c5-6da630a487e4 | textbox | Duration:
584f72fb-3321-581e-972b-20719ade9207 | textbox | Result:
e3afb936-647c-4462-88e7-8d9b6b2648b6 | checkpoint | Blue Phase 1 - Earth
52493554-3ef0-507c-b1d6-10b6f9ccdfb4 | textbox | Test Voltage:
d92930c5-aeec-5196-99ca-3e8b64f41da6 | textbox | Duration:
48173800-7d47-519e-aa98-055204189e37 | textbox | Result:
40d01349-2863-4734-8f6a-6e64342a7c6f | checkpoint | Blue Phase 2 - Earth
311c818f-a158-514c-9218-8f958df774da | textbox | Test Voltage:
ea537935-db5f-5125-ac8a-b21361e75b92 | textbox | Duration:
2d874582-d5fd-50c8-b7dc-7a001bca6d0a | textbox | Result:
46a24b48-8443-4676-89e6-8b2de10eb214 | checkpoint-no-value | Technician Name
2c4e9e3c-152e-58bb-b71f-359533b70beb | textbox | Tested by:
22f5cd24-d7b9-4a00-a505-1c32d1a0ce58 | checklist | IR Testing For Three Core Cables Checklist |  | IR Testing For Three Core Cables Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
4ce90d2f-bea4-4836-9b6b-461d2d60bfb0 | checkpoint | Date
72b53a6a-3694-54ad-ad7b-d643359609df | date | Date:
689938d4-ceae-4503-822a-1e4947c54a39 | checkpoint-no-value | Equipment details
a07de129-917d-5168-8f96-b4bf0ad5250c | textbox | Equipment:
12bc67e1-87eb-508a-a6f5-8483c118d49e | textbox | Serial number:
f2320d49-479a-5965-b085-0058308d516b | textbox | Make:
e466d4c9-1428-4035-be6d-32114dfa9d00 | checkpoint | R - W
036c8cc3-0adf-5f3e-9a37-ab11e1d2c5a2 | textbox | Test Voltage:
345d933a-9edc-5742-977b-bdeffab79820 | textbox | Duration:
cf46549d-e181-5b91-9ae5-af3c4ab05509 | textbox | Result:
681a5144-152a-4cef-a1be-987bd8b2bab0 | checkpoint | W - B
e031e16b-2347-52a6-8278-73da0a7bf3d3 | textbox | Test Voltage:
c516d9bd-679a-5744-aa8d-b399a780660e | textbox | Duration:
cb84268b-a179-58d3-a900-911b7cfd4d1f | textbox | Result:
8deb7c31-39fa-45e1-85ae-e23c7521c69e | checkpoint | R - B
d094da7b-4aa8-5474-a476-39c06be45450 | textbox | Test Voltage:
86ba6090-8482-5786-9514-c3e729b37096 | textbox | Duration:
ca062c08-fc22-54df-9d48-4408187c08d4 | textbox | Result:
37f0e38f-83eb-43d6-960d-a7b981963905 | checkpoint | R - W - B - E
c316b904-df90-59ac-b3b7-6b95f051537f | textbox | Test Voltage:
82ac7f88-7a93-59a9-8df6-29854f1c01a6 | textbox | Duration:
63737b75-580f-574e-92c8-ecaa0d5a94b1 | textbox | Result:
4aded23f-1cb5-4457-bbb6-77654470345f | checkpoint | W - R - B - E
38c3591a-7635-59e0-ad21-0b2df466551c | textbox | Test Voltage:
f74c6406-921f-5f69-be8c-5fa8cd4a3adc | textbox | Duration:
54f9fe7a-337e-50a9-a368-af5bcbcb17da | textbox | Result:
39b8bbd1-85e1-4493-a3ed-5897ae61adc3 | checkpoint | B - R - W - E
d514ae7b-5563-5c59-bcac-654e487646b4 | textbox | Test Voltage:
9056b73c-7804-526c-8451-946f4df7f720 | textbox | Duration:
0b4350a1-9874-5cf3-a9a9-0f5e4a12a506 | textbox | Result:
2b8f99c3-1760-4c3a-8cbd-33840f3587f4 | checkpoint-no-value | Technician Name
1f249d6f-261a-54f5-8a4d-50a86ee59699 | textbox | Tested by:
878113b8-bd0f-58da-b67e-14a6f4a3de53 | checklist | Photos |  | Photos
70763b3b-9c56-5006-84dd-3008db2cc680 | checkpoint | Please upload all relevant photos and press PASS.
42c7ce00-81cd-52b7-babc-e6d813c36467 | date | Date:
64def538-a6df-47be-beed-0c45bfe8c37c | checklist | Polarization Index Checklist |  | Polarization Index Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
b456eae4-5a9e-4c99-aafe-bfb4e98fad2a | checkpoint | Date
4fe8b6e6-46ca-5ba4-8cc6-13771d61c9a7 | date | Date:
307314b8-33fa-4a42-aee1-973ea2b717a2 | checkpoint-no-value | Equipment details
b0734835-4335-5c60-9249-629b913531f8 | textbox | Equipment:
70c3533a-95ba-5ace-8e59-51e66f9c6799 | textbox | Serial number:
bb93a4d7-0f2a-5529-a3ea-51a6e7f41e7a | textbox | Make:
fdb2b844-fc33-4319-beeb-b4fcbf8b0cf8 | checkpoint | Red Phase TO W-B-E
6ecd8542-5fda-553d-9582-98353d1c41fc | textbox | Test Voltage:
46561f78-44a5-5674-a170-49862c897f46 | textbox | Reading After 1 Minute:
c3acf178-1276-5444-8c64-370392f93e6e | textbox | Reading After 2 Minutes:
09cb6b11-9635-5c29-b9ad-c8cde2eba2c3 | textbox | Reading After 3 Minutes:
fc4a427a-3c1e-5113-a9cb-2b697ae99fa3 | textbox | Reading After 4 Minutes:
93579a84-ab4b-58d4-8bbf-97c18e352dfd | textbox | Reading After 5 Minutes:
ad3e3ade-93a7-5e58-8c8e-b54cd2df07f2 | textbox | Reading After 6 Minutes:
22ef61b7-9b5f-59cf-b635-157ce21094dd | textbox | Reading After 7 Minutes:
a7cafd82-bbf7-5bb9-ad74-ebee81841e1c | textbox | Reading After 8 Minutes:
1f7414aa-4c18-5c67-900e-02c684f6cd62 | textbox | Reading After 9 Minutes:
83ebd619-9359-5663-ba85-b61aafe342b6 | textbox | Reading After 10 Minutes:
5d34d901-07a3-50a2-8387-86ef20e5e73c | textbox | Polarization Index:
a62f606a-96f8-594a-b583-fc5cb818e3ec | textbox | Insulation Condition:
54e29ffc-0e91-4267-ab9f-4d5d816ff664 | checkpoint | White Phase TO R-B-E
474206a8-60b0-5a18-ab53-7e80ee411762 | textbox | Test Voltage:
f8021ea7-97ae-5324-a482-db9204897d4f | textbox | Reading After 1 Minute:
cc32d181-f828-526c-9042-92b92c5a4663 | textbox | Reading After 2 Minutes:
d91827cd-f36f-5b9e-a229-5d9f5d98c4f8 | textbox | Reading After 3 Minutes:
9def03a3-5bcd-5e61-94bc-b96aa5b4872d | textbox | Reading After 4 Minutes:
6e2feab9-5b14-553a-9161-798cd6b447db | textbox | Reading After 5 Minutes:
4aa4548d-00fa-5a5b-8ccf-a17e5a1880a8 | textbox | Reading After 6 Minutes:
543a78a4-9e30-58cc-85f1-e899d2734c61 | textbox | Reading After 7 Minutes:
595b2be5-a141-5053-95a6-ec22177df331 | textbox | Reading After 8 Minutes:
55761692-48f1-5fd5-8b07-a3ab6765b5fc | textbox | Reading After 9 Miinutes:
2a04bcbe-0ea4-5fe2-8d8d-fb79ecc2f6d7 | textbox | Reading After 10 Minutes:
917222f0-4c6f-510c-a3aa-a5a519ae66ba | textbox | Polarization Index:
0314b293-4412-5c14-92bd-ea822a7f6053 | textbox | Insulation Condition:
43461a90-5bce-42d3-beae-4948fea250ca | checkpoint | Blue Phase TO R-W-E
5bb945fa-dec0-5934-a30a-f87095ab47cf | textbox | Test Voltage:
10f6fad5-5c21-5468-bd32-979ceea0c281 | textbox | Reading After 1 Minute:
d0cd7728-3d6d-55be-894b-5188bcfc0638 | textbox | Reading After 2 Minutes:
ab0ac166-53ba-5b82-a419-2d272774f778 | textbox | Reading After 3 Minutes:
9afc78f5-8f7e-5c69-8998-8a3ebd592dc2 | textbox | Reading After 4 Minutes:
d7a0febe-9ba5-5842-b7b9-7d1eb42042bf | textbox | Reading After 5 Minutes:
3f10fa1f-35c3-5788-9481-f617d8596886 | textbox | Reading After 6 Minutes:
01ebd851-2440-53ed-953f-91800aa51afd | textbox | Reading After 7 Minutes:
836ba646-6f2d-59ce-8c57-2811f45332c3 | textbox | Reading After 8 Minutes:
e2884b6f-4b50-578e-8dea-6b154fc433cf | textbox | Reading After 9 Minutes:
679fbcad-ff28-5533-95ef-69d78cb31c4e | textbox | Reading After 10 Minutes:
f0d919b3-3d63-5e76-90ac-8ac0348487f9 | textbox | Polarization Index:
3157a760-9992-5ab0-9189-0562df496915 | textbox | Insulation Condition:
7b2d4fcc-ce87-55f5-8fab-9ce380d4f57b | textbox | Insulation Condition Reference Table:
31061a0b-2dfc-50f5-9e5c-242c8e21bfc4 | note | – – – – – – – – – – – – –
9daa4d8b-e188-5455-bd02-4b3724a9f5af | note | Polarisation Index ¦¦ Insulation Condition
44b9d809-b6f3-58b9-bec4-e8c4df52c256 | note | – – – – – – – – – – – – –
907b29d7-2a2d-5004-9657-f16f96092996 | note | <1.0 ¦¦ Unsatisfactory
990b8481-c948-5da1-ad72-3f16676144ae | note | 1.0-2.0 ¦¦ Questionable
f8accb12-654c-506e-a154-563a1a4ad84d | note | 2.0-4.0 ¦¦ Good
b5e7cfda-121a-58c1-8e44-442af1c62676 | note | >4.0 ¦¦ Excellent
12057c24-9b50-5184-a292-0841c5375eaa | note | – – – – – – – – – – – – –
b792b192-2db1-4b58-85e1-dbbd5e28c1c8 | checkpoint-no-value | Technician Name
8eec8460-dc5f-5984-88b6-1b0db97a3467 | textbox | Tested by:
ed8c6de7-b539-50f1-9299-ee77365a55cb | checklist | Pulling Equipment Inspection Checklist |  | Pulling Equipment Inspection Checklist
9d51497a-32d0-5818-9e4b-2d4cf127c673 | section | General details
7f6f856a-61b9-404f-9704-f868669d5ed3 | checkpoint | General details
6316d74c-817e-5711-8f75-447e77378517 | date | Date:
ae2a117e-3252-5a42-a288-7f16cdab9be7 | textbox
c457daaf-7848-5965-97dc-1b78613fd46c | textbox
151fb224-e4d0-5672-bff2-eba4a425ed31 | section | Pre-site Setup Inspection
d04724ca-2955-5e7c-b770-c46fd0f4be7b | checkpoint | Vehicles WoF/CoF and registrations are current
73f3346e-bbbf-59f5-b85e-56df554d9dbb | checkpoint | Cable Drum stand securely fastened to truck
4099c33e-ae2f-54e4-bf8c-e9d54f9d1361 | checkpoint | Cable Drum is in correct rotation (cable end to roll over the top of the drum)
c28785ed-7dfd-57ce-ae25-5266ac3f5479 | checkpoint | Cable Drum is securely fastened to stand
e82bf9e8-6088-5107-b8f3-f7c4d56192e7 | checkpoint | Cable Ramp is securely fastened to truck
9cadbc00-0008-5c54-a167-283808086c48 | checkpoint | Cable rollers are clean and greased
0f175eea-1cef-5842-b8cd-1e772a63276f | checkpoint | Generators are fuelled up and starting correctly
c9a1867a-b076-5e3c-8a27-7373296dbf84 | checkpoint | Hydraulic Power packs are operating correctly
3f66f7da-1e55-565a-b8ca-92ee6c8ae216 | checkpoint | Cable Puller is fuelled up and starting correctly
9991b7eb-c9cd-500e-937c-28cc15c37f8c | checkpoint | Pulling ropes are in good working order
ff4c4e45-a850-5c18-ac8c-627e6088e967 | checkpoint | Communication devices are functioning and operational
e5322261-70e0-55be-abba-87baa36943c7 | section | On-site Setup Inspection - Cable Drum End
8f70841e-cb1e-521d-8975-74026cb32bd7 | checkpoint | Cable Drum stand is securely fastened to truck
e076b10d-6e55-55e7-87d1-e01cb32ce840 | checkpoint | Cable Drum is rotating freely and motorised wheels are correctly rotating the drum
ec7e1c6c-c957-5ef9-81b4-65c9a68b279b | checkpoint | Cable Rollers/Sandbags are well positioned to ensure cable cannot touch the ground if slack occurs
546af70f-20ac-5d13-9cbf-8af2c6423da4 | checkpoint | Bell-mouths are installed at Duct entry
7bcc2378-0202-522a-9213-1239e14070c9 | checkpoint | Lube station setup at Duct entry
b9d19dae-c3e6-5e7d-b721-e30ed9f30f81 | section | On-site Setup Inspection - Cable Puller End
2bde012a-cc1c-5964-a937-236a3e05557e | checkpoint | Cable Puller is in position, Legs are down, Puller is level and securely fastened to truck/ute
54776db4-9bf9-504f-b310-ba35e299a000 | checkpoint | Cable Puller has adequate fuel to pull in cable
3b48d9b5-6b99-44bf-9652-c5f2712ebae7 | checkpoint | Cable Rollers/Sandbags are well positioned to ensure cable cannot touch the ground if slack occurs
6f2e1122-6c1b-43ec-ae6a-1b98d488db10 | checkpoint | Communication devices are functioning and operational
48999da3-078c-43ea-af38-48b9e613d26c | checklist | Screen Continuity Checklist |  | Screen Continuity Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
20881220-f7ab-46c8-8695-7bf876d8f3ea | checkpoint | Date
51ac62df-4a25-519a-bd56-05f909526edd | date | Date:
d1b62727-1f16-4bb3-9dc7-86144f572d68 | checkpoint-no-value | Equipment details
7cc742c4-7401-5fd6-b47b-e649c032de94 | textbox | Equipment:
d31b76c0-a23a-5bd3-abb8-e24cd49308c6 | textbox | Serial number:
410b9098-c716-5fad-b49e-487fddfa7e4f | textbox | Make:
f6d58e84-0a07-4dfc-8c1f-86fbf013132d | checkpoint | Test 1
89e5d871-8dcb-5e35-b144-f668005bc078 | textbox | Phase colour:
d2893114-11fc-5976-974a-1d24d155e1a5 | textbox | Result:
fa8b30b0-957f-4a04-8cf4-d0809d65c438 | checkpoint | Test 2
77c728ee-a166-5607-9209-429a384044e6 | textbox | Phase colour:
0e7376d3-c67b-5c48-b0ea-a7104d969ddb | textbox | Result:
cb107f56-97ba-4b36-b6c1-ee4cb105b09a | checkpoint | Test 3
560a0f0b-e01b-5608-ab50-bceda3302dee | textbox | Phase colour:
adc7a137-ab2e-5295-af50-e991193f9858 | textbox | Result:
c966a889-9568-4c5c-ac06-43b984539d75 | checkpoint-no-value | Technician Name
6b9f2b10-d1db-553c-a5bf-28d252853048 | textbox | Tested by:
5bc31782-bb91-4d36-b8d5-eb49a8d6d771 | checklist | Sheath Test Results For 3Core Cables |  | Sheath Test Results For 3Core Cables
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
334edf19-e542-44c4-ba27-9bd7cac96a6f | checkpoint | Date
5e8daf56-f22d-53c5-b6e2-06ad1f2a7a53 | date | Date:
a1192a90-ba41-460b-b0b9-f38f092dc2fa | checkpoint-no-value | Equipment details
ca9d706c-e8c3-52e9-9878-653a9e66fd85 | textbox | Type Of Test Equipment:
6ed674a9-cd9a-5197-bfd6-04abaacfd2e3 | textbox | Serial number:
b879a46d-1787-56aa-bd35-f64d285cea6b | textbox | Make:
68e9ff4b-8724-513b-802d-554d24100e9b | date | Test Equipment Test Date:
d9739494-b0aa-47a3-957a-247f30b693ce | checkpoint | Test
b3268522-96fa-530d-ab21-15e106fca7c7 | textbox | Test Voltage:
956dca22-b708-5515-a111-b04375a83657 | textbox | Duration:
8a74038a-8f3f-56a7-97cd-2736cd0ebe4d | textbox | Result:
d32291bd-ab16-532f-bd9f-00298614719d | date | Date of Test:
86fc6b1c-bfb2-5c4b-b21f-52b45231324f | textbox | Tested Done By:
01fea2ef-7194-4cb1-a91a-20aa58f85e42 | checklist | Sheath Testing Checklist |  | Sheath Testing Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
0ff44b3d-879a-42dd-b7b2-75add0d1efa0 | checkpoint | Date
ba684863-f354-5576-aa48-fe3d7cb47c71 | date | Date:
248a7d30-9149-42a1-885f-0751dd5fe425 | checkpoint-no-value | Equipment details
3c3e0537-b4c3-5588-aef2-696ce88aa358 | textbox | Equipment:
de4a44ed-5dad-5bbd-9424-5777d0a3972c | textbox | Serial number:
749e97c4-97f2-5af6-9b79-d5beb24727f9 | textbox | Make:
1eb78b9f-2356-42e5-bc18-c6a39cdabf51 | checkpoint | Test 1
90125cd3-b3b0-5a71-b149-54dfafc18b5f | textbox | Phase colour:
d8fee8f8-7a9f-5e53-b9bd-98fe0515a081 | textbox | Test Voltage:
29d54ec6-ed12-5b32-854c-642c6208cd32 | textbox | Result:
35dea0bf-2c15-4467-90fb-85e4f6961273 | checkpoint | Test 2
897474ec-657d-503d-89e8-63ec96efc39b | textbox | Phase colour:
3c49718c-bf4d-5ae2-b170-b23d08c84263 | textbox | Test Voltage:
4c1279a8-2138-5833-bce2-b9983740c3e4 | textbox | Result:
b32d11bf-c4a4-4a97-891a-bdb070651bd8 | checkpoint | Test 3
ecdc2943-0346-515c-b8ec-c4a4519ba255 | textbox | Phase colour:
e214d3a2-1407-5355-b1a1-85e59b22b89c | textbox | Test Voltage:
fc008b16-278a-512f-a939-e8a193ad154b | textbox | Result:
c235d74a-b7e2-4070-8ee3-ec021e81bd2c | checkpoint-no-value | Technician Name
23fb0f26-b3ce-5be2-9326-931bd0cf8db8 | textbox | Tested by:
ad7d0bea-d5db-46d9-af2e-3fbffa5d3efb | checklist | Step Voltage Checklist |  | Step Voltage Checklist
c4f53086-4166-4bfb-b07e-eb81fd5c42d2 | section | Details
38aaacb2-2513-4021-bfdf-6e379f1bfd48 | checkpoint | Date
cd16228b-1c2e-5795-aa45-f854eeabcbac | date | Date:
08aebfeb-644f-41bb-936c-798a2f93fe2e | checkpoint-no-value | Equipment details
78c817f5-0ad9-5ffe-b9c3-0aef3b4a414f | textbox | Equipment:
5863aee6-32fe-5680-a48e-f8913e6a0e76 | textbox | Serial number:
e1e4c26f-1d5a-58d9-b9db-b8b2d5959f0d | textbox | Make:
f8826f7e-8e04-4d71-9a87-f1c83f6b0f4e | checkpoint | Red phase to W+B+E
02696fd5-2c4f-5b2f-8d06-190f5b2a0daa | textbox | Test Voltage:
d4673107-a0d3-5fdd-9000-d6bb1980a25e | textbox | 1st min Test Result:
46d26852-070e-5d44-942b-f24805af90e1 | textbox | Test Voltage:
d43af1a4-cba1-511f-9667-b7643cd5024e | textbox | 2nd min Test Result:
08422196-0ddb-54d5-adc0-cafc9b636e13 | textbox | Test Voltage:
047a1e4f-aba6-5809-9275-99379f1a3fe9 | textbox | 3rd min Test Result:
23ea9141-aaa5-5aab-a50a-aed6f41270c8 | textbox | Test Voltage:
45ea5b8f-4d17-5d57-8195-d48c7177ede5 | textbox | 4th min Test Result:
e7768098-bc14-580c-8e71-55ac0e30889f | textbox | Test Voltage:
40d45379-8aac-5b34-821f-73ad31991366 | textbox | 5th min Test Result:
d6b4deb5-d54f-5b28-ac80-948c1ae391fd | textbox | Test Voltage:
13586c02-9c31-581f-a495-1dd951c2a1b1 | textbox | 6th min Test Result:
b1c257a9-31ad-552b-a69e-369195e5542d | textbox | Test Voltage:
1baaee58-3576-5a0e-8a64-d82738193ebc | textbox | 7th min Test Result:
875bf63c-58f4-501e-8f46-87bd52a19d57 | textbox | Test Voltage:
a610950f-d159-5a55-9c0a-df5c905a793d | textbox | 8th min Test Result:
dbf46284-6b70-5ade-b7f9-a98018abe70a | textbox | Test Voltage:
1db256c3-9386-5539-86bd-c62ce96f2ff3 | textbox | 9th min Test Result:
689c55c5-155a-58ab-bab6-18114e15ad94 | textbox | Test Voltage:
383a3121-9e7b-569b-acbb-6d7783fad9f6 | textbox | 10th min Test Result:
21012eb1-258c-41e5-8d7d-654e76b4820a | checkpoint | White phase to R+B+E
764d743f-dd60-587f-963d-452e7f2bd890 | textbox | Test Voltage:
e08b85ee-2bdd-5775-96c5-be703d70680d | textbox | 1st min Test Result:
81991865-c58f-5aa6-9f5f-e3c76f977330 | textbox | Test Voltage:
e2c8ed60-c2d4-5cde-8024-5ccd7b9e60e1 | textbox | 2nd min Test Result:
a8abb38a-e627-5824-b3a3-f3ef679c033a | textbox | Test Voltage:
3e998113-6ef0-566c-ae5e-33568bb7e2ad | textbox | 3rd min Test Result:
bc4bc70c-bc50-5e53-9fd9-0a4f87ca67df | textbox | Test Voltage:
2175c583-62b5-546a-b93f-3a2b945afcb2 | textbox | 4th min Test Result:
0bdeede4-915e-5d66-92be-fb5d9916cb0a | textbox | Test Voltage:
406eecc2-7627-5f36-8dda-826826bf0f31 | textbox | 5th min Test Result:
54d8ae0b-1dd9-5b56-83d0-404d4c9f3069 | textbox | Test Voltage:
46691894-d689-5693-9692-958040f73632 | textbox | 6th min Test Result:
1ec52c1e-18c4-519a-aab1-80f77cb1d847 | textbox | Test Voltage:
f2af95a2-4231-527c-9c6a-628b4029b74d | textbox | 7th min Test Result:
dc365e92-9ea4-54d3-b9f3-f23fc8a8fc1d | textbox | Test Voltage:
bff300ac-9a67-5567-9ba6-cb60f066f19a | textbox | 8th min Test Result:
928e943f-5e55-5973-8073-c041cbed61a2 | textbox | Test Voltage:
a87ffb53-9811-575b-bfe9-f8cf713c17ae | textbox | 9th min Test Result:
51f6158b-9d74-569b-9244-0b0f1ce5e1eb | textbox | Test Voltage:
b62f825e-9703-52b8-836a-7e2b78ac310b | textbox | 10th min Test Result:
788e64e7-5400-4fd7-92be-1a541cf4b79f | checkpoint | Blue phase to R+W+E
f902d195-f4a6-573d-aa19-5c30b735758d | textbox | Test Voltage:
4a929732-19aa-57d1-92a2-5398932c0911 | textbox | 1st min Test Result:
001987cc-e090-553b-8f9b-0940da1bbbfe | textbox | Test Voltage:
2fde1f28-e95a-5cd2-8294-0b1ba9148726 | textbox | 2nd min Test Result:
4a6b8003-dbb4-5862-9530-0a9963f40c99 | textbox | Test Voltage:
f1dc9f56-da5a-5dac-9c57-9171274c9946 | textbox | 3rd min Test Result:
411af759-04fd-5f21-956f-e594b004da21 | textbox | Test Voltage:
10517f2f-8b3a-5464-a240-d113070e9c63 | textbox | 4th min Test Result:
b77faacd-d833-51ce-89d6-1b1044c73407 | textbox | Test Voltage:
6c2b8bdc-7a76-55df-a01f-314b454d1cb8 | textbox | 5th min Test Result:
897037f0-b863-5c11-9faa-440963ea0ce2 | textbox | Test Voltage:
6608140a-d5ec-5f03-b31e-950841de4e19 | textbox | 6th min Test Result:
729458f2-1419-5cdb-98cc-e17d6af530fa | textbox | Test Voltage:
64179197-276b-56f0-9afe-426fa89e1860 | textbox | 7th min Test Result:
611f2307-12ae-527a-8f8c-2b8273e5a6b0 | textbox | Test Voltage:
ea524c89-2eb0-59f4-8f91-cbaacbddcbad | textbox | 8th min Test Result:
25f81bcf-3a3f-51a2-999f-25f4d5a71622 | textbox | Test Voltage:
539a367b-d736-534c-a892-853c9a79ad06 | textbox | 9th min Test Result:
4cbbb84a-421b-5272-8e98-75bf3f1c010a | textbox | Test Voltage:
5a16c3a3-c2c6-5bd0-bbc1-a05321648e53 | textbox | 10th min Test Result:
3fa1cce6-266d-4996-8f0f-42bccb75c875 | checkpoint-no-value | Technician Name
12c28d50-9a21-511d-8d28-631d88dfa019 | textbox | Tested by:
bb21bd02-c353-4ab6-9d80-7763d4a1dd25 | checklist | Switchgear Installation Checklist |  | Switchgear Installation Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
49026627-f642-40e4-a128-5b4a4163aeda | checkpoint | Visual Inspection
7c16ae2e-3a30-4a3b-b10f-f2c774bd024d | checkpoint-no-value | Switchgear Make
96002e8c-0cda-5fa2-a86f-908c673dee1c | textbox
c14cb3e8-2d59-4cdc-a68d-f558fa9354cf | checkpoint-no-value | Type
47c8a9e3-59cc-57dd-9b78-ad4fb8cf1762 | textbox
60db1a02-949a-48de-9c0a-3b72879dc3d7 | checkpoint-no-value | Date of Manufacture
7726afac-f6bb-529b-b2e5-3d28c68e1d8b | textbox
bbd6b6f2-aa44-4f47-9c61-730498e69d92 | checkpoint-no-value | Serial Number
2e0d3a4a-7a15-5bef-b8fd-104286d576b3 | textbox
3fa8d721-7aff-484e-835d-0cb653db7951 | checkpoint-no-value | Switchgear System Number
535567ab-a406-57f1-ab07-7fc35344a2b6 | textbox
6a4ff850-4095-4cbd-870d-4f43bdf97a32 | checkpoint-no-value | Voltage Rating
91d29de5-5892-59cf-9ae8-11092166915e | textbox
154e0b1e-6b7f-4d9d-abec-383267be5540 | checkpoint-no-value | Current Rating
fb35cf50-12db-5486-817d-47bd6e1ed6a8 | textbox
4887ca4a-05ca-460e-a005-a88ee46dd812 | checkpoint | Switchgear Secured
df8f74aa-be6e-4c18-b94c-d4395a4c0f45 | checkpoint-no-value | Date Installed
cb392cca-0ccb-5407-8801-3a154dc69436 | textbox
740da860-4e57-5a35-be89-c897d70a14b0 | checklist | Transformer Installation Checklist |  | Transformer Installation Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a3a62083-419c-55e2-adbf-73bcf947b62e | checkpoint | Visual inspection
b72140f8-b6fa-5e33-8daa-4c09c3542352 | checkpoint-no-value | Transformer serial number
26626e67-2d21-567e-95c9-52607932999d | textbox
b407dcb5-47aa-5b67-9262-e746e6bb7c65 | checkpoint-no-value | Transformer reference number
5f97f470-8c67-5522-bb3b-0aee477c0920 | textbox
43f0d047-c645-5849-991f-5830ecc78d48 | checkpoint-no-value | Transformer Rating (KVA)
474feabd-03ea-50f8-b48c-9c783e4858e5 | textbox
7486d397-f98d-596d-8840-50c0b97f6d0b | checkpoint-no-value | Voltage ratio
242d2c33-3ec7-549d-893f-b96ec75223a5 | textbox
f4f3d635-9779-5ec3-99ef-6579482aa4ad | checkpoint-no-value | Type of mounting
a0a925c4-e634-510c-8156-5b2779de58a6 | button | Select: | Pad Mounted, Pole Mounted, Platform Mounted
924c155a-9779-56d1-ae28-27b0e715c552 | checkpoint-no-value | Transformer secured
f7c25b90-130e-52c1-8b99-50d7eeb61545 | button | Select: | PASS, FAIL, N/A
222547d6-7697-5d76-9538-100e91177edf | checkpoint-no-value | Date installed
52647426-137e-5cb6-aae4-ba9409bb52f1 | date | Select:
6624eff6-3a52-46d6-be73-90c27b959f1a | checklist | VLF Testing Checklist |  | VLF Testing Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2ddee5ac-2dc6-44d6-a85f-333dc65b39ae | checkpoint | Date
f8adb130-b988-5f9b-85a6-109f7db0ebeb | date | Date:
bb7a9ba5-6989-42fb-aa89-3b855af910fb | checkpoint-no-value | Equipment details
fb4f6ff8-6cb3-55e3-afea-ad7ed2ee8263 | textbox | Equipment:
a02055f6-24be-5673-bd87-d0a2fbcb6d01 | textbox | Serial number:
621699b3-86e8-5912-a699-c0c793ad85cb | textbox | Make:
b36e4bd4-a13f-4124-9a04-4e5040d70982 | checkpoint | Red phase
9b097f54-1752-5d5d-a326-010d159aa6c4 | textbox | Test Voltage:
9153fd33-b5bc-5d1a-b8a8-92d26694c98e | textbox | Current:
52813c21-2719-59fc-9294-69c4508dbeee | textbox | Partial Discharge:
e21df313-7466-50d7-83af-177b226ca199 | textbox | Duration of test:
3706e4db-c99e-5a30-97b0-7667d47a494d | note | VLF frequency chart:
c4eb8a12-aa00-53f3-944d-0e579d565413 | note | 0.01-1.1 microfarad > 0.1 Hz > 30 min
4ee7ce1c-367a-5bc9-93c2-c2b9d9f992dd | note | 1.1-2.2 microfarad > 0.05 Hz > 60 min
c9ccf9ce-ab58-544c-b035-3faaea7725a6 | note | 2.2-5.5 microfarad > 0.02 Hz > 90 min
6df65bac-9ef9-44f7-ad95-7ea0149804b4 | checkpoint | White phase
6dca77a5-92f7-5fcc-9107-f53bd1073de2 | textbox | Test Voltage:
0e90c6cc-323a-5162-b6b4-434f32070f14 | textbox | Current:
ca13db7e-d582-51cf-a31a-06a39b6217a0 | textbox | Partial Discharge:
0ec43125-d36a-580b-a78b-a59e5852a32d | textbox | Duration of test:
4c61e20f-0416-5306-bd5c-68fd495d10f8 | note | VLF frequency chart:
0e67cad3-17b6-5550-984c-9a766d7f4e96 | note | 0.01-1.1 microfarad > 0.1 Hz > 30 min
f35d7ca7-eb24-56fa-ace4-920603965ce9 | note | 1.1-2.2 microfarad > 0.05 Hz > 60 min
a6bc8dd2-4e79-5120-811f-3fd9a75051c5 | note | 2.2-5.5 microfarad > 0.02 Hz > 90 min
2a7a5711-9d75-4f71-8407-1d7c10070237 | checkpoint | Blue phase
04ce581e-c7c2-5da4-9bbf-0b22d8fed6ec | textbox | Test Voltage:
c3426e0d-f325-5478-a2cc-ccc190dd87fa | textbox | Current:
bfe6d4ba-2045-51ad-a36f-306eeb93d27f | textbox | Partial Discharge:
16023a1f-16ca-5bf0-8a30-713ef2f9c5ba | textbox | Duration of test:
2da69957-6167-50c6-a9af-25f04f721014 | note | VLF frequency chart:
4d3c59ab-198a-529c-b89e-f949028188b1 | note | 0.01-1.1 microfarad > 0.1 Hz > 30 min
0934bd70-662c-534e-a2c3-51efaf692345 | note | 1.1-2.2 microfarad > 0.05 Hz > 60 min
9baa64b3-6f99-5989-a4e3-9164976dc9d0 | note | 2.2-5.5 microfarad > 0.02 Hz > 90 min
5f821388-5a82-4765-bb8b-c6734213853b | checkpoint-no-value | Technician Name
12f840b0-4bfe-5f75-826b-71ae31d5e85f | textbox | Tested by:

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix
df560535-05d6-53ed-90e8-dac5c55a8a59 | checklist | Cable Sheath Test (Gas) Checklist |  | Cable Sheath Test (Gas) Checklist
7e63d02f-df3e-524f-804b-9471c364e492 | checkpoint | Date
a08924d8-3c72-59da-aba4-30e9d874bef1 | date | Date:
21489731-6d48-53b4-8a4a-f6019ca50060 | checkpoint | Gas Pressure Applied (PSI)
be560e7b-a23e-5f1f-a2a5-b95b153c4954 | button | Please select | 10 PSI, 15 PSI
8f9184e2-7020-5ada-bb52-350528e8399d | checkpoint | Gas Pressure At Start Of Test (PSI)
93bb7fe7-353f-583a-ab8f-09489f12632d | textbox |  |  |  | PSI
b9df6d0e-d8bd-5432-84a1-54fe5c762342 | checkpoint | Gas Pressure After 30 Minutes (PSI)
17f523bc-c680-5074-b098-d44bae05279b | textbox |  |  |  | PSI
6c5641a6-9238-544b-9492-116cd8840d31 | checkpoint | Gas Pressure After 60 Minutes (PSI)
fd62779b-bc22-53f5-950a-f7d95d2d682f | textbox |  |  |  | PSI
e70506c9-400b-5dbd-92db-8895323d6def | checklist | Neutral Earthing Resistor Installation Checklist |  | Neutral Earthing Resistor Installation Checklist
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a3a62083-419c-55e2-adbf-73bcf947b62e | checkpoint | Visual inspection
6e39a814-37cb-5875-acbb-f6e233117c8f | checkpoint-no-value | Serial number
791631f2-10c6-5332-a696-f5cf0466d702 | textbox
e656a1fb-97b9-59f7-a17f-d1e84f953153 | checkpoint-no-value | Voltage (L - L)
41a38a91-3592-5d01-82bd-a7f84f9d0bf4 | textbox
ecbc75f2-0b1c-540b-b05c-335fb32c4716 | checkpoint-no-value | Voltage (L - N)
e5d531e1-d0f3-552f-b5b0-dcd6d3790734 | textbox
7c797015-ecbf-5d06-abb2-0ee785d17813 | checkpoint-no-value | Rated Current
d95e4cac-d946-5d4c-a6b9-6ffbed05f259 | textbox
6a82fd5d-120f-5c66-b037-a0951e2a45c1 | checkpoint-no-value | Ohms
4f3d0443-4c04-5c89-b089-029d0ecc39c5 | textbox
f4f3d635-9779-5ec3-99ef-6579482aa4ad | checkpoint-no-value | Type of mounting
106ef3eb-a304-5530-bd34-20efae517301 | button | Select: | Pad Mounted, Platform Mounted
27f06ef2-8718-5147-99b0-ceb76b9ab6c7 | checkpoint-no-value | Neutral Earthing Resistor Secured?
e3a47abf-8c69-531d-a9ed-e0a2d88cdfbd | button | Select: | PASS, FAIL, N/A
222547d6-7697-5d76-9538-100e91177edf | checkpoint-no-value | Date installed
61ff4619-bc1c-5bae-a394-d955104bef5c | date | Select:
f92edbb5-7a36-544d-b8d1-c15ede84b398 | checklist | SYS - IR Testing For Single Core Cables Checklist 1 |  | IR Testing For Single Core Cables Checklist 1
7e63d02f-df3e-524f-804b-9471c364e492 | checkpoint | Date
e4d9406d-31cf-5760-92fc-bbe3133613a4 | date | Date:
6bc6ba91-5f23-5060-b66a-adc44c5a15e2 | checkpoint | Red Phase 1 - Screen
f3517135-7f7e-5ab4-8902-cd9ab7a89b7a | textbox | Test Voltage:
459c6b86-3f04-5bd7-94be-9f80da0b8abb | textbox | Result:
9e5aa29f-7d06-5a84-a389-002b7ecdda78 | checkpoint | Red Phase 2 - Screen
4436e177-5549-5223-90cc-91fc0b435f55 | textbox | Test Voltage:
dec148f6-4b47-557e-959b-3f6c0f82599b | textbox | Result:
45c24efb-95f9-5a1c-bcfa-1e2488edc000 | checkpoint | Red Phase 1 - Earth
d28ded27-3bd8-58a3-b996-91689ac46af7 | textbox | Test Voltage:
718660bd-f388-5670-82e8-e7ecc1327c6a | textbox | Result:
6c208e1a-c0a9-5d87-9ddf-89b21809616d | checkpoint | Red Phase 2 - Earth
47072b0b-872f-5afc-b85d-73f68b2e7e0b | textbox | Test Voltage:
40216d13-a2bf-5afc-8aa9-455375a654d3 | textbox | Result:
4584ae1e-78a1-5a59-a791-2cd0568c4652 | checkpoint | White Phase 1 - Screen
2063b6bd-1da8-5a21-b0b9-fd36b3e9e16e | textbox | Test Voltage:
7f225422-5005-50aa-9f01-25dd422a45d8 | textbox | Result:
b36469b8-9070-5c1e-8af7-78ae32bec08d | checkpoint | White Phase 2 - Screen
f77a793b-e8a8-52b1-bbc8-bd38e4cf3670 | textbox | Test Voltage:
ef63e623-5716-5d04-b645-ba7656e8a2f4 | textbox | Result:
7e8c9f05-507e-542b-82b7-e49e9dbcb8f8 | checkpoint | White Phase 1 - Earth
6b15984b-6e44-5325-93d2-ac3e4cf1a526 | textbox | Test Voltage:
dd88e216-7b7c-5d95-b140-5c922b92726e | textbox | Result:
af50cd6d-36d3-598b-a072-633a2bab4628 | checkpoint | White Phase 2 - Earth
19ec9a71-83a8-5ce4-b46a-5196c0377287 | textbox | Test Voltage:
caafcdd3-809c-5661-9fc3-3f2123fa2508 | textbox | Result:
7771e78e-8e40-5a55-be67-25d124701e6d | checkpoint | Blue Phase 1 - Screen
7f85c7b9-70d7-5886-88ce-f4f3325cd37a | textbox | Test Voltage:
89fea5f8-19bd-5cb2-835e-1cb526123713 | textbox | Result:
59abbd6b-7aeb-5d1f-9ba6-fdcd91cbd48b | checkpoint | Blue Phase 2 - Screen
f6d45097-21f0-5ca2-8f29-d19e5a1d1a07 | textbox | Test Voltage:
01f82862-d264-54a0-862e-b5b427b2655a | textbox | Result:
32f75d30-c48b-576b-8d6a-8a672ef52311 | checkpoint | Blue Phase 1 - Earth
9f77d50e-4cbc-5e12-b20f-04509c4686dc | textbox | Test Voltage:
db6c2edc-8f7e-585f-9027-94874ffc1001 | textbox | Result:
7eab31b3-7ef4-5448-9eda-f992bb1e8034 | checkpoint | Blue Phase 2 - Earth
5c27a2da-1d54-5641-bf37-2e4991a9ed23 | textbox | Test Voltage:
a2e32b3e-a2db-5f16-be01-e92c947249b1 | textbox | Result:
9d6d7171-a23b-5dc7-a6e4-84c9337f206e | checklist | SYS - Screen Continuity Checklist Between Pole 173459 And Pole 201792 (Back Cables) |  | Screen Continuity Checklist Between Pole 173459 And Pole 201792 (Back Cables)
7e63d02f-df3e-524f-804b-9471c364e492 | checkpoint | Date
d160df9f-8108-51ea-a6b0-0b151c7c2b2b | date | Date:
149906b5-90e3-5e9b-ad91-2fb3e6b0136d | checkpoint | Test 1
801147d4-836d-5802-a42b-e96c58926e17 | textbox | Phase colour:
d6bf1d28-d710-543b-aaca-b980c028cfe4 | textbox | Result:
12f2501c-4e3e-5d1d-8c10-d7cb896dc86f | checkpoint | Test 2
e15eda9f-198b-5b48-bf0d-17c8595fe7b4 | textbox | Phase colour:
1f6299fa-56da-54cc-ab2e-9a8a43e2c112 | textbox | Result:
f4e2a2e2-c3bd-5ffd-9572-ac37a3fef314 | checkpoint | Test 3
0587f960-f82a-54a9-a8e1-a895324e5b5a | textbox | Phase colour:
e516d8e9-686e-54fb-b6fd-1e07d44ff012 | textbox | Result:
a67145f6-debc-5cd6-aea4-9ccb419a7e62 | checklist | SYS - Sheath Testing Checklist 1 |  | Sheath Testing Checklist 1
7e63d02f-df3e-524f-804b-9471c364e492 | checkpoint | Date
3a01325c-241b-5e36-b22d-e0db7b6c774e | date | Date:
149906b5-90e3-5e9b-ad91-2fb3e6b0136d | checkpoint | Test 1
717cfda5-760f-506c-a148-2cb905a4dc63 | textbox | Phase colour:
d530ef71-d23f-5252-8654-c6cbc2f97bfb | textbox | Test Voltage:
28564bba-8741-5124-9f4f-094e0fed2a7d | textbox | Result:
12f2501c-4e3e-5d1d-8c10-d7cb896dc86f | checkpoint | Test 2
f0a32192-aa97-5925-80bb-4bed7224d527 | textbox | Phase colour:
a08413e6-4dc2-59c0-af0b-bf246358e45d | textbox | Test Voltage:
7ff995ec-c70f-55cf-a17e-39d8572177ca | textbox | Result:
f4e2a2e2-c3bd-5ffd-9572-ac37a3fef314 | checkpoint | Test 3
b2937bf3-1c5d-5b21-a9b4-ac9181c93a4f | textbox | Phase colour:
3a575a97-696b-5379-b03f-a318f9fbe5aa | textbox | Test Voltage:
34fca705-5f2a-55bc-84a2-c5f70816a574 | textbox | Result: