## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
8cff2206-129e-4644-90b8-be16ef09adb0 | checklist | DN1211-001 ITP Stormwater Rev 0 | itp | DN1211-001 ITP Stormwater Rev 0
2d4d7028-cc67-47fb-bc4a-85c5fb76d593 | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
4527df09-8192-41d9-91e4-0a524ba75d96 | checkpoint | 3.01.01 - Construction Pack
ed941b59-045d-5324-935c-4edacad53d24 | note | Acceptance / Conformance Criteria - Submit a Construction Pack including a Methodology and JSEA to the Engineer before works
7607b137-0671-51a1-951e-8fe699bca7cf | note | Standard / Specification - Downer
1a261d26-8d45-54cd-974c-ca5bb4ac14e5 | note | Verifying Document - Construction Pack
dea16211-027b-5047-9162-7ec4d561fef0 | note | Frequency - Submit 5 days prior to commencement of works
e9ed4920-b239-5865-b2fa-0990017f31df | note | Verification Activity: Activity - H
a5d7357f-7bdd-5493-86b3-a183043befc6 | note | Verification Activity: By - PE
0f7a9e73-1447-4c56-b835-e7944a700dd0 | checkpoint | 3.02.02 - Survey Setout
560b023e-147d-55a2-8e7a-6f19ffb12b8f | note | Acceptance / Conformance Criteria - Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed.
4a613baa-0a12-558a-9c2d-7fd82d39c8f2 | note | Standard / Specification - Downer
ae9eaa9a-093e-5ab9-9194-2e331e70a97f | note | Verifying Document - Survey Records
c218bedd-8cca-5021-8535-712a63f6ba1a | note | Frequency - Prior to Works
331200dc-2a8c-5760-bf25-c2480cb1e2e3 | note | Verification Activity: Activity - H
2c23c83f-acf0-5b8d-a45d-f108326dc0ea | note | Verification Activity: By - SV
bfe23b37-5f1c-4380-b939-e4ed0c30ac3b | checkpoint | 3.01.02 - Service Location
4c237af8-4b41-5255-a9a3-16dc1c9cb2f9 | note | Acceptance / Conformance Criteria - Complete the Excavation permit process to identify, locate and protect all services.
70b89522-a4f1-59a0-a34a-0763adc06ad0 | note | Standard / Specification - Downer
2fc828f2-420d-566d-bf73-eeb8dee67d5e | note | Verifying Document - Excavation Permit
ab07887f-321d-5f8c-90d1-45ba4fd516de | note | Frequency - Prior to Excavation
8a58eb97-5274-50e7-adf9-f0281a9d1263 | note | Verification Activity: Activity - H
d3bc6fa7-571e-57a9-9f9c-a1f93196bfc6 | note | Verification Activity: By - SE
4f68fe33-f844-431a-a65d-f2861ef54a9c | checkpoint | 3.02.03 - Internal Permits
a347d2b0-a5ba-55b1-9e68-bfd7c210480a | note | Acceptance / Conformance Criteria - Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc.
4d2a1a95-aec1-51d6-927c-a766ee451138 | note | Standard / Specification - Downer
6e7adeed-b1bd-5543-8106-9a55f1345623 | note | Verifying Document - Internal Permits
85667c04-f2ca-5162-97df-39d3d645efdd | note | Frequency - Prior to Excavation
edd023ec-719b-5ce7-b19e-16a2885d6309 | note | Verification Activity: Activity - H
76da0f14-88c5-5dca-8c1d-05244ea3889b | note | Verification Activity: By - SE
321ebddf-81df-4ed6-91a5-aef27fd4ed7a | checkpoint | 3.01.03 - External Permits
467ca4c7-a6dd-5676-bcb1-2e7a71015ad7 | note | Acceptance / Conformance Criteria - Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc.
79a18264-8b33-5111-81b4-a0a57702ebde | note | Standard / Specification - Downer
12b31bbf-e3f9-5351-8e68-cacdbfa3358d | note | Verifying Document - External Permits
0c3697d8-606a-5355-88b4-ddff917a49e1 | note | Frequency - Prior to Excavation
85ad7aba-b471-542e-9548-bf1406fb8e7f | note | Verification Activity: Activity - H
19b250c0-3c4f-521b-bc99-55e8680c70b3 | note | Verification Activity: By - PE
5c76e8e8-367c-46b3-b7ab-81bf7505081c | checkpoint | 3.02.04 - Approved Construction Drawings
44e9c8ba-e41e-5511-8474-4941676b1db9 | note | Acceptance / Conformance Criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
9b958b4c-d9cd-5460-9bd7-e0ba192ad0e6 | note | Standard / Specification - Downer
95dbed92-8d36-5187-b9f1-f7f29077e822 | note | Verifying Document - IFC Drawings
188acaf8-10f8-5fb7-b161-ddf2b5eee7b5 | note | Frequency - Prior to works start
cca3b916-fec5-57fa-a8fd-438689df35ab | note | Verification Activity: Activity - H
f7e4c0d9-2353-537c-aff2-ab5a287ae4c8 | note | Verification Activity: By - PE
b4243508-5f7b-4b84-acaa-52db86020dfa | section | SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
195eaba4-e2c8-4dab-9b1a-f403d94170f1 | checkpoint | 4.01.01 - Concrete pipes
9adc9a2d-045e-5e23-a8ac-539783ed6e25 | note | Acceptance / Conformance Criteria - RC pipes shall comply with AS/NZS 4058 for the class nominated on the drawings.
4cefca3e-c621-5384-a3a7-52d9d3957ef4 | note | ○ Pipes shall be rubber ring jointed unless otherwise shown on the drawings and rubber rings shall comply with AS1646.
4b3af587-9683-5923-b97a-2bfc64d92402 | note | Standard / Specification - Aurecon Civil Spec Section 17.11.1
d957498e-344a-57b7-bc91-3d990a19576c | note | Verifying Document - Material Certificate / Datasheets
bac41fe5-9ce6-59c4-b3ab-d1c73971b886 | note | Frequency - Prior to use
ac78369b-cfc5-5723-96e4-2361a3ea32fb | note | Verification Activity: Activity - R
4448271c-aec9-5d34-8708-fcdef0f9b7ee | note | Verification Activity: By - DES
a1d7b594-a2e5-4b36-9cdd-49a30fa661b0 | checkpoint | 4.01.02 - uPVC pipes
f0683e84-9738-50b3-a41d-35b92162d092 | note | Acceptance / Conformance Criteria - uPVC pipes shall comply either with AS/NZS 1254 or AS/NZS 1260 and have the minimum strength as detailed on drawings
34947458-a0d6-5828-ba75-4190b714238e | note | ○ Pipe joints to be factory‐made spigot and socket, flexible type
8b2d6460-6cff-5daa-b6e6-7f8288a29694 | note | Standard / Specification - Aurecon Civil Spec Section 17.11.3
2f44b398-a028-5729-9e98-860cb7cc8c61 | note | Verifying Document - Material Certificate / Datasheets
84214fde-6e5e-5352-9163-1b824e0d5510 | note | Frequency - Prior to use
fcdf153b-3aca-58c7-a3bf-d188895bcd64 | note | Verification Activity: Activity - R
9bb0cce1-3ec6-5419-8760-d7c55f74dc34 | note | Verification Activity: By - DES
7e0ecffd-10d8-4ee8-8516-79c11f006f55 | checkpoint | 4.01.03 - PE Pipe – Profile Wall
9a308a55-0860-5992-9be5-44b36c805e80 | note | Acceptance / Conformance Criteria - PE pipe to be used in gravity situations shall be PE100 Profile Wall pipe to AS/NZS 5065.
aed94f90-05ff-55a9-91c5-c36e1f1afcbc | note | Standard / Specification - Aurecon Civil Spec Section 17.11.2
35bad388-3360-5371-b7d9-77932a998b8b | note | Verifying Document - Material Certificate / Datasheets
6cad8bac-24a2-58fa-a02e-35d4e65dc46f | note | Frequency - Prior to works
a04ea7b9-a44d-5eb9-8261-97022c172090 | note | Verification Activity: Activity - R
b9872fda-1592-5ae4-941b-92c0d17856e2 | note | Verification Activity: By - DES
bd47eec3-a6f8-49ca-805c-35fcbc826807 | checkpoint | 4.01.04 - Other Specialised Materials
23d596fc-3fa7-5ae4-a8c0-c4b3e8b0ffde | note | Acceptance / Conformance Criteria - All other pipes and pipe fittings supplied as per drawings, including:
8d607cc9-c0b6-5df4-b5fc-7a77c38c3ccd | note | ○ Any Mortar Lined Mild Steel (MLMS) pipes manufactured from arc buttwelded steel tube with external black HDPE coating. Pipes joints to be flanged, welded hemispherical joints or jointed with welding bands.
be72994b-f283-591d-a395-ca199073eac8 | note | ○ Gibault Joints assembled as per manufacturers recommendations
3eb05f78-a6db-5899-8f27-69377fc491cc | note | ○ Flanged Joints made with moulded rubber gaskets or jointing rings as per spec. All proprietary products supplied and installed as per manufacturers instructions.
26689c0a-4f0e-5284-9764-c5cb9f2e9ac4 | note | Standard / Specification - Aurecon Civil Spec 17.11.5,17.11.6
737bfd8a-2e51-50a6-8bb2-b254641c9aeb | note | Verifying Document - Material Certificate / QA Sheets
f7d167bc-441a-50fe-a6ae-2bda3a7f34e9 | note | Frequency - Prior to Use
911ec583-2bc6-5bfc-820b-45d0ad9e6435 | note | Verification Activity: Activity - R
a28b0823-fdf8-55cc-8bd4-2d6e9f9cda4f | note | Verification Activity: By - DES
72a56231-7abc-44ef-885c-6aaf5ad520f1 | checkpoint | 4.01.05 - Concrete
127c0086-aff3-57e8-9c26-e03167393225 | note | Acceptance / Conformance Criteria - Any structural concrete or mortar mix requirements as per Section 14 of this civil spec.
9819d098-86ad-5654-bd5b-242509481579 | note | ○ Site concrete used for pipe bedding to be 1 part cement to 7 parts AP20 with water as required to produce firm, moist mix with min 10MPa 28‐day strength
7defe212-9dbe-50da-976a-ab20cf25d894 | note | ○ Arrange pre‐pour inspection with Engineer 1 day prior
506a82f4-c60f-51c6-a67c-56c06132ec5a | note | Standard / Specification - Aurecon Civil Spec Section 14,17.11.7
cd472632-f0f8-5553-a4d1-1cc26f09f46d | note | Verifying Document - Supplier Records, Concrete Dockets
149e14bd-6c58-531f-b542-fe6bfbc6d42a | note | Frequency - As required
7ed4c668-3f4f-5693-8b1e-9d8a5fcac2a3 | note | Verification Activity: Activity - H
3745e15d-fe1e-5e5a-8359-2e5960a922b7 | note | Verification Activity: By - PE
2b22b82a-c061-4034-995c-408cdd287b85 | checkpoint | 4.01.06 - Pipe Bedding and Backfill Material
debfae14-ef3a-55b5-98fa-91e693499337 | note | Acceptance / Conformance Criteria - The basecourse aggregate shall be sampled and tested by an IANZ Accredited laboratory for Crushing Resistance, Weathering Quality Index, and California Bearing Ratio.
a03d4765-5fb9-5c33-945c-d1720efc57d5 | note | Standard / Specification - Aurecon Civil Spec 17.12.15 TNZ M/4 Asset Owner Specifications
1364df2c-b6ed-5467-8ab4-0e54e447ce09 | note | Verifying Document - Material Certificate / QA Sheets
ce51d16b-059d-5684-8ab9-3b333f0090ff | note | Frequency - Prior to Use
c5b9cfa1-d202-57f0-b540-98d5abc01437 | note | Verification Activity: Activity - H
6cfc08a5-cc34-5264-8174-e6086579958d | note | Verification Activity: By - DES
cbcfc19c-9f81-4dfc-8f81-af17e67834f4 | checkpoint | 4.01.07 - Catchpits, manholes, and drainage structures
233fa766-7dd9-5a5f-b80c-37865b637a36 | note | Acceptance / Conformance Criteria - Manhole, catchpit & service pit frames and covers supplied and set to correct grade and finished level as per drawing details.Pre‐cast items manufactured and supplied as per NZ standards. Manhole segments to be minimum 20Mpa
8eedeedc-6c24-5800-9c29-160f7e065735 | note | ○ Manhole/service biscuits to be level with top of subbase.
6647dd47-6eda-590e-b7f7-dee6b0f2fe72 | note | ○ Re‐entrant corners require trimmer bars as detailed on drawings
95968c82-1db1-555c-8676-b97f79074adf | note | Standard / Specification - Aurecon Civil Spec; Section 17.11.16-18
cf6888f5-b4c9-5ca6-8f5d-daa500bcef3f | note | Verifying Document - QA Checksheet and Supplier Records
66a52d92-9afe-5042-8b89-7f159e8e617a | note | Frequency - Prior to place pavement concrete
bdb90f46-3150-5a49-8a21-2eedb579311e | note | Verification Activity: Activity - R
f64ca9f9-233b-5451-a09a-2eed002bb5dd | note | Verification Activity: By - PE
fdcb322e-f85c-432a-8b42-e0f44f21d46b | checkpoint | 4.01.08 - Step Irons - Access Ladders
1585664f-66c4-5f44-b291-8be4da1ffb82 | note | Acceptance / Conformance Criteria - Check if amended by Drawings to be Type 316 Stainless Steel or Plastic Coated.
f2163e57-1279-5bab-9bb4-f79a1bde9a7f | note | ○ Otherwise, Step irons shall be “safety type” 24mm dia mild steel to the dimension shown on the Drawings, galvanised after fabrication at the rate of 0.7 kg/m2.
2f11480c-647a-5753-a120-cabeddf52a92 | note | ○ Installation shall generally comply with section 5.7 of AS/NZS 1657 except that ladder cages shall not be fitted
95ab47bf-2125-591c-9a2c-e8f7bab25acc | note | Standard / Specification - Aurecon Civil Spec Section 17.11.19
03f3f629-b02a-5fbf-b5c3-4d4a3f4c41d6 | note | Verifying Document - Supplier Records and QA checksheet
0dde39a7-86a2-5525-8b83-3d832eb6e3ee | note | Frequency - Prior to use
64df4f6d-5416-5dd9-8fff-99a21a97493f | note | Verification Activity: Activity - R
b2d03611-494e-5951-a765-cf6135780868 | note | Verification Activity: By - PE
ff1b383d-b706-431d-9ae4-42b8e629d255 | section | SECTION 5 – CONSTRUCTION ACTIVITY – DRAINAGE INSTALLATION
9d4d0c9e-435e-48f6-84db-f2992a12a460 | checkpoint | 5.01.01 - Protecton of Piplines
f78a821e-415f-5e2e-b73d-12755d4c10c2 | note | Acceptance / Conformance Criteria - During construction, the Contractor shall be responsible for the protection of all existing and new pipework.
79d110c4-a6f1-5a7b-9c4a-d4bb116e1575 | note | Standard / Specification - Downer
d5f090a2-98e9-5bb5-9c33-317628bfec03 | note | Verifying Document - QA Checksheet
7aa323ce-0bf2-51aa-bed4-bea82733419f | note | Frequency - Daily
e11d4164-f482-5196-b2f6-cfe5399e7ed0 | note | Verification Activity: Activity - I
bb8094cd-984d-53e2-ab88-a054c27a114a | note | Verification Activity: By - PE
a345a459-81d5-401f-9b6c-5efc0032e920 | checkpoint | 5.01.02 - Depth of Cover
243d57b8-72c2-5de5-8e07-495866fa8eb0 | note | Acceptance / Conformance Criteria - The minimum cover as detailed on the drawings.
52dd0f39-9f8f-5b99-9415-0d0f0bb8259d | note | ○ If minimum cover cannot be achieved notify Engineer and provide adequate protection to the satisfaction of the Engineer.
f932b781-7a84-51f9-8eb8-5480477b8911 | note | Standard / Specification - Aurecon Civil Spec Section 17.13.17
63690037-5f08-537e-b78f-7239f40fa81e | note | Verifying Document - Site Record
cb9cd2d0-c8d0-5f02-b5f3-c8f666eacf4f | note | Frequency - During Installation
0e7f727e-040d-5830-a7ad-691f2a2c6464 | note | Verification Activity: Activity - R
378d59e2-471b-5ae4-9551-fa2d5219ec41 | note | Verification Activity: By - SE
782406fe-3996-4549-8990-75ef934d7938 | checkpoint | 5.01.03 - Length of Open Trench
be4d85dc-0814-58ae-b359-044c531fa8f1 | note | Acceptance / Conformance Criteria - The length of open trench shall not exceed the greater of one manhole length or 30m and when offsite this open trench shall be reduced to a maximum length of not more than 10 metres.
c1fc1e3f-0427-5c6d-8d7f-ceed5d0837aa | note | Standard / Specification - Aurecon Civil Spec Section 17.13.3
f60db694-6383-5f4c-8200-de2a6a2562b0 | note | Verifying Document - QA Checksheet
b02390a5-ab99-5a50-9c7c-467ae16684f5 | note | Frequency - Daily
cc9e8e61-6d2f-521e-9214-3253db507e97 | note | Verification Activity: Activity - R
a65c64cd-9b3b-56cd-887c-d2a6ae05f037 | note | Verification Activity: By - SE
5b80427c-41a2-40c3-b07c-5a2a6584f46d | checkpoint | 5.01.04 - Trench Dimensions
7bbb3f16-a2d4-57be-b31f-e6d1fd87fe10 | note | Acceptance / Conformance Criteria - Excavate trench to lines, levels, width and gradients shown on drawings.
9b504735-98aa-5d86-a5d7-1db6b1b9cceb | note | ○ Trench of sufficient width to permit installation of all materials and fittings.
a874d695-57ab-5bb3-b931-01c9114413f3 | note | ○ Pipes minimum 100mm from trench wall.
492749dd-1523-5761-b1b5-d6da9aa5d14f | note | ○ Trench width <600mm pipe diameter at top of pipe level.
29734e0c-11ca-5ec5-8e90-7f62f02dac9c | note | Standard / Specification - Aurecon Civil Spec Section 17.13.4
8c7ca7c7-788d-511b-aa79-e1397c8aeff1 | note | Verifying Document - QA Checksheet
b21a2c41-b238-5a2d-adf3-6f9bdc934c18 | note | Frequency - Every 10m
9416b7bc-a97d-5f66-bc1c-8a231bdfbd3d | note | Verification Activity: Activity - R
1eafbd54-b51c-50ce-b6ee-98564bf17c0f | note | Verification Activity: By - SE
5fdf8d9e-095f-4361-89bb-27b8cb8ec707 | checkpoint | 5.01.05 - Keeping the Excavation Free of Water
1a850783-2d0b-582e-a04f-6a1c76590acf | note | Acceptance / Conformance Criteria - Subsoil water shall be kept below the metal foundation
141cf7f6-e550-5f0f-af0e-a79cb3d9383f | note | Standard / Specification - Aurecon Civil Spec Section 17.13.5
1cd856c6-f750-5b18-a059-93049a8ed452 | note | Verifying Document - Site Record
2fac5181-acf0-57ba-b625-13a4d0d8672a | note | Frequency - Daily
69db99de-4638-53fe-99bf-b4a5cb5f4e8a | note | Verification Activity: Activity - R
9849c5af-a222-52aa-bac6-f9d48347e9c0 | note | Verification Activity: By - SE
89ca5935-9df6-4b6a-83c0-313c4a7c8d7a | checkpoint | 5.01.06 - Trench Subgrade
045a70b3-71d5-5287-b9e6-1d9ecd5a009d | note | Acceptance / Conformance Criteria - Trench subgrade to be inspected to assess if suitable for pipe laying or construction to proceed. Advise Engineer if unsuitable
040755ef-c1a0-5c4a-a018-520ed2ae7428 | note | Standard / Specification - Aurecon Civil Spec Section 17.13.9
31180b77-512b-51cb-b23d-5f2c07b62905 | note | Verifying Document - QA Checksheet
973ed82b-de82-5f5a-954f-2255a59abbd6 | note | Frequency - Prior to pipe laying
552ba684-0153-5b26-a150-96e9121023c2 | note | Verification Activity: Activity - I
a5e69fa0-b3a2-577b-a9aa-bd02a31b1c94 | note | Verification Activity: By - SE
b014b3a8-e695-4f36-90b8-a1a4ee48c3d0 | checkpoint | 5.02.01 - Line and Level
1dc26ab6-a3fd-5455-8d0a-2e116f3feb33 | note | Acceptance / Conformance Criteria - Pipes laid to line +/‐25mm, grade and invert level shown on drawings. Lateral tolerance +/‐25mm from centreline between manholes or change in grade.
bab9ffc4-45ce-53ac-9d04-4cf32bb9532f | note | ○ Engineer notified prior to pipe laying.
3ea82a8d-8547-5028-b673-da7ff2fa58fd | note | ○ No pipe laying shall be carried out without Engineer being notified 24 hours prior
26db5922-2ff0-518b-83a4-ac59cb83f6c8 | note | Standard / Specification - Aurecon Civil Spec Section 17.13.16
42c6fb70-72aa-5cff-8a2f-3377e7ef102a | note | Verifying Document - QA Checksheet
cf15610b-6709-56bd-8349-680cd7f3e761 | note | Frequency - Before Backfill
c2065efc-7a74-5eb8-928d-f9a1bf197541 | note | Verification Activity: Activity - HP
cd506cb8-369d-538d-a2cc-c27971e5e235 | note | Verification Activity: By - DES
d55230cb-87fc-47e6-a50d-3a73a887e4df | signoff | AUTHORITY HOLDPOINT
5e31d25d-ad2b-4c81-a38d-b41c1f84f1a8 | checkpoint | 5.02.02 - Cleanliness
0af505bb-9062-5fcf-821c-26439672b306 | note | Acceptance / Conformance Criteria - Internal pipe walls shall be kept clean and free of all dirt, rubbish and water. Spigots, sockets, rubber rings, etc. shall be thoroughly cleaned before jointing.
78d5aea9-466e-5f0d-a183-2076429b8ac6 | note | ○ Pipe condition inspected prior to laying and line checked prior to backfilling
8cda70bb-97fc-54db-8fc5-858a07049eac | note | Standard / Specification - Aurecon Civil Spec Section 17.13.16
d0e5cbca-1d5f-5644-a551-010c0a583b7b | note | Verifying Document - QA Checksheet
3f6c573c-8dcc-58ee-861a-884d28cea776 | note | Frequency - Before Backfill
47625cff-e74d-5e8f-a2c1-5a53769a4b4c | note | Verification Activity: Activity - I
02e1e9a2-a583-5c28-b078-8ff18d52c72f | note | Verification Activity: By - SE
046e59e8-5098-48d7-9b9f-f2b2e560e0de | checkpoint | 5.02.03 - Bedding and Haunching
0e03011d-35c8-55b1-a15b-e5013c4064f5 | note | Acceptance / Conformance Criteria - AP<12 granular bedding material.
6618dfb2-3482-5ed7-8258-cedfd360ea1d | note | ○ Any sand used must be clean and well‐graded
7e475510-b6e6-57a2-8ca4-ceb444d44b49 | note | ○ Bedding and Haunching ‐ Clegg Hammer test minimum CIV of 12.
9d5c5a5a-b214-5b1c-8300-643623b45267 | note | ○ Results to be attached to checklist with photos.
5a6ce6de-cbee-5660-82b7-99dfc8a78011 | note | Standard / Specification - Aurecon Civil Spec 17.13.15
376eb8ad-6cac-55f1-b695-99daab7e05c0 | note | Verifying Document - QA Checksheet
81db3dc3-e702-50f6-b52e-90ae10f9e12b | note | Frequency - Every 10m
108ad5b7-4411-5c64-9af4-4f6c3a252c0c | note | Verification Activity: Activity - I
7b6b7c6a-d6cd-5b12-ab9d-683a8a86316e | note | Verification Activity: By - SE
59cfeed2-39e8-417d-9875-047bf9ef91be | checkpoint | 5.02.04 - Backfill Placement
31cff7bd-ce3c-5d2a-98f7-300be39ccfa3 | note | Acceptance / Conformance Criteria - Subbase quality AP65 granular backfill material to be used. Backfill and compact in 200mm layers.
859bb964-f286-5354-8b79-953ac6b7b317 | note | ○ Clegg Hammer test minimum CIV of 25.
bf6beecb-8536-5fc1-9593-ca8b2a7cf2c8 | note | ○ Results and photos to be attached to checklist with photos.
f82a8456-66a6-5a5c-b098-f0414837cf81 | note | Standard / Specification - Aurecon Civil Spec 17.13.15
a87877e6-3a4f-58e5-8ca5-579b593d536d | note | Verifying Document - QA Checksheet
9f6d7840-3e3c-5c3e-b04e-3e7b7697a536 | note | Frequency - Every 10m, in 1m lifts
c7fa6895-b54e-5487-b72d-73aa626da828 | note | Verification Activity: Activity - I
313ab56a-1c6b-5fee-aa8e-7f13da98b7d6 | note | Verification Activity: By - SE
556adb63-ec3d-44e1-a072-47b950b882e5 | checkpoint | 5.03.01 - Alignment
2a5507d3-41b5-51b8-815c-939aa47e5f26 | note | Acceptance / Conformance Criteria - Structures shall be positioned within 50mm horizontally of the location specified. All structures shall be watertight.
49ac3cb9-39f3-5e13-935c-97f134f6cf65 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
2fe2fa2e-8943-5a1e-8d39-51e02b34df88 | note | Verifying Document - Survey
d7353356-07b5-54ce-8b57-50bfe29a6e1b | note | Frequency - Each Manhole / Sump
74294371-5786-5745-9d73-973c301e8a47 | note | Verification Activity: Activity - C
e9d2e9ca-bdd0-5e6a-b104-7de62da52ae6 | note | Verification Activity: By - SV
eac41a61-564e-40df-a0ea-ef7181a260b8 | checkpoint | 5.03.03 - Drainage Structure Bedding
4b498e0e-de7a-54d8-8d7f-a76b8497ee04 | note | Acceptance / Conformance Criteria - Unless specified otherwise, all catchpits, manholes and other stormwater structures shall be founded on a minimum 150 mm bedding.
4db72a30-e2e5-57b7-b66c-76776888b6b8 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
ac1a6220-36a3-522e-84d4-94618443f944 | note | Verifying Document - Site Records
9033a582-6abe-5407-b070-f17ffb48a613 | note | Frequency - Each Structure
23d9e508-9f50-53d3-b76e-81a7c148f583 | note | Verification Activity: Activity - R
4934ccd7-bd99-5921-8a57-22c572bdf8ad | note | Verification Activity: By - SE
03b960bc-b12f-4950-b50e-d4db8496a770 | checkpoint | 5.03.04 - Structure Backfill Testing
0b165c62-5756-5fdd-adf3-2e8134ae5072 | note | Acceptance / Conformance Criteria - Subbase quality AP65 granular backfill material to be used. Backfill and compact in 200mm layers.
7eb5fa30-0f81-59d1-917b-ed5246af465b | note | ○ Clegg Hammer test minimum CIV of 25.
1a7d9ceb-aa73-5e38-8f37-7494e8003176 | note | ○ Results and photos to be attached to checklist with photos.
a962c154-f6d6-534b-9b7d-c8ea96fb372a | note | Standard / Specification - Aurecon Civil Spec 17.13.18
ffdde332-faf8-5fa5-955f-2be833774552 | note | Verifying Document - QA Checksheet
1b7f3a69-5b6a-52d6-9718-06a9783e4e45 | note | Frequency - One test every two layers per manhole
79a72f65-0b70-5915-871c-3777d3742d5c | note | Verification Activity: Activity - I
66926283-1cc5-5eaa-be19-58d5c86805b8 | note | Verification Activity: By - PE
2c9922e0-de78-4e14-8353-3209a20a8525 | checkpoint | 5.03.05 - Pipe Penetrations
83b73fc2-341d-58cf-b1ee-bcfa8ce2f6bf | note | Acceptance / Conformance Criteria - Pipe penetrations shall be formed by drilling holes around the line of cut before knocking the section out.
2beea6a6-ff8f-5576-8b40-234266f13fb3 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
ecae186e-1d05-50b8-955b-3594be52ac23 | note | Verifying Document - Photo
53200386-00de-5655-8178-677dd359fcd2 | note | Frequency - Each Structure
41efd525-3470-5d13-8f14-e3576d1e8f45 | note | Verification Activity: Activity - I
29bbe744-ff00-5809-8d73-b167c394b396 | note | Verification Activity: By - SE
0eddba25-2fe6-41d3-be93-96000b567d92 | checkpoint | 5.03.06 - Benching
eaf9f5d3-a6c5-5d92-8855-f67ecb80ff03 | note | Acceptance / Conformance Criteria - The concrete shall be rendered to a smooth finish and shall slope towards the channel. Particular care shall be taken to create smooth transitions at bends and junctions. Benching is to be in accordance with the drawings.
7f3b5d67-b357-52c5-8753-8da01e36fafd | note | Standard / Specification - Aurecon Civil Spec 17.13.18
2adc6455-2808-541b-b0d1-b986691e25dc | note | Verifying Document - Photo
b2ac9386-30e7-5dd4-a84d-cc6ae1997cec | note | Frequency - Each Structure
95477da3-238e-51aa-add5-33e48d8c1ae9 | note | Verification Activity: Activity - I
38b41d58-202b-5267-8310-293674658199 | note | Verification Activity: By - SE
5aede6b2-5baf-4f6b-b59d-3aeb04c8aa63 | checkpoint | 5.03.07 - Corbels
1b629889-2871-5781-9f4d-dddbcbaba577 | note | Acceptance / Conformance Criteria - Pipes shall be haunched and surrounded with concrete to a minimum distance of 200mm from the outside of the manhole in accordance with the drawings.
859eb528-5317-5bdd-aab8-70e7d22ccc74 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
e23c89f6-06b4-5a66-8467-7639c84b79d8 | note | Verifying Document - Photo
d8a7d9df-3370-516b-9aa8-d3162a6b57bb | note | Frequency - Each Pipe Entry
69b1725a-de06-5132-9d7e-aae25ff4b67f | note | Verification Activity: Activity - I
33423871-d2c8-5027-b60a-52d3a1813216 | note | Verification Activity: By - SE
37427201-020e-4f11-a046-9227ab94f4f1 | checkpoint | 5.03.08 - Pipe ends
311454d8-7750-5305-bfa0-62161cf191b0 | note | Acceptance / Conformance Criteria - Pipe ends shall finish approximately 50mm beyond the inside wall and be plastered with cement mortar or encased in benching concrete in accordance with the drawings.
29347e21-4363-5305-ba64-93dc74f0fc52 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
3ab18a1e-6d14-5f42-a592-00c340041c51 | note | Verifying Document - Photo
20660926-01af-5155-a4a1-d5b33f753b57 | note | Frequency - Each Pipe Entry
00572355-483f-5c33-8ca3-27da9b3d4a98 | note | Verification Activity: Activity - I
1aa6d669-cf88-55fd-8da4-15ecba24dfcb | note | Verification Activity: By - SE
2666c36a-10f2-464a-9c34-135ae2cbdccd | checkpoint | 5.04.03 - CCTV Inspection
1b3fecfc-5de0-529b-b0d9-75eb6eef726d | note | Acceptance / Conformance Criteria - Lines fully flushed immediately prior to CCTV inspection.
8a253ffa-1890-5286-88d5-6988f6dae2b7 | note | ○ Inspect pipelines for correct line and grade between manholes. Pipes to be checked for visible infiltration and debris. CCTV submitted and reviewed by Engineer.
90689c79-3a91-5e81-9584-d79d797e00fd | note | Standard / Specification - Aurecon Civil Spec Section 17.12.23 NZS 2566.2; Section 6.3.4.1 & 6.3.4.2
2daa0de8-d726-5248-aba6-9bc43aecc181 | note | Verifying Document - CCTV Logsheet and Video
5f6d054c-e05a-5c0c-84f3-08441032f183 | note | Frequency - Each Pipeline
dbf10a59-2fc2-57b2-9172-c5ce43d61a3d | note | Verification Activity: Activity - HP
412477e5-c12d-57b9-b106-5e308f36fd52 | note | Verification Activity: By - ENG
e04848e4-2203-40f3-a22c-67c350706bb7 | signoff | AUTHORITY HOLDPOINT
2810c580-f74e-4b0c-85ce-c90fbd2f4943 | checkpoint | 5.04.04 - Manhole Testing
8ecf99e3-5f32-5fec-aa61-267e0b0bcaf1 | note | Acceptance / Conformance Criteria - Manholes and pipelines shall be checked for infiltration. Visible leakage in manholes and pipelines shall be rectified prior to acceptance.
02cc5bb6-a588-54bf-a86a-e710a85b8c0f | note | ○ Stormwater Manholes shall be free of visible faults or permeable zones and jointing or penetration repairs shall be to best trade standards
39b73db0-83a0-5c5b-988a-37efa896a833 | note | Standard / Specification - Aurecon Civil Spec Section 17.12.22 NZS 2566.2; Section 6.3.4.1 & 6.3.4.2
2b418a15-749f-59de-9ef5-d102ecb8af8e | note | Verifying Document - Test Report
9ad4f95d-15c0-5e6d-8f08-8f30d38e3576 | note | Frequency - Each Pipeline
affac232-4189-51dd-aa94-d531cef68068 | note | Verification Activity: Activity - HP
c52cc343-043f-5fb5-939a-8f2d5baf385c | note | Verification Activity: By - ENG
6786d93f-3dd0-4a03-853e-ab7f662202fb | signoff | AUTHORITY HOLDPOINT
6eff4f33-dac8-46f2-a493-858539323533 | section | SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
dc05f96a-a9fe-4d5d-82dd-a10d3cdd1d5e | checkpoint | 6.01.01 - Construction Record Compilation
05fbf73c-b0c6-56dd-80b6-5af9fd47d612 | note | Acceptance / Conformance Criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
19053b39-aed1-5dac-aff5-6291198d3e79 | note | Standard / Specification - Downer
da20a950-2ef9-5833-8b40-b8a1794cbe3e | note | Verifying Document - Records
b52aceb2-c1bb-59fa-b386-46d3beda53c4 | note | Frequency - Post construction
ef181242-248a-5bcf-ba38-f1b93c6b1026 | note | Verification Activity: Activity - H
1fc31b8b-de60-56c5-a91b-27c074c62c12 | note | Verification Activity: By - SE
2a0db845-2476-4923-a971-74ef5157458b | checkpoint | 6.01.02 - Survey Records
da632324-26f1-582a-8fa3-fa3c6969a5a0 | note | Acceptance / Conformance Criteria - Ensure all items have been surveyed and records are assembled for asbuilting
98c2e71c-7c50-594e-aa1c-ff53238a0954 | note | Standard / Specification - Downer
598a8fd3-ffb2-55b6-b661-8f347a1ef381 | note | Verifying Document - Records
f27f5dbe-c222-55cc-8ee6-1a1a8ccca456 | note | Frequency - Post construction
5cbc269f-c871-5c8d-9585-13da86cbdfc3 | note | Verification Activity: Activity - H
5fd576f4-8fa0-5d10-b66a-2176e126a5dc | note | Verification Activity: By - SV
7c69b0d0-63c3-4a9a-aa46-c306afd7ce16 | checkpoint | 6.01.03 - Redline Drawings
c8c39aed-40ea-5a9b-8ba4-634a45caf263 | note | Acceptance / Conformance Criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen.
a0f9ef5b-e757-5ec2-ad2e-41496c8a59da | note | Standard / Specification - Downer
d78c191f-c650-541d-8a9c-537abc151cf4 | note | Verifying Document - Redlines
ecf17b12-8c1c-52a3-93fe-311df23fa837 | note | Frequency - Post construction
6a2301fa-118d-5b70-b9eb-b2e594de4d33 | note | Verification Activity: Activity - H
68d587cc-b4d6-5a4b-a78e-6a48f93b8c2f | note | Verification Activity: By - PE
bce5c348-70ed-4be4-9eb8-50372ce6715f | checkpoint | 6.01.04 - Defect, Snag and Punch List
664c81e5-ec5c-5003-9536-cd943d060457 | note | Acceptance / Conformance Criteria - Update the project Defect, Snag and Punch List Register
2c9185e0-efa9-5b1c-a558-e32bf0bf5f85 | note | Standard / Specification - Downer
d5793ac7-8cd3-530d-be9a-13f47f79a130 | note | Verifying Document - Register
8fe34fcd-9c07-5651-b70d-7ec7a6e35d33 | note | Frequency - Post construction
134e9368-dd0b-5bc8-a979-a689163e74fd | note | Verification Activity: Activity - H
a379b82b-f9e6-546f-ae9a-fa068099c087 | note | Verification Activity: By - PE
e0c9ad2c-563c-4fcd-9f11-56dd4beb120b | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
81f68add-28e6-5766-af8a-b9819b4d2e21 | textbox | Contractor's Rep Name:
52632d9b-b8aa-5ffc-bbbb-a1607a4410f8 | textbox | Engineer's Rep. Name:
75e31f39-a8ca-5036-af21-16cb1957581e | date | Date:
4937d918-0619-4a9a-8c03-4787e180e651 | signoff | Add Signature
b309012d-e62a-4976-a475-bf13ec43969a | checklist | DN1211-002 ITP Utility Duct and Pit installation Rev 01 | itp | DN1211-002 ITP Utility Duct and Pit installation Rev 01
eb37bf05-fcde-479c-a454-9539c332b951 | section | SECTION 3 - PRE CONSTRUCTION (P&G/ESTABLISHMENT)
f07c7d89-4930-418a-8064-619e3fd10c47 | checkpoint | 3.1 - Pre- construction
2590dac8-c6b0-5b85-9c56-9a31f8f49838 | note | Acceptance/Conformance criteria - Site Clearance and service location completed. Before U Dig, GPR service locate and pilot holing as required. Protect existing services and liaise with utility providers as necessary
b5856f12-bd4d-515c-86c8-3366462286b3 | note | Standard/Specification - Aurecon Civil Spec 19.5
7bc2f8f4-61c2-525a-888a-3a8903944a5b | note | Verifying Document - Service Locate or Asbuilts
3bb341d7-7336-5945-a6e5-969a713a9ec6 | note | Frequency - Prior excavation
35acb7fb-6e38-5852-8f7c-424e6eeac7e6 | note | Verification Activity: Activity - H
e9d8d56a-5735-5e85-8e19-97faa9585e3b | note | Verification Activity: By - SE
a6ff28d9-94bd-4840-877a-3fce79c9ae7f | signoff | AUTHORITY HOLDPOINT
9269f14c-8067-4c2f-ba23-007657cac845 | checkpoint | 3.2 - Existing Services
edc4f73a-2a00-53c2-97f6-4ab2648f8a28 | note | Acceptance/Conformance criteria - Protection, relocation,and preservation of existing services as per Specification
cbb62cab-0cb9-57a5-8e5c-2dbae6021f98 | note | Standard/Specification - Aurecon Civil Spec Section 19.9 & 19.10
86b4c5fc-dfef-56b7-a36c-a774e94b1c8a | note | Verifying Document - Service Locate or Asbuilts
2bc75a12-b600-522d-81f7-1901c123d2d0 | note | Frequency - As required
36a03a74-c0ea-517b-8736-b3a38e13807c | note | Verification Activity: Activity - H
6c00a5df-7901-5138-b246-b1d8181810d0 | note | Verification Activity: By - PE
3f17fd37-55ff-4570-b2c7-8126b9c24c36 | signoff | AUTHORITY HOLDPOINT
a2127abf-46a0-4b43-a498-0fe57d6e0559 | section | SECTION 4 - MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
3512c76a-3459-4965-863e-6fdf3deeb600 | checkpoint | 4.1 - Service ducts
2c91b6e3-83a1-5419-8638-75c33eb85da7 | note | Acceptance/Conformance criteria - Supply ducts as per drawings; grey for general use, heavy duty for electrical or as specified by utilities providers. Duct cover; min 900mm in roadway, 600mm in main footpath, 500mm in footpath ends Provide 75mm concrete slab protection in areas with greater than 375mm cover Provide 50mm concrete encasement in areas with less than 375mm cover
8eeb9b8a-56a4-5d1e-bc41-a4babc728234 | note | Standard/Specification - Aurecon Civil Spec Section 19.10.1,19.10.2
6b060009-75b8-5bd5-8368-3eb7f9216a4f | note | Verifying Document - Approved MAR/Delivery dockets or photos
acedb981-9654-514c-9b4a-278497c1d8ca | note | Frequency - Once prior
267ccce2-a739-5952-877f-0dc2731abd10 | note | Verification Activity: Activity - H
59a06eb3-f41a-5dd7-8f0a-575aa41d1f1a | note | Verification Activity: By - DES
83a9ec44-871b-49dd-998c-48370e07b977 | signoff | AUTHORITY HOLDPOINT
f18bc4d8-8021-49da-b5cb-98d02b03d034 | section | SECTION 5 - CONSTRUCTION ACTIVITY
a75aabde-22fb-4231-ab59-45174ed9f836 | checkpoint | 5.1 - Excavation
9107cbbb-9f9c-5cad-a92e-487270ddd4f4 | note | Acceptance/Conformance criteria - Set- out position completed RL marked. Excavated trench to be free of debris and water. Bedding material placed as per design - 100 mm thick GAP 7. Ducts checked prior to installation of any defects.
39b88ce7-9846-5074-8ecf-738a2448d71e | note | Standard/Specification - Aurecon Civil Spec Section 19.11.2
c1e2c76b-7f37-5934-ba9e-d95ae0949dc7 | note | Verifying Document - QA Checksheet
2d18907c-79c3-5c28-a2eb-f22db454c14c | note | Frequency - In Process Check
ff67200b-5ae6-5941-a2dc-942affaf745b | note | Verification Activity: Activity - V
f93c2eb3-da81-5937-a487-adea66d63245 | note | Verification Activity: By - SV
bf94bf9f-a0d1-4fc0-b963-0afb6c2b399a | signoff | AUTHORITY HOLDPOINT
215ed220-1280-4c82-baed-27acb663ed22 | checkpoint | 5.2 - Bedding Layer
746aa30b-2b4f-53da-868f-3b7cd92501e8 | note | Acceptance/Conformance criteria - Surround all ducts with 50mm bedding material, well compacted. Minimum 25mm bedding between ducts all sides Material Certificate submitted to Service Provider/ Engineer ‐ GAP 7 material is to be used unless stated otherwise in drawings. NUO to be notified for review if required.
43f51c2f-29cc-5394-8999-2da89ccf95a0 | note | Standard/Specification - Aurecon Civil Spec Section 19.11.16
a563f490-e7c3-5aa9-be56-de436d10d24e | note | Verifying Document - QA Checksheet
9cc39c9b-1381-5ab8-abe7-20ea28435af4 | note | Frequency - In Process Check
04447890-420c-5f21-893f-3549f05debfb | note | Verification Activity: Activity - H
6ada5190-01dd-56d8-a57c-b2150883c4e6 | note | Verification Activity: By - SE
526662c4-953b-479c-825a-9fbb85668065 | signoff | AUTHORITY HOLDPOINT
e487f170-e34c-4298-ae90-a72ecdbcabdf | checkpoint | 5.3 - Backfill
8a1e9754-24c4-574a-8e15-0d5c61e2ea91 | note | Acceptance/Conformance criteria - Backfill and compact in 200mm layers, NDM for 95% MDD or Clegg test for CIV ≥25 Material Certificate submitted to Service Provider/ Engineer ‐ Backfill above the bedding with GAP65 or AP40
5e8c67d7-c768-5be8-b75e-f1655c445088 | note | Standard/Specification - Aurecon Civil Spec Section 19.11.17
b35043d2-d1aa-5888-872b-9fc22196df1b | note | Verifying Document - Test report
a5bce3d5-3389-5a6d-97e8-dc950650e5ca | note | Frequency - Every 50m
e98dfc61-a5fd-5ac9-8bf6-91e17e184983 | note | Verification Activity: Activity - H
1ef95600-af84-5c0b-a53a-76f766f14062 | note | Verification Activity: By - PE
a1162077-eeb2-4bea-96c8-76e9d6b340f8 | signoff | AUTHORITY HOLDPOINT
b8ebe52d-de2c-43aa-8b18-f8dbe09fa3c7 | checkpoint | 5.4 - Testing & Commissioning
9c407b51-d045-5315-87da-0ecfd540f0e6 | note | Acceptance/Conformance criteria - Draw lines for future placement of cables installed with polypropylene rope Test ducts by passing mandrel through line without effort: 65mm ID duct: 52mm diameter, 100mm length mandrel 50mm ID duct: 40mm diameter, 80mm length Supply as‐built information to the requirements set out in the Project Specification.
fc00e56e-84c1-59cb-b615-4c36b7dfba7b | note | Standard/Specification - Aurecon Civil Spec Section 19.12
102814d5-c18b-5a6c-8bd0-07ba9c4bdb00 | note | Verifying Document - QA Checksheet
79a792a2-0884-5d39-b941-4af3e378d13f | note | Frequency - Upon Completion
19864fc0-0524-561c-b8f7-43105c8a495e | note | Verification Activity: Activity - H
ca0e3e43-ea89-54e7-9262-db6c911f5948 | note | Verification Activity: By - PE
dd62b81e-ea15-44a6-a386-72c5897ed496 | signoff | AUTHORITY HOLDPOINT
96b07720-735c-455b-911e-a384cded0e42 | checkpoint | 5.5 - Service Covers and Benchmarks
3ecbf58a-fe9c-5217-a997-047cc3349e73 | note | Acceptance/Conformance criteria - Service access cover orientation shall be perpendicular and parallel to the pavement coursing and to road kerbs for covers in insitu concrete paved areas as shown on the landscape drawings. Contact the civil engineer and landscape architect to agree locations prior to finalising cover positions.
f56435bc-90a6-55a2-8636-29da91c0ece3 | note | Standard/Specification - 19.11.10
0c3a0d78-15d5-5fb7-a419-c92d1c2798c2 | note | Verifying Document - QA Checksheet
ec01d163-27ea-505a-8464-034ab43ed3d9 | note | Frequency - As Required
b93098e2-d3dc-531a-9795-8853b6f15276 | note | Verification Activity: Activity - H
1c52cc3a-b86a-58c1-9074-232c45bf6eac | note | Verification Activity: By - SE
e39e29ca-d94f-459b-8454-f2f85bd6213f | signoff | AUTHORITY HOLDPOINT
717d7a6e-05b8-45db-b40b-80767d27eedd | section | SECTION 6 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
9c9a206c-6add-475a-88ae-27f763da9b98 | checkpoint | 6.1 - Construction Record Compilation
19e198cf-2e5c-5f4f-8e21-afb409ae9a43 | note | Acceptance/Conformance criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
e65fcb41-fecb-59b5-bb24-2455201fb53c | note | Standard/Specification - Downer
7efceeeb-e4df-53c3-8b56-bdd96417d03f | note | Verifying Document - Records
4793bbf9-db10-5924-99ce-fe256dafcd77 | note | Frequency - Post construction
1fe0df99-7ed8-5468-8863-6ae30c4139d4 | note | Verification Activity: Activity - H
cc70e5d4-cb3b-5d16-b641-d41f2d63e0f5 | note | Verification Activity: By - ENG
1a24f0e3-1722-43ce-ae65-590f06f4b2f8 | signoff | AUTHORITY HOLDPOINT
ac244f8a-2026-43f1-ad5c-48ea32f1d0de | checkpoint | 6.2 - Survey Record
d3dc67bf-b879-5fae-a8d2-906df4a658a1 | note | Acceptance/Conformance criteria - Installation of works under contract completed compliant in accordance with all relevant regulations, COP and standards
3416c22b-eec0-5f21-89be-941ee753cf6a | note | Standard/Specification - Design Specification / Downer
9c6733bd-562e-5537-841f-ea3cc8577ec3 | note | Verifying Document - QA Checksheet Redlines
afd06a73-8609-5707-b6d0-f1bc3368e708 | note | Frequency - Post Construction
a9e8cb3f-0a3b-514f-8d54-38e8ed108ba2 | note | Verification Activity: Activity - H
dfd59477-1fd4-5c76-a803-073a6fb009cb | note | Verification Activity: By - ENG
088c15d7-da34-4d75-9363-f8b30300ccdc | signoff | AUTHORITY HOLDPOINT
9d5b07a8-0784-40cb-9352-32ee9eb4a2bb | checkpoint | 6.3 - Redline Drawings
69999292-4ebe-5e3d-847c-d0a7be67f73f | note | Acceptance/Conformance criteria - Ensure all items have been installed create a Redline Drawings for Asbuilt creation noting all changes with RFI numbers and departures in red pen
7a1ed21d-0d77-5713-9fa1-8c8ceff91700 | note | Standard/Specification - Downer
bf339961-4b0b-57ac-8139-5041b33656cc | note | Verifying Document - Redlines
65963a04-4dd7-5075-a2f0-8e8915e7ed4b | note | Frequency - Post Construction
e0c8edaf-dea6-56d1-8261-f0a21b984742 | note | Verification Activity: Activity - H
0a2e7f0f-6a32-5177-a05a-75a8df861e41 | note | Verification Activity: By - ENG
8ab762d7-cbf5-47ca-b725-c31af6ac1c9f | signoff | AUTHORITY HOLDPOINT
7875f554-b8d7-42bf-bea9-b555e2df123c | checkpoint | 6.4 - Defect, Snag and Punch List
db86d1e3-492c-5769-98e2-4ec62e205f98 | note | Acceptance/Conformance criteria - Update the project defects, snag and punch list register
eddd7c84-c1a5-5cc9-8e69-e9f3b0362997 | note | Standard/Specification - Downer
acad2b6b-e761-5f8f-9669-7fcb517bd475 | note | Verifying Document - Redlines
c6bf8eb9-bb48-537e-bf78-6a68420e59fe | note | Frequency - Post Construction
cb4360b8-1086-5f7e-aa77-ce00f6d5805e | note | Verification Activity: Activity - H
aff1ef69-7ebe-59de-8b87-bc339ca969d7 | note | Verification Activity: By - ENG
17546a9e-1204-4bb1-90e2-84bd07051f34 | signoff | AUTHORITY HOLDPOINT
97413000-021e-477a-9924-788a0906d843 | section | SECTION 7 - SIGN OFF
e4337606-a5fd-4264-928b-e7d13d730032 | checkpoint | SIGN OFF
16b93af2-cdfa-55ce-b788-7afcb2baa260 | button | Customer Release Granted: | Yes, No
57fbe50f-65c0-5efe-9912-570aea0224b9 | textbox | Acceptance/Conformance criteria - Certificate Number:
c314a229-23d7-4fdf-bd54-b3d1ba228bb2 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
8687e237-ff81-5716-85c7-0dfd9cb212a6 | textbox | Contractor's Rep Name:
783f0fa4-f9f9-5090-91ee-4a3c568b2ca9 | textbox | Engineer's Rep. Name:
4f54f042-2e4d-50e3-a688-19c6cc6c9452 | date | Date:
c6f0e5e7-3beb-4d04-974c-90bd7f763e51 | signoff | Add Signature
df5c59b1-6213-4cb0-b11b-e5ee56e8dca3 | checklist | DN1211-003 ITP Earthworks (Excavation, Subgrade, Sub-Base) Rev2 | itp | DN1211-003 ITP Earthworks (Excavation, Subgrade, Sub-Base) Rev2
ace71d99-7590-4b60-84ca-8562cc459726 | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
8e6ce5d8-fc80-4d85-bd14-f42a914fb65a | checkpoint | 3.1 - Pre- construction
ff4041d3-eefc-50a8-bbd5-5bb9cda1560c | note | Acceptance/Conformance criteria - Site Clearance and service location completed. Before U Dig, GPR service locate and pilot holing as required. Protect existing services and liaise with utility providers as necessary
a473c20d-01cd-5b95-9819-7bff37be6bd5 | note | Standard/Specification - Aurecon Civil Spec 19.5
14298c7e-070e-5276-a77c-3fe505ae084d | note | Verifying Document - Service Locate or Asbuilts / Sample Dig permit
3ca754fd-44bf-5a98-a8fa-c9dfb2d53119 | note | Frequency - Prior excavation
c54ec032-8640-5dee-95d1-20b581ce443e | note | Verification Activity: Activity - H
e92e1b37-392b-52eb-bb28-05ac30f5fc98 | note | Verification Activity: By - SE
0b548170-090d-5213-b11a-51155b891cd2 | note | Downer Signature - H
bcd75f4d-0789-50dd-af6e-8b7c07c2d54b | note | Engineer Rep Signature - I
f61e956a-aecf-484b-a649-02ed87447703 | signoff | AUTHORITY HOLDPOINT
9fe84e94-f4fb-456f-981b-7fdc4b7dc038 | section | SECTION 4 - MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
3bbab417-d3e9-4e47-ad77-5723f15ae196 | checkpoint | 4.1 - Aggregate MAR
fb236df5-dd6b-5477-9b65-6278738381be | note | Acceptance/Conformance criteria - Sub-Base to be ATAP40 and comply with TNZ M/4 specification for aggregate properties - At least seven working days prior to delivery of Sub-Base course the contractor shall deliver to the engineer the results of production property tests carried out by an IANZ accredited lab in accordance with the relevant NZ standards
893555e1-10ef-5261-af5c-a25d147fcaef | note | Standard/Specification - Aurecon Spec 7.5.1
571005ec-00fd-5e68-b4f0-c5e1a0dad899 | note | Verifying Document - Approved MAR / IANZ test report
eae2e3e3-565b-538a-9f70-15e8092685de | note | Frequency - Once prior Sampling rate as per civil 6.5.1
5ddf5cab-cf1c-5a0a-a47c-f84146824b19 | note | Verification Activity: Activity - H
976ccc07-16ab-548d-9859-7cfa97863a17 | note | Verification Activity: By - DES
285b46d4-dddd-5aee-9241-1b80949827bc | note | Downer Signature - H
379a4e40-f982-501c-9163-b59c8b21f2f6 | note | Engineer Rep Signature - R
d193c427-efca-572f-90fd-501055f74ea4 | note | MSQA - I
31ffd868-f6bb-41e1-8fac-fc126e036f00 | signoff | AUTHORITY HOLDPOINT
cab42782-a0da-4a33-ba7b-d0323d6823f4 | section | SECTION 5 - CONSTRUCTION ACTIVITY
12f38ade-7d6f-41d5-b4d5-bcfb053b85d1 | checkpoint | 5.1 - Excavation
b894e34d-03b1-5791-95f1-761ebdada396 | note | Acceptance/Conformance criteria - Set- out position completed RL marked. For excavation level
d017c624-d5dc-5e6b-9213-40e2e1366a16 | note | Standard/Specification - Aurecon Civil Spec Section 19.11.2
d00f4e8f-9b97-5f99-a969-4017be3e26d5 | note | Verifying Document - ITP sign off
a60ce95e-7604-518a-b9f3-d9910b860c2a | note | Frequency - In Process Check
e7e73d05-006c-5f6a-a19f-4073cda23581 | note | Verification Activity: Activity - V
45aa8f54-916b-5ea9-8c40-9426b45700bc | note | Verification Activity: By - SV
99b6a560-a379-59e4-a1ce-bb3cf145839f | note | Downer Signature - V
d935b566-d07f-5c27-828b-eb253358953d | note | Engineer Rep Signature - I
30b82867-c9c1-42ea-8ebb-cdcd19072387 | section | Site Clearance
094ec8f5-ac29-4080-b31c-833d84019202 | checkpoint | 5.2 - Site Clearance (Cut to Subgrade)
c30d62a1-3574-5c8f-a38f-96ba896fa722 | note | Acceptance/Conformance criteria - Area of work Cleared in accordance with Resource consent andlocal authority requirements. Discovery of unsuitable materials to be advised to the engineer and disposed of or repalced as directed.
62538f25-ef86-5f73-b615-ebf3098a7364 | note | Standard/Specification - Aurecon Civil Spec; Section 3.3 and 3.6
ae9adcce-a36d-581a-848e-8bbf4931acf4 | note | Verifying Document - ITP Sign off
853a8297-65af-5108-8d7a-4bf6ea45c5bd | note | Frequency - In Process Check
e077800c-6d6f-53d9-8531-f6140ff31b7e | note | Verification Activity: Activity - W
91f370fb-3b69-5d09-815e-5d632a9ca0b0 | note | Verification Activity: By - SE
eaf6f3a4-987f-573f-a9a5-d02042d2ef72 | note | Downer Signature - V
0c6ab31b-7812-52de-a927-7754424e1216 | note | Engineer Rep Signature - I
cab926f5-221c-4acc-8ca9-853506a53dcf | checkpoint | 5.3 - Discovery of antiques and valuables (If applicable)
7db73c8e-4765-5aa2-ab87-e1d1d00da2fa | note | Acceptance/Conformance criteria - Arcaheology: Works to be completed as per CMP Archaeoligical discovey protocol, records in site diary and Aconex sent to the Engineer.
53f97b25-4928-55e3-bac8-d65f24d43790 | note | ○ Antiques: Owners must contact the Heritage New Zealand for authority to proceed.
9dc26e3d-260d-545a-a9d9-1feb4df44ecc | note | Standard/Specification - Aurecon Spec 3.10 and Heritage New Sealand
5302fe05-30bc-563a-bcce-2283cf55569b | note | Verifying Document - ITP Sign off
1fc8a831-8c52-599d-88e9-99e629ce8998 | note | Frequency - Upon Discovery (May not be Applicable)
fca5829a-c2c1-5652-963a-4b22a4ddce0d | note | Verification Activity: Activity - H
476efa48-b0ac-53e7-8697-e118cae2b8a4 | note | Verification Activity: By - PE
f3fa93f9-80fe-530a-94af-02ac7637684f | note | Downer Signature - H
a88503a7-da51-52c1-8308-d424a53c588d | note | Engineer Rep Signature - I (IF APPLICABLE ONLY)
ff82ae73-3a2a-4f9d-80ff-1b17063c7343 | signoff | AUTHORITY HOLDPOINT
a94b7c9f-d69e-4f87-a61e-b715b2673503 | section | Removal of Structures and Obstructions
bd80a347-8588-4ff5-b8ae-f39e0f551e97 | checkpoint | 5.4 - Discovery of Contaminated or Hazardous Material (May not be Applicable)
9b92b695-8425-56dd-9dd3-9a2b3adb9841 | note | Acceptance/Conformance criteria - Contaminated material or Waste exhibitning hazardous characteristics handled and removed asper work safe guidnlines and taken off site to be tested. Hazardous or contaiminted materials disposed at approved landfills only. Volume or any disposed hazardous or contaminated materials to be recorded.
88560b09-e5c7-5468-9844-942b86b48523 | note | Standard/Specification - Arecon Civil Spec 4.5.6 and management plan
f031d704-835c-53d5-8b04-c533b43bc93b | note | Verifying Document - Disposal dockets (If applicable) /Site Diary (If applicable)
fc26ebd6-7358-5356-8756-ddda31648990 | note | Frequency - Upon Discovery (May not be Applicable)
570647aa-7d05-557d-a4eb-c578ba0c583b | note | Verification Activity: Activity - H
aec8e483-3fd1-5658-9058-b7322ade5323 | note | Verification Activity: By - PE
c3d4f7bb-d5e9-5d7f-ae6f-4974f2b4fe1d | note | Downer Signature - H
6e2930d2-331c-5c2f-a406-eba8c0bc34fe | note | Engineer Rep Signature - H (IF APPLICABLE ONLY)
d0cde45f-d143-4dbc-a194-a4cf2b321493 | signoff | AUTHORITY HOLDPOINT
1df1efc4-d6ed-4a72-9c34-9ea1b8c8780a | checkpoint | 5.5 - Disposal of materials
124d76cb-654a-5850-a314-c7326114739f | note | Acceptance/Conformance criteria - Demolished Materials sorted as required and disposed of correctly. Materials or item salvaged for re-use as appropriate
11ef7a89-029e-561e-afc4-5f81cd7c1d34 | note | Standard/Specification - Aurecon Civil Spec 4.5.7
a8972989-14e6-570e-8516-c7ba8f31cdd0 | note | Verifying Document - Daily Diary (If applicable)
b8d5f968-9e53-500f-bc3d-567e0e5501a0 | note | Frequency - In Process Check
0d3ba357-c32f-51a6-837d-1f81b9215242 | note | Verification Activity: Activity - I
cc4eef03-4570-594b-ac4e-fcc273c3232f | note | Verification Activity: By - SE
2759368c-d3fd-578e-8cf4-0c59956242da | note | Downer Signature - I
fd4f12f9-df3b-44bb-8128-52d989d42d3c | checkpoint | 5.6 - Demolition and removal of obstructions
72a70df0-d7b7-5706-be30-8484485e08d0 | note | Acceptance/Conformance criteria - Submit works over approvlas for Relevant NUO's where utilities found. Confirm approval to remove structure or protection requirements as per Aurecon DRG's
ad7fc044-92f7-5d5c-a8dd-a8635b14b5ea | note | Standard/Specification - Aurecon Civil Spec 4.5.5
1999a1fa-713a-54d0-af48-2c61e6fee695 | note | Verifying Document - Email confirmation where applicable or works over permit algining with the consent
5271d8c6-f4ce-5108-9f18-89fe660eb6e9 | note | Frequency - Upon Discovery (May not be Applicable)
23c9e276-7ce3-5f1b-8b95-d141ac06afb9 | note | Verification Activity: Activity - H
e358d265-7e69-5b2e-97db-e32c35e3be0d | note | Verification Activity: By - PE
bcc1e6fd-6bb5-5c4b-b1fc-24d541659d67 | note | Downer Signature - H
69bb49fc-138a-501e-b026-26ca60951f73 | note | Engineer Rep Signature - I (IF APPLICABLE ONLY)
8f2075a6-93c3-4171-89a1-c6aaf3bbfc36 | signoff | AUTHORITY HOLDPOINT
86eaeac8-3b79-4114-8fa1-2ccc9991d5d2 | checkpoint | 5.7 - Tree Removal (If applicable)
9216cda7-9b51-548f-845b-c2d5f1c04034 | note | Acceptance/Conformance criteria - Refer to Tree Management Plan, Tree Management plan certification and relevant resource consents/approvals
1c6d8a21-5539-562e-8e23-3528e85f5ce1 | note | Standard/Specification - Resource Consent
c7eb60b0-6a95-5c2d-8152-ec67dcc2e994 | note | Verifying Document - Resource consent
8d22fc03-f820-59f1-bb5e-90d3f696b82a | note | Frequency - Each Tree (If applicable)
efce7e94-26e2-5a34-8649-60993d94b904 | note | Verification Activity: Activity - W
08d0871b-c315-55ff-9970-a8afd8f84f75 | note | Verification Activity: By - PE/DES/ENG
45b2561d-aa2f-5ae6-b942-efbf433bad6d | note | Downer Signature - W
216618cf-3201-5b4d-8fae-9cecc2f52537 | note | Engineer Rep Signature - I
0ab2e537-2e6c-580b-b04c-2fbdf89bf248 | note | MSQA - R
12611ff3-5c86-4d3b-9792-9c4d24936106 | checkpoint | 5.8 - Services/Sun Surface infrastrucure removal
eb1bf017-e62b-50a5-ab91-2701ed304e39 | note | Acceptance/Conformance criteria - Existing services and drainage structures to be located where possble or as agreed with the Engineer. Pilot hole, disconnect or isolate live services prior to demolitions as required. Services or pipes to be abandoned are to be completely removed or grout filled as per drawing or approval by assest owner if different.
8182fe47-8b96-5482-a2a4-39caf363f3ae | note | Standard/Specification - Aurecon Civil Spec 4.5.4 and 4.5.5
0958450c-8719-501e-ab65-a1a6a71b69ca | note | Verifying Document - Service As built
55131228-a7fc-51cd-ad51-2c901b147f7f | note | Frequency - As Encountered
88356190-9274-597e-bbed-c7f8a4ecafad | note | Verification Activity: Activity - H
d09e11a6-ab67-5913-af54-576ec9aafa31 | note | Verification Activity: By - PE/ENG
3f443a11-94bd-545a-ae4a-5b6ffd826ed7 | note | Downer Signature - H
a26dc229-d921-585d-a1fa-80588a09c1b6 | note | Engineer Rep Signature - R (IF APPLICABLE ONLY)
261e0b4a-7a96-4f9a-9ebd-6d949a69285e | signoff | AUTHORITY HOLDPOINT
d11f3b49-1062-4af8-87de-e1225d3623ee | section | Excavation
66a8b671-0afd-4fde-82a6-460171fbe408 | checkpoint | 5.9 - Subgrade Testing
6967eb8e-b19c-5a47-8b87-726c2f8c2120 | note | Acceptance/Conformance criteria - Contractor to Confirm subgrade strength and report to Engineer via Inspection. Clegg to be ≥ 10 value.
c123a86c-52ab-55dc-a216-9ff5ba76e506 | note | Standard/Specification - Aurecon Civil Spec 5.6.11
b73ba664-789b-5051-b7ad-45d79bcbd8b1 | note | Verifying Document - QA sheet
0cb73695-5357-5514-8deb-dd4ec0b3e911 | note | Frequency - Every 20m or as agreed by the Engineer
b5501518-f598-5787-9396-834367a05d87 | note | Verification Activity: Activity - H
49fe3fb1-4315-5ad3-ad8c-6bf9a802a849 | note | Verification Activity: By - SE
7a6bbf69-3722-543b-9c6a-cae672a27843 | note | Downer Signature - H
58d99fa0-7bf2-5f9c-824a-8777f76a3a7b | note | Engineer Rep Signature - R
3d12b03a-ef00-5af4-b4ae-cc7aa50d7b03 | note | MSQA - I
8d776011-757b-4c7d-ba22-76a7142683f3 | signoff | AUTHORITY HOLDPOINT
105a52fd-100d-4ac2-bf44-9f39f2e41bbc | checkpoint | 5.10 - Line and Level of subgrade
e916c287-c22f-5d1e-9d58-fe4e9c726d58 | note | Acceptance/Conformance criteria - Pavement Subgrade tolerance +/-10mm from design subgrade level (or as applicable with existing services). Excavation depth must be at least the design pavement depth for LMC locations. Subgrade shape as per survey set out. To be verified on site.
36bd24cf-d0e4-5cf7-8fa9-aa12cac87c91 | note | Standard/Specification - Aurecon Civil Spec 5.6.9
3224cd23-42b2-5c14-b651-61d9c865a532 | note | Verifying Document - As builts
e61235a8-c42a-5b20-a0b2-5686ea754d47 | note | Frequency - Each Subgrade section
ec3c57b4-acd6-58ec-8807-d1999f868b3d | note | Verification Activity: Activity - H
cfdeb5f7-ba5e-548b-9ef9-9f4c1f8d8350 | note | Verification Activity: By - PE
e752214e-25c9-50f7-b496-419c32901325 | note | Downer Signature - H
b948f073-ad29-5d4f-994d-d2dbd6c098ff | note | Engineer Rep Signature - R
cf246ba4-958d-5948-9c74-a4367d067a64 | note | MSQA - W
5dc78e02-6d86-4aba-ae0f-3e099cc405ba | signoff | AUTHORITY HOLDPOINT
50229bf5-9f05-4a92-933f-79f5b725dc00 | section | Sub-Base
67ea49e8-12b8-4a0b-b844-fe4bb1ad7514 | checkpoint | 5.11 - Sub-Base Level and Shape
f429d50b-6a9c-52d5-b93b-094a94edf37d | note | Acceptance/Conformance criteria - Construct lifts between 2.5 to 5X maximum stone size to ensure good compaction (100-200m). Surface shape, finished and tolerances shall comply with requirments of TNZ B/02- -25mm/+5mm to design FL measured between centreline and pavement edge
e04543af-13d1-53a9-960b-7a246a320236 | note | Standard/Specification - Aurecon Civil Spec 6.7.4 TNZ B/2
b0cefe15-e409-53c2-acb1-16df6b333028 | note | Verifying Document - QA cheetsb and as built survey
09051cfe-7831-5841-8af3-0186266728a2 | note | Frequency - Every 10m for each section of basecourse
db622578-3d9c-5f4d-b6a9-ad7c13202883 | note | Verification Activity: Activity - H
f7952678-1b48-5f69-bb4a-82d252c09954 | note | Verification Activity: By - SE
6d135904-c407-5793-b3c9-85912964e24d | note | Downer Signature - H
25cdad00-f174-5d9f-85bc-ffa986fae855 | note | Engineer Rep Signature - R
cc6c4c16-be5d-5560-ae5e-b27f302e9030 | note | MSQA - I
e8a46aa4-7ee5-4c17-b04c-fe483812b9a2 | signoff | AUTHORITY HOLDPOINT
b49b8c92-b5fb-49d8-b24c-cb823df44de0 | checkpoint | 5.12 - Sub base Compaction
a9f324de-bd5b-5cee-a141-1555dc18f668 | note | Acceptance/Conformance criteria - Clegg testing of Sub-base course to achieve CIV 25+
9ec98ca9-ae5f-5859-a4e6-8cad6a3b4d2b | note | Standard/Specification - Aurecon Spec 6.1 and GCOR-0042
10ddb4d3-d9b1-5a09-9cef-8e8c717acd68 | note | Verifying Document - QA sheets
da51b825-3d34-56d4-b6e0-0f674fcefa37 | note | Frequency - Every 10m for each section of basecourse
e8bb3690-474a-5ea4-bcdf-acbe99d0c406 | note | Verification Activity: Activity - H
61b2bdc2-d69a-5eed-b212-3dc84c75a6d9 | note | Verification Activity: By - SE
53bde335-ba9d-5aee-be44-c25e47590d6a | note | Downer Signature - H
7c211728-44c9-5890-8b98-331deaeb3730 | note | Engineer Rep Signature - R
0c0056b9-c5a6-59be-b046-05eac96dc016 | note | MSQA - R
15919276-5ce0-45ef-a71a-3f3ef1553e3e | signoff | AUTHORITY HOLDPOINT
f5e9fc48-a751-49b6-8a7d-499945da7310 | section | SECTION 6 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
14199a51-90eb-4e11-bf40-2e82d736c699 | checkpoint | 6.1 - Construction Record Compilation
1fbc5eb9-4ac0-56f7-ab12-29a773ab3993 | note | Acceptance/Conformance criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
6b6c84e9-7641-5bab-be4e-23717491bebd | note | Standard/Specification - Downer
ddc89d8f-ccf9-58ae-845e-7bd9a90ab38c | note | Verifying Document - Records
9be18f34-a31a-57d0-9fb4-3bb48c7e9da6 | note | Frequency - Post construction
ab7ef68a-7f92-5ccb-9aa1-598fd99ceabc | note | Verification Activity: Activity - H
27574554-2145-57b9-9b47-02c9e8ce1784 | note | Verification Activity: By - ENG
0b4e6472-a59b-580e-bbca-2d4df034b068 | note | Downer Signature - H
e4f759c8-d340-5363-ba51-4953b18da370 | note | Engineer Rep Signature - H
90bbdd32-fb07-5e77-97f8-48e4a5103ba5 | note | MSQA - R
24f24fb9-56bb-48a5-9469-b14a831b1cef | signoff | AUTHORITY HOLDPOINT
6e82c65b-e598-4c85-9e54-cd5715399d46 | checkpoint | 6.2 - Survey Record
dab791a1-567f-5816-bd38-cbf951ebb66e | note | Acceptance/Conformance criteria - Installation of works under contract completed compliant in accordance with all relevant regulations, COP and standards
2ffdebc2-b75d-5304-b441-9dc1660c8e03 | note | Standard/Specification - Design Specification / Downer
7375d42b-a4f4-5067-a151-843d944298cf | note | Verifying Document - QA Checksheet, Redlines
455db852-f7d0-591f-85e6-a06b6813a48b | note | Frequency - Post Construction
6b9a81ac-af89-517d-8105-2baecd5ee0be | note | Verification Activity: Activity - H
4a563c05-7a4f-5d0a-8973-87cfdd1b9dad | note | Verification Activity: By - ENG
90b4d2b2-a3a5-5f14-b65e-adef3cfa2d84 | note | Downer Signature - H
fab60652-0f7d-58a2-aa02-2952abe70691 | note | Engineer Rep Signature - H
f01b3191-e9cb-5544-aa5c-eccab3724349 | note | MSQA - R
5bdd24d5-7e38-43c0-afe8-9265b45feb73 | signoff | AUTHORITY HOLDPOINT
7e2902a8-18bb-4ae2-a431-c1153a039f15 | checkpoint | 6.3 - Redline Drawings
96d60e2f-df8b-500c-808a-d7efa178179d | note | Acceptance/Conformance criteria - Ensure all items have been installed create a Redline Drawings for Asbuilt creation noting all changes with RFI numbers and departures in red pen
4ab4d7b8-426a-5740-86e9-2e08dd5cf791 | note | Standard/Specification - Downer
2b47d52c-057f-5469-8bd2-f28a5deedd77 | note | Verifying Document - Redlines
c2ab2b52-5f78-5a70-8cbb-0b022927816f | note | Frequency - Post Construction
964ff206-1400-55a6-896d-5be8ce513a48 | note | Verification Activity: Activity - H
b7953067-92f9-5fee-8d72-0a7a221f8648 | note | Verification Activity: By - ENG
ed8ddaff-fcd0-5c4c-abb1-3128c2efba6b | note | Downer Signature - H
9500d528-efaf-57f9-9d0c-bc1ba877ee5e | note | Engineer Rep Signature - H
f94fce0f-a5ce-5ac6-bd9c-d2c97a4a293e | note | MSQA - R
1c35f19b-7914-417b-a22d-bd1420370cb1 | signoff | AUTHORITY HOLDPOINT
68118900-ee6a-4f2f-9523-0a301ed9fde4 | checkpoint | 6.4 - Defect, Snag and Punch List
e7efd3b0-ff3d-528e-85a7-b064eb8b539f | note | Acceptance/Conformance criteria - Update the project defects, snag and punch list register
bc6b536a-8bd3-54d4-b048-26971085fd83 | note | Standard/Specification - Downer
2b1eadd7-362b-5629-8f5e-96029f14ad25 | note | Verifying Document - Redlines
6d28c682-9670-5f3e-b708-ff9c21364883 | note | Frequency - Post Construction
af3302e1-1718-5797-8b39-09fd6a032b71 | note | Verification Activity: Activity - H
5ef68211-60b4-575c-9ca6-4033554b14af | note | Verification Activity: By - ENG
3dc004b7-4de3-5fc5-811d-597729b0b633 | note | Downer Signature - H
7ebbb442-e33d-550d-96db-f114c9808959 | note | Engineer Rep Signature - H
dd31e2e8-669c-5461-9c25-c502911ad651 | note | MSQA - R
9e0d01ca-8801-498a-a74f-45d478cfaee4 | signoff | AUTHORITY HOLDPOINT
004a2451-3e4e-4606-91ef-32f2246c79b9 | section | SECTION 7 - SIGN OFF
b3f4e0fc-2cd1-4f1d-91dc-8bd201bbea15 | checkpoint | Customer Release Granted:
924c9d68-8da7-5b29-b401-9029b5153107 | textbox | Certificate Number:
893dd132-4466-5fa3-9f1e-59f744167c3f | date | Date:
f259dc66-0893-47f8-bcb5-4019e2ca4f59 | signoff | Sign Off
b80d3e11-ad18-4a7a-987f-e939491cf2a6 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
eeff83fe-9d68-575e-86dc-0075572d98c4 | textbox | Contractor's Rep Name:
108f4bac-0c48-5ebb-ba75-908597fe59b4 | textbox | Engineer's Rep. Name:
135764f4-ce24-5f2f-a59e-f31922c27e46 | date | Date:
d3d09d47-7640-41eb-acaf-ad6bf2f694ef | signoff | Add Signature
3b2975e8-cf2c-4fda-ad8f-28866cda3174 | checklist | DN1211-004-ITP Light Pole Foundation | itp | DN1211-004-ITP Light Pole Foundation
d84a9721-b766-4516-b053-25ee3e537b8d | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
673e1b31-1795-4cea-b8a4-ef3a58d80b28 | checkpoint | 3.1 - Construction Pack
fd68e972-5337-5a0d-b2cf-dfe1e15c9b39 | note | Acceptance/Conformance criteria - Submit a Construction Pack including a Methodology and JSEA to the Engineer before works
36286287-b899-5450-9713-added23dc830 | note | Standard/Specification - Downer
7a5abcec-e626-5c67-a79f-909087d7d728 | note | Verifying Document - Construction Pack
27c44348-b7d8-57e2-9593-270d35363057 | note | Frequency - Submit 5 days prior to commencement of works
d0168738-0bc1-5afe-8d8e-559c9c781fe3 | note | Verification Activity: Activity - H
e8d8ea0c-5b11-5f98-ae22-7013a9a9a958 | note | Verification Activity: By - PE
5111a84b-a6ef-5ea6-855e-3b11cc4fe982 | note | Engineer Rep Signature - H
1c932211-233b-406f-802c-69cbc805b289 | signoff | AUTHORITY HOLDPOINT
046ff1d2-d773-4b41-aac7-339dd80d95a6 | checkpoint | 3.2 - Survey Setout
071f199e-9709-59d8-8d67-05f4e468baf7 | note | Acceptance/Conformance criteria - Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed.
ee4690d8-a500-5bcb-b997-a519b6b14248 | note | Standard/Specification - Downer
7f84dab8-c4aa-50fe-9834-9de2aef06af9 | note | Verifying Document - Survey Records
55c57a93-e767-5ee6-99bc-db6a333fbc17 | note | Frequency - Prior to Works
725e30f6-1178-5ac9-97bd-b9bd253c658d | note | Verification Activity: Activity - H
63a235df-ad5a-516a-8318-59465a99577f | note | Verification Activity: By - SV
e293f2ad-0e2f-5593-a4f9-15e628d080bb | note | MSQA signature - C
a5744ee5-2f5d-4125-bc32-ffe26b8b37c5 | checkpoint | 3.3 - Service Location
c59a2203-e160-5889-8e29-8dfdc4ce1edd | note | Acceptance/Conformance criteria - Complete the Excavation permit process to identify, locate and protect all services.
50ad1f61-48a2-5c07-9248-a70d3fc87719 | note | Standard/Specification - Downer
9eb1ff3f-031d-5a65-a277-7b15c38c2577 | note | Verifying Document - Excavation Permit
80dd3353-d89d-590c-8a8b-24501d7e5082 | note | Frequency - Prior to Excavation
d9da61c0-5d22-5a35-bff3-64749bec083c | note | Verification Activity: Activity - H
03a87d8e-84ff-56ef-b9ee-eafa15ab4ecb | note | Verification Activity: By - SE
e518f1d6-4ebf-4e16-999b-0a4bee5e7dfd | checkpoint | 3.4 - Internal Permits
f620c7ed-fa63-5520-80d7-2310496bed88 | note | Acceptance/Conformance criteria - Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc.
1975d496-2d42-5197-b316-0f249f0a528c | note | Standard/Specification - Downer
59e678ed-6d93-551e-ad32-e53eeee2749b | note | Verifying Document - Internal Permits
4c09870b-3414-54bd-8d02-8bf96b907870 | note | Frequency - Prior to Excavation
1a354041-59d9-5dbb-bf65-a1473d1826d7 | note | Verification Activity: Activity - H
c6b5220e-fe1f-54b7-b023-3dfa4db6c74b | note | Verification Activity: By - SE
8ce2c473-cc59-4ef9-a845-3b55003fa0cb | checkpoint | 3.5 - External Permits
6409c741-a039-58be-aa44-1ac23a466afe | note | Acceptance/Conformance criteria - Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc.
a09fcdc1-68d4-5d48-a537-aa67b2aac5c3 | note | Standard/Specification - Downer
16b425ef-4e0f-5fc7-8445-d3dcc6556cee | note | Verifying Document - External Permits
0c3b7919-4f95-539a-a8e9-43fe1638964a | note | Frequency - Prior to Excavation
e5221398-3fa5-517a-8dfa-3b8785a23e3e | note | Verification Activity: Activity - H
f6bb8467-4c34-5387-aad2-1ec244e92244 | note | Verification Activity: By - PE
18b94ee7-beef-53ac-a7d7-05e4a6ab2bc4 | note | Engineer Rep Signature - R
1932e812-9c8f-423c-8682-c88e0e8e9292 | checkpoint | 3.6 - Approved Construction Drawings
ea28bc33-1cd1-5db5-9d86-408c761b93e8 | note | Acceptance/Conformance criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
501a21de-f6e0-5fe5-b28c-976037a55a06 | note | Standard/Specification - Downer
63518f7f-c700-58be-a0df-eb6122164ffb | note | Verifying Document - IFC Drawings
e96647ef-295d-53b4-a599-37cbcdc10645 | note | Frequency - Prior to works start
f998183e-4b4f-5616-81ce-43cb5a0f1d47 | note | Verification Activity: Activity - H
0059a289-faf2-54d4-8f32-a876eaadbf61 | note | Verification Activity: By - PE
f3f2ecd9-9ed4-49c7-8c4a-e2b20c9057c8 | section | SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
3dc6321d-f072-43a5-8778-441ff9134c11 | checkpoint | 4.1 - Mix Design
5dcf2ca8-0e1b-5b1f-a368-2392b2eba718 | note | Acceptance/Conformance criteria - Concrete to be 30Mpa as per DRG-SS-2231 19mm max aggregate . Contractor to provide mix design and strength testing records on request
a21d4841-d3e4-543f-9b9e-01b4537e9ca0 | note | Standard/Specification - Downer
a4af93ce-2c1b-5ba2-8d48-add42e801ea6 | note | Verifying Document - Approved MAR
67d60c79-9b46-5433-9556-b8af22534ea8 | note | Frequency - Once Prior
855ff496-5fa5-5381-8e68-3583531183c1 | note | Verification Activity: Activity - H
db2d85b6-0af3-5023-8a89-38b65bf84ca6 | note | Verification Activity: By - PE
4ae8fc68-dc34-5b3b-a679-a4a9d869033d | note | MSQA signature - R
44b4b073-b525-5f29-8968-64f8410c565b | note | Engineer Rep Signature - R
dc885cc8-5741-4890-9467-611607979bec | checkpoint | 4.2 - Mortar
8df9fde9-1cd1-5e7b-837f-a1f7c3511d7e | note | Acceptance/Conformance criteria - Consisting of two parts fine, sharp, well graded sand to one part dry cement.
3b03def6-6419-579f-b9d8-85f04ea2569c | note | ○ Mix by hand or mixer in small quantities use within 30 minutes
47b487ab-afca-50f7-ade3-f92cedb9f05e | note | Standard/Specification - Downer
6fca6c94-3013-5bfd-aa18-71d64b3d9be8 | note | Verifying Document - Approved MAR
0bd81cbd-79eb-5bb3-b499-42254fa34315 | note | Frequency - Once Prior
466c9518-7d01-5a86-8ead-d2f9474d41d9 | note | Verification Activity: Activity - H
fad436e2-a961-5b66-8f7b-cc34a6e49634 | note | Verification Activity: By - PE
81e20db2-f441-5cb3-9483-de64719d8654 | note | MSQA signature - R
d7c06e17-a1c1-5784-97d2-d2681e39280e | note | Engineer Rep Signature - R
1642d5c2-43f2-4749-85ae-e9d1f45fbe2b | checkpoint | 4.3 - Reinforcing
a5556231-3768-5cde-b02e-91d2f3312813 | note | Acceptance/Conformance criteria - Reinforcing as per Aurecon Specification
d5d257a3-b385-5b86-b2eb-c33c2aa4bb09 | note | Standard/Specification - Downer
d39b9b93-9f2a-57d0-8cfd-0ed502c8c7ad | note | Verifying Document - Approved MAR
23fe36b3-c7d9-5aa3-b867-54e234045f36 | note | Frequency - Once Prior
0c65330c-ba2f-5b1f-81ee-de4cc50bc05b | note | Verification Activity: Activity - H
054b2cd6-118d-5e58-b431-af9b28dab5b6 | note | Verification Activity: By - PE
b52bfb01-d7a5-5733-9aa8-3fcca807fb3c | note | MSQA signature - R
923ccdae-0d88-5e6f-adde-1a306271a705 | note | Engineer Rep Signature - R
f3354c4f-7906-4cb8-9dab-42e563db0340 | checkpoint | 4.4 - Hold Down bolts
9183297a-7711-5f44-b519-25b5976c54e4 | note | Acceptance/Conformance criteria - Hold Down bolts as per pole manufacturers requirements
9a2ef176-5916-56e6-94fc-41f32b286ab3 | note | Standard/Specification - Downer
f63ed307-10ac-5e35-8720-b6225a4fce30 | note | Verifying Document - Approved MAR
32236ccf-abe8-576a-9348-e997505c22da | note | Frequency - Once Prior
c2f4a7fe-4999-5a5b-8f2f-230ab511c25f | note | Verification Activity: Activity - H
836afd44-ec11-56b7-8586-62e360ea9d63 | note | Verification Activity: By - PE
ca586fe1-7b3c-5475-8ea6-5ac9a46dcda6 | note | MSQA signature - R
690a0c49-f4e1-5d00-8c04-37c87b5917a0 | note | Engineer Rep Signature - R
18cdfcb0-48bd-487c-a14f-218cf4979f1a | section | SECTION 5 – CONSTRUCTION ACTIVITY – LIGHT POLE INSTALLATION
f3448578-ed6e-4d5a-9d54-f8bf6cdb7dd8 | checkpoint | 5.1 - Set
f3273900-d22f-58c5-ac9d-3935c7fc67ba | note | Acceptance/Conformance criteria - Centre of Pile set out as per Model coordinates provided.
ca16090f-a082-5769-8dea-d036491110f0 | note | ○ Hold down bolts to be surveyed to essure they align with the location of Light pole bolts.
8d102aa6-d245-5c8d-b3fe-b7d1cafee1ec | note | Standard/Specification - Downer
ec0fd8f2-4b63-50a6-9b78-b0a78950fcf0 | note | Verifying Document - QA Checksheet
2d3299ee-9619-5a2b-8653-42fa2c99ec09 | note | Frequency - Prior to concrete pour
320dbf0b-63d1-5cea-a063-5cd2a79654e4 | note | Verification Activity: Activity - H
0c25dd24-0ac1-5baa-90e2-3ea28447e926 | note | Verification Activity: By - PE
4ead5bf5-32b1-42ef-b316-391e4d45236f | checkpoint | 5.2 - Reinforcing
61318046-7f65-571f-a259-d267b9ecc1e7 | note | Acceptance/Conformance criteria - Reinforcing and embedded items cut, bent (cold) and accurately placed as shown on design drawings. At least 30mm cover to all reinforcing +5mm/-0mm
e87fe87f-f91d-5b8a-86eb-61b758a36bf6 | note | ○ Bar spacing as per Drawings +/-10mm Bend locations as per drawings +/-5mm
b838a733-185f-5b3f-bc79-f8715213646a | note | Standard/Specification - Downer
d9995f24-a8e8-5596-9b7d-475ce3b34f7a | note | Verifying Document - QA Checksheet
7e4c9575-073f-59a5-9591-ec8fbd686030 | note | Frequency - Prior to concrete pour
71d6ad96-8044-52da-bfc8-4fa328689afe | note | Verification Activity: Activity - I
abf7b133-a432-5f3a-b4b5-5e76a83c549d | note | Verification Activity: By - PE
ef8343be-e1ab-4fed-bb0d-22a45f343e1f | checkpoint | 5.3 - Conduit Install
3e8f9ba0-2b9b-5651-8bb4-89efde2a28fc | note | Acceptance/Conformance criteria - Conduits installed as per NUO requirements and DRG-SS-2231
a5854f54-2b24-5f47-b505-cf92133fa684 | note | Standard/Specification - Downer
894ccfb8-940b-5893-8485-0ebb4f43fa20 | note | Verifying Document - QA Checksheet
35710b20-2f55-5319-ad8e-4e47320ecb9e | note | Frequency - Prior to concrete pour
3593675f-8f79-5369-94de-588c4df9e4a0 | note | Verification Activity: Activity - I
0eadb16f-1ab8-4f1b-8402-0077e22441a4 | checkpoint | 5.4 - Pre Pour inspection
54b9377d-3723-5e7a-861c-cd53344e50c9 | note | Acceptance/Conformance criteria - Notify Engineer for inspection atleast 24 hours prior to pour
db7c387e-6546-5ab0-9e6d-c7ff762b334f | note | Standard/Specification - Downer
8d870049-351a-587a-abf8-4bd518ff82c4 | note | Verifying Document - Pre pour checksheet
75b09384-b399-5bd9-8286-438a60891060 | note | Frequency - Prior to concrete pour
70394458-8c9f-5c46-8001-66f676c40dd5 | note | Verification Activity: Activity - H
5bc7ccc0-8c2c-544d-999c-1b9c492085a2 | note | Verification Activity: By - DES
adfa0260-fa42-56bb-b9d2-32fbbf04d361 | note | MSQA signature - C
4940ffca-180d-431b-980c-de50fe2c2c94 | checkpoint | 5.5 - Light pole bases / Pile
748951df-d44e-5061-b7a4-aff48e99ccf3 | note | Acceptance/Conformance criteria - Concrete shall be high grade with a minimum compressive strength at 28 days of 30 MPa
9ffeae4b-2075-5f22-92ac-0914a21a417d | note | ○ Concrete slump shall be 175mm +/-25 mm.
f0086a6b-eeb1-5a64-898d-920acd12db34 | note | ○ Concrete to be tremied. Vibrating pokers to be used during entire pile length pour.
bc2668d1-d5c3-5490-9d61-5a74c5ecaa19 | note | ○ Delivery dockets dated and showing the concrete supplier and design strength shall be collected and held for every pour. Record location and date of each pour.
aca4d5b3-2f1c-5597-ae93-587ffee7d343 | note | ○ 3 cylinders taken for each pour slump targets as per mix design (1 sample per 75m^3 or each pour)
6c68476d-900b-5f58-ac4d-e0eb68934a54 | note | Standard/Specification - Aurecon Spec 15.5
d6ebfa5f-e17d-5857-bd46-d964757d6ee3 | note | Verifying Document - QA Checksheet
6d6512d4-7ebf-59e3-876f-81279c7883a2 | note | Frequency - each structure During pour
6a62a0d6-6143-5276-9198-b30a2347042e | note | Verification Activity: Activity - C
c8920a0d-809a-5a9e-bb63-495fcefdaa45 | note | Verification Activity: By - SE
4d082e6f-bc64-5387-a093-27bc7bf7e529 | note | MSQA signature - W
f8516e85-0edc-4417-bd81-45ce9f68d63f | checkpoint | 5.6 - Post Pour
96050fa8-4879-5353-90a7-44055be44578 | note | Acceptance/Conformance criteria - Concrete cylinders to achieve minimum target satrenght after 28 days. At the Engineers request site samples/cores for indepentdant testing of fresh or cured concrete to review grading, mix design, strength and thickness.
0110dcb5-fb5d-5539-98ce-e90a4f5248c0 | note | Standard/Specification - Aurecon spec 13.
02edeef7-462a-556b-b662-573891049e0f | note | Verifying Document - Test Report
1050a44c-2166-5db9-8805-5c0473284365 | note | Frequency - As requested
4aae929f-bd16-5c00-af93-9fb7c7c26db1 | note | Verification Activity: Activity - H
ffbc812e-4b0e-54e3-a1d1-79f26a6c7adc | note | Verification Activity: By - ENG
45421a52-d625-5361-9a85-4bb323b4e0b4 | note | MSQA signature - R
b0c80322-4e52-591e-8fbc-01d267959061 | note | Engineer Rep Signature - R
36cde351-9b29-4f48-92c6-c852df138bd4 | section | SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
422cc682-adb4-4f4f-8b4a-e7b3ab072630 | checkpoint | 6.1 - Construction Record Compilation
a50682f3-d35f-5d18-b47c-e2af593fec1e | note | Acceptance/Conformance criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
9668b294-9dc0-52cc-854a-078340cab13c | note | Standard/Specification - Downer
8cc142da-7611-5cad-b3c2-15b1f56ccc9a | note | Verifying Document - Records
801e4bdc-c26d-52c1-a483-5db94dd00322 | note | Frequency - Post construction
11f85c52-be7c-5938-bee1-225a5029e82c | note | Verification Activity: Activity - H
498fb547-a49f-5547-affe-ae11a7639737 | note | Verification Activity: By - SE
c42a5358-4476-5f10-827a-db1fafe08182 | note | MSQA signature - R
d5dc4768-4981-54fc-8de7-965bab943e10 | note | Engineer Rep Signature - H
a5c39621-28de-47fd-84df-4193839101da | signoff | AUTHORITY HOLDPOINT
dbb1165a-10c5-4842-9673-5ba4bc077d9f | checkpoint | 6.2 - Survey Records
ac51a0f0-df6c-5d4f-9d21-4759a0487658 | note | Acceptance/Conformance criteria - Ensure all items have been surveyed and records are assembled for asbuilting
cb36f807-f149-5434-96bf-d3a19b8fea0e | note | Standard/Specification - Downer
9470851c-0218-58c9-bc55-d238cef824ef | note | Verifying Document - Records
9b21bc37-22bd-5ad1-b88d-55cf5498ac0d | note | Frequency - Post construction
89b48158-5579-5e8e-8bfd-cc0f6b6809a8 | note | Verification Activity: Activity - H
21ceaaf2-b2a6-5494-b59d-6fe8467a5fac | note | Verification Activity: By - SV
62359f2f-f2aa-56d6-a3b6-6974aec89fd9 | note | MSQA signature - R
70c80119-4b6b-5042-9d89-27d08fa6268c | note | Engineer Rep Signature - H
c0b4e904-81c5-43d4-a7b1-025ee6aee9c7 | signoff | AUTHORITY HOLDPOINT
6f8901db-2b43-4b7d-a3ab-add77086dddc | checkpoint | 6.3 - Redline Drawings
d9a32c47-b533-536d-abb8-e5b25af3c85a | note | Acceptance/Conformance criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen.
c61e0633-2468-5a98-9c81-f069b7895294 | note | Standard/Specification - Downer
ead58c63-11d3-55a2-b14c-598855ebf9d8 | note | Verifying Document - Redlines
4479407b-9eca-5545-bf6c-d3f1af8200fc | note | Frequency - Post construction
632b2ab2-670e-55f3-b4da-9ecb4e13ff35 | note | Verification Activity: Activity - H
0011151c-5ba2-5287-b50c-32d6433efe56 | note | Verification Activity: By - PE
4b9a0fb6-2a9a-5879-9c40-4d52eac70b0b | note | MSQA signature - R
833aba58-8f34-5063-bd4b-5d2be0ed6c7d | note | Engineer Rep Signature - H
b025ec4c-f78f-4b8c-8994-23c758d47c58 | signoff | AUTHORITY HOLDPOINT
3020c138-75cf-4f3a-b482-580f52e9fbe6 | checkpoint | 6.4 - Defect, Snag and Punch List
8cf41353-1ada-56c3-945e-020d969f96f6 | note | Acceptance/Conformance criteria - Update the project Defect, Snag and Punch List Register
02234cff-a8f8-507b-9377-828cd3697606 | note | Standard/Specification - Downer
f5708e36-4ac9-5964-aae1-3fbfc6e96e19 | note | Verifying Document - Register
0db3db9b-9ed6-5be1-b443-05783bc44542 | note | Frequency - Post construction
69a8bbec-883b-58dd-853c-afbfe565e8f7 | note | Verification Activity: Activity - H
ed4fe93f-fbcd-5bcd-9cd7-ac35fb2981f6 | note | Verification Activity: By - PE
92297df4-e0a3-5b54-87fe-177336431d6c | note | MSQA signature - R
e59c7158-16e9-565e-a92a-8e75753786d5 | note | Engineer Rep Signature - H
ed065743-2095-4a0f-81b3-12e1145032ea | signoff | AUTHORITY HOLDPOINT
ad55e0fa-6bd2-4b95-8407-d4cad8e26569 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
564dddf9-2d95-56a8-905b-2d718805470e | textbox | Contractor's Rep Name:
c3083b99-cd8f-5fa6-bcbc-61664696c295 | textbox | Engineer's Rep. Name:
41a1cb8b-220f-52e2-898f-55d8c8c14143 | date | Date:
91108046-524b-4669-9d70-0282c5b8e432 | signoff | Add Signature
7958f9fa-5a75-4f88-b658-c81b9f62b2b1 | checklist | DN1211-006-ITP Bus Shelter Foundation | itp | DN1211-006-ITP Bus Shelter Foundation
cba63b97-c908-4afa-ab0b-b47a7a1c6414 | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
51ced275-2d2a-43f3-a087-7a73c3591301 | checkpoint | 3.01.2001 - Construction Pack
e94bd8d4-54bf-5abf-9745-032b49da898c | note | Acceptance/Conformance criteria - Submit a Construction Pack including a Methodology and JSEA to the Engineer before works
2d8ea5cc-2bc7-5dfa-9c53-864c7c398a61 | note | Standard/Specification - Downer
d9be808e-f28f-5345-b109-53e2c0303ac7 | note | Verifying Document - Construction Pack
6027e86b-4611-5ba5-9b78-f0f56f945fcc | note | Frequency - Submit 5 days prior to commencement of works
5d41f0d1-6be3-541d-b258-dd224102e85a | note | Verification Activity: Activity - H
e066f176-97d2-5a1f-9ce0-fd71487e6281 | note | Verification Activity: By - PE
68078607-ccbc-576b-88bb-fc7475450b06 | note | Engineer Rep Signature - R
e81239e9-297a-4d9d-8ced-f05a1bc9b9dc | checkpoint | 3.02.2002 - Survey Setout
365a4a91-4264-5a48-afc0-b95e339432f9 | note | Acceptance/Conformance criteria - Survey Set out as per contract drawings and specification, capturing pre- construction levels where needed.
347ba862-129a-522b-b71b-060a29028054 | note | Standard/Specification - Downer
0a0ee717-0c2d-5b60-a36d-8c743f690d46 | note | Verifying Document - Survey Records
aaa6aa21-446e-5f22-8173-3e5d54783411 | note | Frequency - Prior to Works
9f116a89-3511-5af4-b342-46ad079b1525 | note | Verification Activity: Activity - H
0bf37fda-d4af-5df4-845c-e3c7ea4f63fe | note | Verification Activity: By - SV
9444fcd4-223b-4628-8d0e-4c31d87799ae | checkpoint | 3.01.2003 - Service Location
0b599521-1b25-5208-814a-f575cf107017 | note | Acceptance/Conformance criteria - Complete the Excavation permit process to identify, locate and protect all services.
3f81e338-e6e6-5cfa-904a-4b4ae59759f5 | note | Standard/Specification - Downer
2d3e72bd-161e-55c9-9715-3560720ecd37 | note | Verifying Document - Excavation Permit
aec528ba-4d83-58b1-aa4a-61f52ae95933 | note | Frequency - Prior to Excavation
eba84832-3482-5d42-b1ce-2ad8a9c565e9 | note | Verification Activity: Activity - H
31087ea9-a4b4-5985-9593-cf0a267651b4 | note | Verification Activity: By - SE
2be5cd2c-6d78-49f1-9885-9d083ea9db78 | checkpoint | 3.02.2004 - Internal Permits
d44a9d2d-e983-58f5-a41e-b961a3bea7d1 | note | Acceptance/Conformance criteria - Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc.
e9c5c2b5-52f8-5b1e-a4af-8dea89efd787 | note | Standard/Specification - Downer
cacb440d-e0bd-5cf1-9ce1-ffaf8da4114d | note | Verifying Document - Internal Permits
da14e229-fb27-5d75-aea9-b167b27df948 | note | Frequency - Prior to Excavation
dc7fa015-99ce-5c2b-870e-1e3ceafb36ff | note | Verification Activity: Activity - H
10f68098-3ec6-55f9-a6cf-15c99428ae3d | note | Verification Activity: By - SE
ee1e7102-2da5-49b4-9dd3-0ae9aaf90eda | checkpoint | 3.01.2005 - External Permits
f769d8a9-8e52-5193-904d-e2df45c3ab9b | note | Acceptance/Conformance criteria - Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc.
009596ee-c059-546b-9fe0-b323bf362e1e | note | Standard/Specification - Downer
6701a68f-701a-5b29-9add-6010572ab374 | note | Verifying Document - External Permits
a6fd8d06-9d64-5156-8e41-b89d5782d692 | note | Frequency - Prior to Excavation
4736c828-cfa6-5c8d-abc6-7965dbf06ddb | note | Verification Activity: Activity - H
2fec2a68-801f-540f-9b2b-ea7e1f537bc0 | note | Verification Activity: By - PE
01879716-1181-514e-b787-9dd457d3eca0 | note | Engineer Rep Signature - R
cc881e49-2165-4fd0-968a-96531f6db7b1 | checkpoint | 3.02.2006 - Approved Construction Drawings
30b1c7b6-a468-55cd-a9c1-7d017434213e | note | Acceptance/Conformance criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
2da79b86-3a6c-5245-9528-63f084cbcd73 | note | Standard/Specification - Downer
b047b26d-4d91-59fe-b2c0-a31b5dade130 | note | Verifying Document - IFC Drawings
2e6326f3-d03e-57e6-888c-217a9cf2b4c4 | note | Frequency - Prior to works start
d101084e-b78b-52d7-99c1-62e5b5a9cab1 | note | Verification Activity: Activity - H
f6a0a763-aa7a-589d-b37d-070208b5a4e0 | note | Verification Activity: By - PE
9e49a8b1-8b44-45a1-88ef-8e000dae4890 | section | SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
12e55008-3c0f-4ad8-9b8f-4e365ab60e37 | checkpoint | 4.01 - Level and shape of Subgrade
59a7ab6e-8569-558b-9f9a-cfdedb399152 | note | Acceptance/Conformance criteria - pavement subgrade tolerance ; +/-10mm from design subgrade level. Excavation deppth must be at least the design pavement depth for LMC locations. Subgrade shape as per survey set out, to be verified on site
828f3e5e-3508-563f-941e-def7dd1b1321 | note | Standard/Specification - Aurecon Civil Spec; Section 5.6.9
7c1d39ad-bf03-5169-b88b-9037717854d0 | note | Verifying Document - As-Built
1489c8a2-82e5-5206-b08f-f65ed3c0f5a2 | note | Frequency - Once per footing
6fa042fe-b3d9-5e74-bdfe-4ae68b498f87 | note | Verification Activity: Activity - I
1bc3cfe4-2dd1-51ef-bbfe-4ef725feb84a | note | Verification Activity: By - SE
df874953-91f9-5e72-85fb-3a247c673391 | note | MSQA signature - R
bb4d7403-3c7b-45ba-a869-423cc6c3d555 | checkpoint | 4.02 - Aggregate basecourse (If used) AP65
73345508-7033-5b85-a7f4-fd685302d898 | note | Acceptance/Conformance criteria - The basecourse aggregate shall be sampled and tested by an IANZ Accredited laboratory for Crushing Resistance, Weathering Quality Index, and California Bearing Ratio.
cded969a-b548-5420-8cd9-1f53cddb391e | note | ○ Grading to be compliant with AT 0800 grading specification
c0caffcd-ce79-5153-ad73-7f7756b3052c | note | Standard/Specification - Aurecon Civil Spec 6.5.2 TNZ M/4
302a69f0-6c6a-582b-871a-96f5fe62abd0 | note | Verifying Document - Material Certificate / QA Sheets
0d292ed4-8fa1-59d4-9143-564dc3bad905 | note | Frequency - Prior to Use
17bc5438-cda7-5115-9690-2333f4cfd4aa | note | Verification Activity: Activity - H
8b2fe84b-34c9-528d-8cde-d96ecb839714 | note | Verification Activity: By - SE
867547ea-370f-5fb3-86fd-ac1c6173c674 | note | MSQA signature - R
df6a7832-887c-4014-a633-fe7ac1360803 | checkpoint | 4.03 - Mix design (Concrtee and Blinding)
4c96208a-f7de-59c7-a5e0-ddcf33de32d7 | note | Acceptance/Conformance criteria - Blinding to be 10Mpa mix
cc068b9f-d2a0-5c8c-a708-62e29fc2e7a9 | note | ○ Typical structures - confirm supply of "high strength concrete"; 20MPa concrete; 19mm max aggregate size.
723d1aeb-f5a2-5961-9df9-cd4eb5ce1869 | note | ○ As specified on drawing use marine grade concrete 30MPa,
4b738b1d-6883-5578-b16a-d75345b9ca28 | note | Standard/Specification - Aurecon Civil Spec Section 14.6
eef9275d-5fcc-5ca9-8cb4-ff23518f1c9b | note | Verifying Document - Approval Mix Design
5c035c6f-e645-5f5f-aa1b-5f1ebcd74654 | note | Frequency - As required
7636007c-0d96-5745-919e-b24747553d9d | note | Verification Activity: Activity - H
6238f9b8-3ae6-5a45-bd2a-eea91c08b6bb | note | Verification Activity: By - PE
d2444b61-2886-5995-ac4b-d4a8595a8dde | note | MSQA signature - R
f4644701-367c-45fb-a70e-0e58752e87af | section | SECTION 5 – CONSTRUCTION ACTIVITY – BUS SHELTER FOUNDATIONS
5f035888-ae64-466e-a233-e5d1238bc3bf | checkpoint | 5.01 - Setting Out
855112c3-234b-5481-965c-84c1bc1eb44a | note | Acceptance/Conformance criteria - Before construction,Contractor to mark out extents of structure
8da6574c-2724-5430-82ef-5df6cdeac4dd | note | Standard/Specification - Downer
038fcbc6-3f36-55a9-b79b-eeca934546f7 | note | Verifying Document - Pre pour checksheet
dcd42667-1212-5ceb-a0b2-aea684cdbac2 | note | Frequency - Once per struture
f6974117-cbcc-5d88-ad3a-f60a6fe33e70 | note | Verification Activity: Activity - I
f645478e-7624-5048-9a16-ab9af7d92f37 | note | Verification Activity: By - SE
c18cbeb8-4c3b-5c2d-b9eb-2c364d07f2e3 | note | MSQA signature - I
8f9d519e-55bc-41d5-b177-60d761b04db9 | checkpoint | 5.02 - Subgrade Testing
66aaf42e-2c3e-5ebe-852e-fe777856030a | note | Acceptance/Conformance criteria - Conctractor to confirm subgrade strength and report to Engineer via QA inspection
ec12c4de-0127-5acc-a979-0984cf5b4284 | note | Standard/Specification - Aurecon Civil Spec; Section 5.6.11
fe7130ab-fdab-56e3-9870-ddbe51557894 | note | Verifying Document - Pre pour checksheet
460832b6-a54f-5736-92ba-04ab0dbd493d | note | Frequency - Once per struture
6c811b9f-f09c-567c-a6bd-1bfd653780f4 | note | Verification Activity: Activity - H
54ba236e-b2f3-5dce-9d37-d8250bf4e01d | note | Verification Activity: By - SE
807697cc-56f2-52b5-92e5-a9aa4a1b261d | note | MSQA signature - I
a24a9d14-aac1-402c-ba8c-0cd09a4f5c70 | checkpoint | 5.03 - Blinding Layer
5e1b831d-1023-5b37-a081-7ffc88f462d7 | note | Acceptance/Conformance criteria - 50mm 10Mpa blinding layer to be placed within footpring of structure
66504dfb-693d-5703-bfda-5a44edc3d034 | note | Standard/Specification - DRG-SS-2270
252cc2aa-c569-53f1-90c1-92b7743ccf10 | note | Verifying Document - Pre pour checksheet
4cbc9fef-4b34-5eb1-8eb3-3ee14a9231bc | note | Frequency - Once per struture
5dff5cbd-e8fc-58ed-bc7a-d009c1d6497b | note | Verification Activity: Activity - I
0727f492-1d30-5b91-b9e3-3e1453dabce5 | note | Verification Activity: By - SE
d4e6d691-e1bf-46d8-a915-d6e0259f210e | checkpoint | 5.04 - Concrete
81196c4f-9313-5379-a01d-c252189114f5 | note | Acceptance/Conformance criteria - All concrete shall be batched by weight and mixed in an approved plant requirments of NZS 3104 High grade and Special Grade
0e949702-a84b-59ff-b350-bbd75ff69c40 | note | ○ Concrete for sturtcures to be 30Mpa concrete with slump target as per mix design
5dc63737-2922-51cf-8ed5-6b5c1160da07 | note | ○ 3 Cylinders taken per pour
ea1f6bcb-2c64-545e-9c88-b6933fdefb5a | note | Standard/Specification - Aurecon Civil Spec Section 13.6.3, Clause 2.15.5.3.2 of NZS 3104
aefdb6d6-15e6-577a-bf55-557d9bcf0fca | note | Verifying Document - Supplier Records Concrete Dockets
18a8b3d0-50db-5a8a-8e72-d4b06e57d2d0 | note | Frequency - Once per Pour
dfbb9361-d1e5-554b-9052-644a56e6097c | note | Verification Activity: Activity - H
5dead79d-c964-5f6d-91ca-24727f6ce3d7 | note | Verification Activity: By - PE
d3826195-ce6d-571d-9239-6f08020726eb | note | MSQA signature - R
a6e475c1-b3d0-5268-b44f-31c27b060dff | note | Engineer Rep Signature - R
30026ddd-0dd8-4b14-a91e-e2cd0fb1644e | checkpoint | 5.05 - Reinforcement
ea72fc0e-a293-57ad-a8df-df1e7f63bd37 | note | Acceptance/Conformance criteria - Reinforcement and embedded items cut, bent (cold) and accurately placed as shown on design drawings. At least 30mm cover to all reinforcing +5mm-0mm
b5f98be5-2266-540b-a0f3-b34d1297d17c | note | ○ Bar spacing as per drawings +/- 10 mm Bend locations as per drawings +/-5mm
75f8e81d-77ff-5a67-a990-1aeaad7d5017 | note | Standard/Specification - Aurecon Civil Spec;14.6.7 AS/NZS 4671
92d75003-dd5b-5e38-9155-639c4391d432 | note | Verifying Document - Prior to Each pour, QA Checksheet
1e098ca4-9437-5cb6-b1a8-26b57624805e | note | Frequency - In progress check
eaa02864-84b3-58f8-9569-f74669dca50b | note | Verification Activity: Activity - I
1fc5e63d-2cf7-56e1-8496-4b58ca63d2f3 | note | Verification Activity: By - SE
e923351d-820c-5ec8-8485-ca4094165125 | note | MSQA signature - I
d48c4816-0e42-4738-a825-d20fd5778633 | checkpoint | 5.06 - Pre-Pour Inspection
025b3664-70eb-580e-8f9a-401241b58362 | note | Acceptance/Conformance criteria - Notify Engineer for inspection of formwork 24 hours prior to pour I nspection
a4480c31-3e5f-5384-8b7c-fc5d3bd3671f | note | Verifying Document - Prior to Each pour, QA Checksheet
0512f188-604d-52a0-a610-52206328479b | note | Frequency - Once per Pour
8fa988a2-57f6-575d-be55-9db3c2c6b633 | note | Verification Activity: Activity - H
902ca77d-f78c-5354-831f-ef26c8594f4e | note | Verification Activity: By - SE
e30778d8-7421-5a59-b7c0-23d87c7998d8 | note | MSQA signature - H
b5e4d00b-53a3-45ba-9d24-220c5e83209d | signoff | AUTHORITY HOLDPOINT
79307f0c-e6f6-4b10-8827-a8903b8a9bae | checkpoint | 5.1.2 - Post Pour
a3db9835-59bf-54f9-832a-89f1617f16e6 | note | Acceptance/Conformance criteria - concrete curing for at least 5 days. Form removal after atleast 12 hours. Post pour inspection to be submmitted for Engineer's acknowlegement showing finished concrete is within tolerances (surface level +/-5 mm)
e79495da-3afb-5cd5-8fb3-860043c2e8a6 | note | Standard/Specification - Aurecon Civil Spec Section 10.1.11, NZS 2566.2; Section 6.3.4.1 & 6.3.4.2
944ceb1e-2784-5bc2-bb7b-772c26e965fa | note | Verifying Document - Test Report
fcc433ee-bf30-5e8e-a427-e4df3ee3b7a6 | note | Frequency - Each foundation
e06a5f8a-6110-5223-971c-b4c79e01c93f | note | Verification Activity: Activity - H
5cbc1f74-0bc5-59de-8317-4a1b35e62f63 | note | Verification Activity: By - SE
07ecb7e2-6015-54ca-b5a6-37a28467c1d4 | note | MSQA signature - R
a59e8bd3-5979-4f45-a22a-386110acd4bf | checkpoint | 5.1.3 - Testing
6d55d0d2-2ecc-5705-bb27-3dc4c6e6c860 | note | Acceptance/Conformance criteria - Slump test during pout to check workability of concrete or as directed by Engineer 3 cylinder test taken for each pour. Slump target as per mix design
8af51288-a816-5f19-b5c8-962a614d74ab | note | Standard/Specification - Aurecon Civil Spec 14.7.12 NZS 3112
e689eaa5-c0cf-559b-8812-f8d28463410a | note | Verifying Document - Prior to Each pour, QA Checksheet
2386d503-22da-55a6-a54e-d7d331688927 | note | Frequency - In progress check
1cab9526-1da7-58c7-b2e7-36320384a359 | note | Verification Activity: Activity - H
1325aad7-1583-507e-b5b9-e6d6150cea66 | note | Verification Activity: By - SE
a1813211-7605-54f2-a51f-d9c601cb45ae | note | MSQA signature - R
e2ba92ee-9874-46a1-846e-e88793825e5b | checkpoint | 5.1.4 - Independent testing (If Requested)
bbba655c-f334-567c-b6ae-b41538924b93 | note | Acceptance/Conformance criteria - The Engineer's Rep may request site samples/ cores for independent testing of fresh or cured concrete to review the grading, mix design, strength and thickness
f20e733f-ba4f-567c-a3c3-5508119b8eb7 | note | Verifying Document - Upon Request
c001fba5-d1fd-5c21-a5da-ee9631df12e1 | note | Frequency - IANZ lab resport
13dc12f2-40cf-5947-ac62-91b2067cc095 | note | Verification Activity: Activity - W
ed3fa985-bfba-5156-8a8d-7e2fc7f94c82 | note | Verification Activity: By - SE
da58075f-0be7-5d75-a723-6ee716fd1017 | note | MSQA signature - R
37e28d73-49bc-572c-b19c-ebdb40924367 | note | Engineer Rep Signature - R
6ce23d65-38e6-48cf-ad66-eedc2aa489db | section | SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
2f9335af-bfe1-4e03-a3a1-1baa68480bed | checkpoint | 6.01.2001 - Construction Record Compilation
2370f002-e04c-57bc-ac1c-3893f0832a37 | note | Acceptance/Conformance criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
f4745e88-d63b-5c1f-929e-207e73a057a5 | note | Standard/Specification - Downer
330cf7a0-f3bd-5abe-a0d2-c1f520f73f7b | note | Verifying Document - Records
15c19bbf-07c7-5be4-860b-40d9c28b0dd0 | note | Frequency - Post construction
36296401-22bf-5ad9-bb27-bd9745b54642 | note | Verification Activity: Activity - H
61391abe-59b7-57ed-9f3b-15b8a3b34768 | note | Verification Activity: By - SE
0793e617-1423-537f-820e-2002612817de | note | MSQA signature - R
335bce4f-a8ce-5e38-ab78-5e71f0bce415 | note | Engineer Rep Signature - H
35a740a1-9fa2-4e83-bc96-ce1fc2572251 | signoff | AUTHORITY HOLDPOINT
835dfdc5-9ad2-4f89-bb9a-85266f8e4715 | checkpoint | 6.01.2002 - Survey Records
d65e58dc-b2d6-5cc0-87f3-c696b965697a | note | Acceptance/Conformance criteria - Ensure all items have been surveyed and records are assembled for asbuilting. Installation of works under contract compliant and in accordance with all rlevenat regulations, COP and standards unless specified by the engineer
1ba215c8-8ada-5e90-8e7d-25736020c9c6 | note | Standard/Specification - Downer
2bb31c02-b1ff-5a32-b253-ffc0450b9330 | note | Verifying Document - Records
456866e9-f9b5-5720-bc21-b941af0f652a | note | Frequency - Post construction
0d76c141-c2eb-5853-a34f-689563ca09c4 | note | Verification Activity: Activity - H
df7e6f82-61ab-5f6d-b7dd-ef52e27e12fb | note | Verification Activity: By - SV
c3e1d631-b526-5e5c-a6cc-c195ce85f226 | note | MSQA signature - R
90f9012b-eab8-5e2d-a4f6-f7dafd6d80e8 | note | Engineer Rep Signature - H
64dba0e6-be84-4ebf-9ce6-26b2cdc3dcb7 | signoff | AUTHORITY HOLDPOINT
4000ebbd-5212-411f-8b72-0ad4a70216c6 | checkpoint | 6.01.2003 - Redline Drawings
e7d88c02-3e4e-5976-99f9-10773643cb6e | note | Acceptance/Conformance criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen.
0bdcce43-bf81-5c09-88cf-0a716f3ad9a2 | note | Standard/Specification - Downer
de106e5e-6007-552a-acd1-311933c20e53 | note | Verifying Document - Redlines
1f9a3bb3-d8de-5874-8396-8bbb1d71648c | note | Frequency - Post construction
50260f46-7291-5a10-b405-df2ca09b6b2e | note | Verification Activity: Activity - H
bb1c35a5-777c-56cc-badb-af710f92b76f | note | Verification Activity: By - PE
f714c367-8eb6-5929-9377-616f5852bc47 | note | MSQA signature - R
dc692f2e-0fbf-5a85-a3a0-56c24b09f3d8 | note | Engineer Rep Signature - H
6f0a0012-e7c2-4004-8a6a-3a3b5b1fea80 | signoff | AUTHORITY HOLDPOINT
a89d0dbf-e19d-4784-b2a8-796c24d0eee5 | checkpoint | 6.01.2004 - Defect, Snag and Punch List
56d77f95-4dc6-5abf-bb8b-2e5137cf481d | note | Acceptance/Conformance criteria - Update the project Defect, Snag and Punch List Register
89991430-5252-5d3b-9dfb-9e50ab659368 | note | Standard/Specification - Downer
92988bd6-3d39-59b5-9306-ff9110235fe5 | note | Verifying Document - Register
84a6265b-fe76-528c-944d-a288abb80ac1 | note | Frequency - Post construction
524b3694-a270-5cf7-bcc4-ab1939c06bf7 | note | Verification Activity: Activity - H
630c5375-61c0-535a-80e3-6a07d1201e9b | note | Verification Activity: By - PE
a91bfe6d-5799-50d1-81f8-dd38691bdb08 | note | MSQA signature - R
ddd82585-6d3e-5703-9e1a-92486e7c618d | note | Engineer Rep Signature - H
9e327e23-2233-4d7d-a821-baaab24d9ae8 | signoff | AUTHORITY HOLDPOINT
e4b1b9d6-00c2-4dc8-9c1e-0890573d9025 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
089392bf-cd3d-5abd-9082-f8bea23fc6de | textbox | Contractor's Rep Name:
95c509e2-6781-5066-b137-b478d190bf25 | textbox | Engineer's Rep. Name:
98a34ec1-ecb1-561c-b216-dfbcaa7b56f7 | date | Date:
2dc22bc2-749a-4ddf-9e28-b69d34331dcf | signoff | Add Signature
45a1f418-c6e3-4bf6-adf0-dbe36d8859e3 | checklist | DN1211-007 ITP Subsoil Drainage Rev 0 | itp | DN1211-007 ITP Subsoil Drainage Rev 0
bd77c6c8-2306-4877-a39a-e8e3c9f26afa | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
bf2f8cc9-9880-4009-9328-8f505f7c08af | checkpoint | 3.01.01 - Construction Pack
ea0cf074-93ad-5658-811d-31d8e1f26cdb | note | Acceptance/Conformance criteria - Submit a Construction Pack including a Methodology and JSEA to the Engineer before works
79dba8b7-c84d-56b1-b5ac-20118f3d3acd | note | Standard/Specification - Downer
fee11e90-9177-5863-a4c2-1b2f5c183976 | note | Verifying Document - Construction Pack
9a28e0a3-de6f-5593-a6ff-b9288ebc795a | note | Frequency - Submit 5 days prior to commencement of works
65bcf97f-9739-5277-bb5f-4517388905c7 | note | Verification Activity: Activity - H
ad044d3e-31d5-5b1b-a59b-eadecbcffd5a | note | Verification Activity: By - PE
d6d24726-e2f1-536b-85f4-1c116397f75c | note | Downer Signature - H
eab2ea00-c6fe-5e5a-897e-49d7708c432b | note | MSQA Signature -
5fe6947e-0f20-5533-8b37-382cb6aa603f | note | Engineer Rep Signature - R
61891922-2831-4c98-8ab7-392c008aac04 | signoff | AUTHORITY HOLDPOINT
43dce90f-f729-402e-bd1d-20e0eace5176 | checkpoint | 3.02.02 - Survey Setout
d82755bf-d0ab-598a-b8fc-49fbe93b1512 | note | Acceptance/Conformance criteria - Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed.
3ef93464-9994-5cc1-8289-c3fa9dd49339 | note | Standard/Specification - Downer
a9cbcb26-3fac-531e-85ba-9c66472a775c | note | Verifying Document - Survey Records
f7f1bb99-45c4-5151-8eb5-4ad28a8e17a1 | note | Frequency - Prior to Works
de058cb2-b941-521b-818c-b37308544514 | note | Verification Activity: Activity - H
738bd7e1-4ae2-57c3-bcc8-749e1b5cd425 | note | Verification Activity: By - SV
ce151afd-f16d-593b-b12b-b1a474e806a6 | note | Downer Signature - H
2d9c8233-664d-5905-bba1-5f976b88a138 | note | MSQA Signature -
e7481aa6-2adc-5d62-8acb-3976002ead1a | note | Engineer Rep Signature -
a0036637-1aa5-48a0-a949-b46ac54803e5 | signoff | AUTHORITY HOLDPOINT
43d23988-21fa-45dc-a4dc-2e19e158e4d9 | checkpoint | 3.01.02 - Service Location
65531b73-a03e-50be-b8dd-6b4717922506 | note | Acceptance/Conformance criteria - Complete the Excavation permit process to identify, locate and protect all services.
1103b056-8951-54ac-8b1d-3c908f6b5456 | note | Standard/Specification - Downer
80698099-b122-548e-8bef-a151aff9bfc9 | note | Verifying Document - Excavation Permit
6fc88e45-551d-5a07-a202-516cd70d924c | note | Frequency - Prior to Excavation
8e4f66e1-451d-5bd1-b499-648b6879ea74 | note | Verification Activity: Activity - H
05fdf411-2883-5391-b72b-a4d19d487a70 | note | Verification Activity: By - SE
c99b72e7-322d-5855-8a56-d451962f8c92 | note | Downer Signature - H
d68bb6ac-9062-5e98-bb15-64e38bd80406 | note | MSQA Signature -
8e43d9fa-7b3f-5c45-b827-b62a49f4491a | note | Engineer Rep Signature -
6d91cd6e-b1b0-43b4-a6c0-ccdfbe6c284d | signoff | AUTHORITY HOLDPOINT
aaf07747-d3b7-41b5-b99e-ec49e47734cd | checkpoint | 3.02.03 - Internal Permits
5fb21a87-b659-58a1-b8ab-600d735a31e3 | note | Acceptance/Conformance criteria - Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc.
e939a224-64f1-5d0f-98cd-23ffcf7dc84a | note | Standard/Specification - Downer
a28f663a-5176-5f18-b1d6-690d3c5fa4db | note | Verifying Document - Internal Permits
b708ae1c-8158-5de7-855e-f31d6e05eb19 | note | Frequency - Prior to Excavation
4febbe88-ed94-5933-ae40-11fb575d9a7d | note | Verification Activity: Activity - H
4f3cfc58-748d-5b74-a511-7d6da00da3b2 | note | Verification Activity: By - SE
48a39409-75c4-500f-be4a-babce943b467 | note | Downer Signature - H
7c32bf09-79e2-59d5-9c7d-17ed65a4eb81 | note | MSQA Signature -
359b47f8-4268-55e4-a041-26488068d7bf | note | Engineer Rep Signature -
faf6948f-b198-48bf-b437-7759db826082 | signoff | AUTHORITY HOLDPOINT
1458902b-b507-4681-96cb-f471cbf2f999 | checkpoint | 3.01.03 - External Permits
2564b722-9f59-50d6-80ab-0246f8ad88e1 | note | Acceptance/Conformance criteria - Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc.
1aa195cf-0f15-5999-bb5a-b0a870dc4c9c | note | Standard/Specification - Downer
bf0d7954-9392-5fdb-9ae3-836d8fe00b57 | note | Verifying Document - External Permits
e88473df-aa65-515e-8c33-e8a657471852 | note | Frequency - Prior to Excavation
932e237e-fc47-5355-b0db-3c4d643d4f41 | note | Verification Activity: Activity - H
d2e18e7e-a59a-59c5-8571-5ac0c657ec5d | note | Verification Activity: By - PE
aaec2c42-98d3-51df-972e-7ed14a36b7ae | note | Downer Signature - H
2b4523f2-6ad0-5fe4-b138-9ba8f2a19a1b | note | MSQA Signature -
9316e4d5-6dc2-5a4b-9baf-158ccd6fa42c | note | Engineer Rep Signature - R
1c725e2a-3f15-4f50-9ccd-09b1911ee20f | signoff | AUTHORITY HOLDPOINT
ce089177-b0d6-4e95-94f0-90d2d4b8c83f | checkpoint | 3.02.04 - Approved Construction Drawings
260e4154-f75d-5777-a2f4-afbc5e3cab08 | note | Acceptance/Conformance criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
f2b38240-d137-5f26-b15c-43fa0bdf71e9 | note | Standard/Specification - Downer
d616e74b-332c-5f9a-b362-8e568b6e1f13 | note | Verifying Document - IFC Drawings
ef2d6ffa-d73a-5576-a5f5-73109d5e11f7 | note | Frequency - Prior to works start
d67fa783-15b4-5545-9aea-d6d3fff5dfb8 | note | Verification Activity: Activity - H
a01d0dda-e0e1-57dd-ac7f-dba017ab0204 | note | Verification Activity: By - PE
f2c164dd-f262-573c-8fb1-7b9a6f0f870f | note | Downer Signature - H
b94d6615-1f7c-5536-8e41-7977200e63c2 | note | MSQA Signature -
5c90d41e-4ce5-59cc-ad26-1fd3f494c85c | note | Engineer Rep Signature -
9f4deb11-f127-47a5-ae84-b7a875653216 | signoff | AUTHORITY HOLDPOINT
07efec65-d0da-4de8-944d-27d49bb95888 | section | SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
68775303-c8ae-47ff-80c6-23bbbedd9936 | checkpoint | 4.01.01 - Material Properties
f217d482-e3d0-5d11-b389-07035805f005 | note | Acceptance/Conformance criteria - Filter Aggregate, pipes and filter fabric shall comply with TNZ F/2 for non‐wrapped drains and TNZ F/6 for fabric wrapped drains.
e8b2cbfb-c196-5db0-a309-f943f29fc09f | note | ○ Filter aggregates specified in TNZ F/5 shall not be used.
448eab9c-7811-58bb-8697-4d51adcdaeb0 | note | ○ Pipes supplied and installed as specified in drawings
cf5ad9a4-6230-598a-aae8-5dcf8f225035 | note | Standard/Specification - Aurecon Civil Spec Section 16.5 TNZ F/2, F/6 ATCoP
8245e6dd-28c8-5fb5-b0c6-efe627cbf0d0 | note | Verifying Document - Supplier Records
8cf2b99f-77f9-556a-bb3c-d3996051af7d | note | Frequency - Prior to use, Checked on Delivery
53b650be-60d2-525e-a02f-17b6c06776f8 | note | Verification Activity: Activity - H
e524b300-0223-52e6-9413-bd1366de9d0c | note | Verification Activity: By - PE
e4e99c51-567c-5bcd-8810-3a699fbe7273 | note | Downer Signature - H
c98c1704-48dc-55c4-91be-5c6cdf218b03 | note | MSQA Signature - R
465c07cd-3230-51bf-84b0-36efc5b76bcf | note | Engineer Rep Signature - R
6fb6ffb1-5832-4818-b154-0f9f954cb878 | signoff | AUTHORITY HOLDPOINT
0147825b-cf73-4cc3-9071-d34e1da82f0e | checkpoint | 4.01.02 - Drainage Aggregate
c37ae1e8-63bb-5164-aaa6-4790a80eb4e0 | note | Acceptance/Conformance criteria - Shall be NZTA F/2 or F/6
97a6cfe6-c814-5a9e-b90d-0868d1afaa81 | note | ○ Drainage Aggregate chip (20/7mm) DN1211-DOW-RFI - 0048
16e7b566-8d41-564d-b612-5e1889153f3b | note | Standard/Specification - Aurecon Civil Spec Section 16.6.3 RFI-0048
e7e81b7c-b863-59e9-a631-3d0e2230b944 | note | Verifying Document - MAR record
6d2489b1-8e5d-5a86-a5f9-01e8c70dbe25 | note | Frequency - Pior to Use, Delivery Dockets
1876e486-0509-5175-a578-5c7eef44ebc4 | note | Verification Activity: Activity - H
3686693d-3b99-518b-9da9-2392b3dd8b21 | note | Verification Activity: By - PE
6440567f-3f87-5ce9-a7b5-17d078b50d90 | note | Downer Signature - H
8e0ce1e1-99d6-5be1-886a-2de757866a3e | note | MSQA Signature - R
51a398f5-ad81-54e9-a865-cd9b343e3823 | note | Engineer Rep Signature -
a5239ccf-f7c9-4c5f-afa8-c6a16c446f84 | signoff | AUTHORITY HOLDPOINT
2e8ce2e7-d345-4ca4-80da-4d0abe07f341 | checkpoint | 4.01.03 - No-Fines Concrete
70bbe53f-1e27-59de-97d7-6c80658be1f0 | note | Acceptance/Conformance criteria - As per TfNSW 3222, for aggregate size distribution to be
9eeec034-90c1-50d8-8878-1947351783ec | note | ○ 26.5 mm @ 100 %
90b04c42-1082-5932-9eab-638ff8e8cb72 | note | ○ 19 mm @ 95 - 100%
9ee66dbd-9c60-5fdf-a9a1-20928bbcb1e7 | note | ○ 9.5 mm @ 0 - 5%
24c05f67-6061-5041-a971-808c245d704f | note | Standard/Specification - Aurecon Civil Spec Section 14,17.11.7
f8b24fde-8166-5b2d-948b-ad01f681a881 | note | Verifying Document - Supplier Records, Concrete Dockets
8560e117-c49f-5d42-83f7-aea2d50a92ea | note | Frequency - As required
6f796a00-50c9-5709-8dd4-5dd0c6eb7d2a | note | Verification Activity: Activity - H
d4a1fd63-f2f8-5bc2-b934-75b7eba918df | note | Verification Activity: By - PE
bb69ea44-cf6e-5860-954d-d17d19a11049 | note | Downer Signature - H
ed711539-b018-5be8-9c64-5c2020ffb89f | note | MSQA Signature - R
44ad8fda-5146-5015-aea5-413f53a39702 | note | Engineer Rep Signature -
3cab49b8-be66-4f7a-b7a8-8ea215b89cf1 | signoff | AUTHORITY HOLDPOINT
c64b3c04-f47e-4c4c-b533-f99019be953f | section | SECTION 5 – CONSTRUCTION ACTIVITY – DRAINAGE INSTALLATION
c8a0223c-06fc-40a6-9c68-eb348a1f94f6 | checkpoint | 5.01.01 - Subsoil trenching
c52fba46-b2f0-5b73-ab36-16f0c8292087 | note | Acceptance/Conformance criteria - Construct subsoil trenches as per TNZ F/2 or Approved 20/7 drainage chip, falling towards drainage outlet. Install Geotextile filter fabric at base of trench where specified.
192182b3-0a8a-571c-8dce-02393e265161 | note | ○ Drainage aggregate bedding installed at trench base; 75mm thick for Ø=75mm pipe and 100mm thick for Ø=100mm pipe.
c72e44cd-1678-5f63-995a-c9bb52e5ff45 | note | ○ Suvey Set-out position as per deign unless design clash changes required
bf02c448-ae31-5cdc-91ea-a6c9a88c24d3 | note | Standard/Specification - Aurecon Civil Spec Section 16.6 TNZ F/2 ATCoP
d799c23b-fb2f-5e80-a4ec-31a073e18e1b | note | Verifying Document - QA Checksheet
5f788dbb-5789-56f7-9f6a-279f5b61fffb | note | Frequency - Inspect on regular intervals
064e97e0-5db1-56f2-a1ef-b20c9bb6a63b | note | Verification Activity: Activity - I
382a253b-78da-57ef-92e2-115daa9fe88d | note | Verification Activity: By - SE
a4dad87a-3a6e-52bd-9935-82127d261ec2 | note | Downer Signature - I
36306535-6424-58ca-bb40-f4106b45b079 | note | MSQA Signature -
59b98526-810d-522f-b4c0-f6d6565ed6c1 | note | Engineer Rep Signature -
d5e89d4d-d0fc-4c0e-902a-b523dbec7f00 | checkpoint | 5.01.02 - Subsoil installation
06259d71-2a3b-50f2-acc4-e35d1ad42e79 | note | Acceptance/Conformance criteria - In absence of subsoil depths in drawings: Install subsoils at 600mm below FL forsealed roads and traffickable areas, and at 450mm for non‐trafficked areas.
50118ced-3526-56b3-b44c-62f4c4b42505 | note | ○ Subsoils laid straight, falling towards drainage outlet as per TNZ F/2 and drawing
0c870df0-8a7f-598b-9c09-cdb0346fbf61 | note | Standard/Specification - Aurecon Civil Spec Section 16.6 TNZ F/2 ATCoP
71938e2d-345b-5309-91fe-e70f43e48d95 | note | Verifying Document - QA Checksheet
789cec01-064d-5683-8ca2-44d9aa42f08c | note | Frequency - Inspect on regular intervals
76609860-3417-56f3-b184-491201af84ba | note | Verification Activity: Activity - W
821fbcd6-e5a3-5c6d-8fa0-f8eabc0eb832 | note | Verification Activity: By - SE
71fd24a7-c915-560e-921d-5b2a218d2712 | note | Downer Signature - W
0981c8c6-5547-5d55-a3dc-8bca9cee0239 | note | MSQA Signature - R
92741011-a481-5c21-933b-4acf7a3ecb7e | note | Engineer Rep Signature - I
d1789ef1-906e-4357-9f59-c9c912eab2f6 | checkpoint | 5.01.03 - Trench Dimensions
a4110df9-fadc-58ae-bdbf-0beb2fd5b157 | note | Acceptance/Conformance criteria - Excavate trench to lines, levels, width and gradients shown on drawings.
942b15a4-3cdd-525e-b263-44731e28d6d0 | note | ○ Trench of sufficient width to permit installation of all materials and fittings.
eae182bc-43e6-5b81-b873-b3c18f9411cb | note | ○ Pipes minimum 100mm from trench wall.
cef253fe-142b-5124-9139-dd9f20397883 | note | Standard/Specification - Aurecon Civil Spec Section 16.6.2
b37dfaf3-e181-599c-ab44-4e4ecce231bc | note | Verifying Document - QA Checksheet
eac61ef5-5985-534a-bcb7-ac8ffc3e5f38 | note | Frequency - Inspect on regular intervals
a96126d2-89cc-5d41-8972-de41f1fb961f | note | Verification Activity: Activity - W
46eada62-0fdf-5afe-b35d-c435e85002d3 | note | Verification Activity: By - SE
e0e437c2-7352-5653-846d-120af4c0fae8 | note | Downer Signature - W
ec500b82-59c5-5f7f-a125-892dda413c76 | note | MSQA Signature -
6e7a62e7-8922-5aa1-82e0-3b562239f09b | note | Engineer Rep Signature -
e0c4c158-4874-46ad-a1a5-866eecc6e2bb | checkpoint | 5.01.04 - Backfill Placement
2f370463-b8e6-5b2a-95d5-75df5d152ec0 | note | Acceptance/Conformance criteria - Backfill with 150mm + 150mm depth of drainage filter material above pipe, hand tamped
141bc838-9c82-51e3-823d-25c57cb9bb62 | note | ○ Backfill and plate compact remainder to FL as specified in drawing
fce31f72-e72a-559b-a1c1-9395ea3e2168 | note | Standard/Specification - Aurecon Civil Spec 18.6.3 TNZ F/2 ATCoP
db812c18-7f42-569a-8b5b-c42d12ed6921 | note | Verifying Document - QA Checksheet
80293f32-66e7-5a89-8f74-b9c4f1f97274 | note | Frequency - Inspect on regular intervals
eca36b70-d3e1-5747-86a9-0c09965c44bd | note | Verification Activity: Activity - I
91a87f5f-b150-5f64-b9c0-78661028c073 | note | Verification Activity: By - SE
f92dd20a-90f1-5b1c-b1b2-c02ec377800e | note | Downer Signature - I
46ad12e6-ef62-599e-8bfd-521b23025814 | note | MSQA Signature -
b8cbcea1-4d27-5e5f-a407-f8f27d720aff | note | Engineer Rep Signature -
0bea6f71-a4e3-4344-b68c-abedb287fa14 | checkpoint | 5.01.05 - Flow Test
fbf184e3-d68f-5d1a-9cf7-f89a950f6b61 | note | Acceptance/Conformance criteria - Visual inspection of water flow.
2c9efa6b-dd6d-52b7-8cd3-731bc0da5f88 | note | Standard/Specification - Visual Inspection
b6064f0c-2286-540a-88ff-475cfb06e4fd | note | Verifying Document - ITP Sign off
1af3e5a0-e321-5152-9c0f-d10fcfaebd4f | note | Frequency - Once per Zone
bb23e05e-9d7d-5dc6-93df-34b49f233562 | note | Verification Activity: Activity - H
a3769521-4fcd-5faa-aef8-e1071810b17d | note | Verification Activity: By - SE
4af178cc-ebe9-50ba-be8a-ba6f97a2030e | note | Downer Signature - H
163098c1-aef4-566f-a97d-27e43d2ca342 | note | MSQA Signature - R
9841047f-f245-5669-b2e9-b1c68fc76c88 | note | Engineer Rep Signature - R
700f57f0-1c69-417f-9929-fbdbf4bb77f4 | signoff | AUTHORITY HOLDPOINT
aad4628d-7150-40c8-af29-2a79c8fff27d | section | SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
f28e29d9-b47d-4905-b4cf-b5763391b55f | checkpoint | 6.01.01 - Construction Record Compilation
793e64cd-9d72-5d0b-be27-02911cf96080 | note | Acceptance/Conformance criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
b76f9868-1f5b-5941-8f89-0540f6cf3f4f | note | Standard/Specification - Downer
eaab2fbc-d8f3-5e6a-abbd-b05375023b0b | note | Verifying Document - Records
fe23fb8a-508f-536b-9bf6-4ef7c44aa0c2 | note | Frequency - Post construction
e81b4a56-ba76-5b3f-9384-b4678ebfbb3d | note | Verification Activity: Activity - H
86973c03-215d-5a40-91e5-3320542d0763 | note | Verification Activity: By - SE
13ef076a-de92-5eca-b089-d791cbf72283 | note | Downer Signature - H
204112a1-acd0-5189-ba1f-6ed8fc4305c1 | note | MSQA Signature - R
601d3edf-48e4-5d6d-a61e-87b74aebd230 | note | Engineer Rep Signature - H
742b9875-0f70-46ea-bcfe-2c9a7309d479 | signoff | AUTHORITY HOLDPOINT
2f0219ff-ac9f-464d-9d31-ce83bd045937 | checkpoint | 6.01.02 - Survey Records
3bfe2156-5c1f-5596-98c2-67393e6ef0f3 | note | Acceptance/Conformance criteria - Ensure all items have been surveyed and records are assembled for asbuilting. Asbuilts to include type, size, quantity, location and level of subsoil laid.
03087dc6-da2f-53ad-bf85-45f5f6387ca6 | note | Standard/Specification - Downer
34e5230a-0b0c-580f-a010-620165f44c9b | note | Verifying Document - Records
1d4ab298-7dd2-5ca9-8d64-6d315053e51c | note | Frequency - Post construction
8abee67d-3526-5a7e-806b-46001efb79ba | note | Verification Activity: Activity - H
67a720e7-872a-53b4-90c7-70f1d04dcd31 | note | Verification Activity: By - SV
de8af7dd-c030-59d3-a5b7-88a2b682be0d | note | Downer Signature - H
a58100e3-f9ab-5a73-9813-913ae000872c | note | MSQA Signature - R
56768ca6-ada6-525c-8b9b-c6646781130d | note | Engineer Rep Signature - H
07269b68-a976-43d9-a9f4-9f67f452dfec | signoff | AUTHORITY HOLDPOINT
91274242-fe22-4f94-a85f-98331bc9aaff | checkpoint | 6.01.03 - Redline Drawings
24a80682-0eaa-5fbc-9a71-a5e5df2c3475 | note | Acceptance/Conformance criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen. Relevant change correspondence to be included.
3aed348b-2bc2-5c22-8640-78bfd4203df5 | note | Standard/Specification - Downer
e6259c30-98f1-5b5b-b627-026e86f37f82 | note | Verifying Document - Redlines
d54eec1f-9c4d-579a-845e-8c411e1283f2 | note | Frequency - Post construction
058fdb4d-ed45-5aa1-8026-23eab1e5360e | note | Verification Activity: Activity - H
a6b3824a-c2f2-507e-a66a-a24022b3cad0 | note | Verification Activity: By - PE
ba099808-0310-5487-95f1-7e8fc5f5afef | note | Downer Signature - H
88270550-0beb-56f2-b0b2-4cb18a2fe6c7 | note | MSQA Signature - R
c0d5e5ae-7289-51a8-991c-fc5db187ad4b | note | Engineer Rep Signature - H
dc28da3e-daa3-4ae0-8a3e-a3f5480535a9 | signoff | AUTHORITY HOLDPOINT
9e3113eb-6498-4ad6-8d92-544f64700d9f | checkpoint | 6.01.04 - Defect, Snag and Punch List
974f498b-01e4-5495-ab4f-acd8a491405a | note | Acceptance/Conformance criteria - Update the project Defect, Snag and Punch List Register
a62763d0-1e2c-5f43-a689-e065a28c3aaf | note | Standard/Specification - Downer
36c748fc-fe8a-506d-bbb5-5929ea2827de | note | Verifying Document - Register
a85331e9-d7a1-5c08-983a-72f0d7e58cb8 | note | Frequency - Post construction
749e13ac-6248-5a71-a288-e1e50d92f7dd | note | Verification Activity: Activity - H
e1f9981a-2be3-5f9b-8dd5-c259a9a5fc6a | note | Verification Activity: By - PE
b96675fb-0e44-5f78-a2db-20e5de279a75 | note | Downer Signature - H
c568cb85-ca1d-562e-929c-d9d166118680 | note | MSQA Signature - R
b05e1978-b14b-558c-9d9c-a5bed62a0602 | note | Engineer Rep Signature - H
49d4df9f-0d16-4b82-add0-268a304b0d88 | signoff | AUTHORITY HOLDPOINT
46976617-06e1-4b36-bc05-d2a133d10f2a | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
74b485bd-52c1-511c-bfd1-e07b6e89b8f9 | textbox | Contractor's Rep Name:
c3d57432-d7a9-5e8a-af7d-6d158661e001 | textbox | Engineer's Rep. Name:
e6cd50d6-63fa-5510-8c6d-90fcafbb00d8 | date | Date:
2f3c8722-3fbb-4001-94e3-55b9d039ec91 | signoff | Add Signature
07dfc33f-a1d1-4509-a1ec-c6a6c75d06e1 | checklist | DN1211-008 ITP Pavement Quality Concrete (PQC) Rev 1 | itp | DN1211-008 ITP Pavement Quality Concrete (PQC)
5050301a-aa2b-43a4-8f3c-393b9be50075 | section | SECTION 3 - PRE CONTRUCTION (P&G/ESTABLISHMENT)
767c53e6-a4a8-4d9c-8cf7-21dd583df2d3 | checkpoint | 3.1 - Mix Design
0eb92f74-3169-5946-a34c-93fff624bc2e | note | Acceptance / Conformance Criteria - Details of the proposed mix which include the following: Materials sources, test certificates and specified results, 7-day and 28-day compressive and flexural strength results for proposed mixes.
0bc3d31e-3f94-579f-bb3f-de508a34b1e4 | note | ○ PQC mix design requirements below or as approved:
61248093-6ffa-5103-b212-0d3ee0e34425 | note | — Nominal aggregate size 19mm, GP Portland cement as per NZS 3122
92add9be-337b-5205-b472-8708c48cfa0a | note | — Target slump of 80mm +/‐20mm for truck mixes, 120mm +/‐30mm for pump mixes;
2c82b3a4-c478-5361-a441-510a14eae5e3 | note | — Target flexural strength of 5.0MPa at 28 days (min 4.8MPa) and 4.5Mpa at 7 days;
1895d0ec-908f-52de-9054-c12c542065df | note | — Entrained air content of 1.5‐2.0%;
cc2ce1f7-8b91-58b1-bf68-f5f83823535c | note | — Black oxide and McCallum red chip aggregate % content to be confirmed by landscape architect following preparation of sample panels);
73a83529-2f59-56ef-a698-e626dfaefd41 | note | — Aggregate source properties as per spec; target aggregate particle size distribution (PSD) as specified in Table 11‐1 and supplied within production tolerances in Table 11‐2
b7db7a6f-5788-50f5-98dd-3312acc70d53 | note | Standard / Specification - Aurecon Civil Spec; Section 10.3 NZS 3121, NZS 3122
289ec399-0e77-5d71-8ace-758e88b4cfac | note | Verifying Document - Mix Design Report Approval and Supplier QA (source properties)
50862dd9-5fac-5b7c-8161-fd2e26d9c620 | note | Frequency - Each Mix prior to Use
88ee5201-ba2f-5501-a2d8-4e7fff85735c | note | Verification Activity: Activity - H
63a15990-a428-5e10-96c6-36152137065b | note | Verification Activity: By - SE
ddf7ed80-eeb0-5599-9b46-e4e8f7b03334 | note | Engineer Rep Signature (Blank as req.) - W
2d983b97-04d0-5018-b2b0-3543e752fbac | note | MSQA (Blank as req.) - H
7d80449a-4444-428a-83b1-09ff37211772 | signoff | AUTHORITY HOLDPOINT
4adc1301-81a5-4628-bbbf-80c22bf358e5 | section | SECTION 4 - MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
01d608d6-7241-4166-92d0-23cee50d3962 | checkpoint | 4.1 - Exposed Aggregate Concrete
4d6198a2-ef56-5188-8c40-bc562db4325f | note | Acceptance / Conformance Criteria - Areas designated for exposed aggregate finish as per ITP Item 8.1 and subject to additional concrete mix design requirements:
a218cd9e-992b-54e9-aba6-f0fd4b2c6049 | note | — Crushed or pebble/round aggregates, gap graded (source properties as per NZS 3121).
4d661eb8-c522-51a7-b19d-06e740a68f56 | note | — Colour and target exposure depth to be confirmed following preparation of sample panels (0.6mm minimum texture depth)
43a5e969-4263-5c70-aebb-002071e950b2 | note | Standard / Specification - NZS 3114
6055a111-20b1-5e10-be91-db05fce3246f | note | Verifying Document - Each Mix prior to Use
bdb75beb-e05f-539f-a514-b784e2af0d0e | note | Frequency - Mix Design Report and Trial
81d75dd9-6c43-5e42-93a0-d0da045c7dd0 | note | Verification Activity: Activity - H
737a86ca-05c3-59ae-af98-23ea3cd55317 | note | Verification Activity: By - SE
f23b3973-d4c6-58a4-ac19-e417c14459bf | note | Engineer Rep Signature (Blank as req.) - W
f9934cb3-41be-50d4-8c9f-141f7288388c | note | MSQA (Blank as req.) - H
76abd495-9983-4a02-8726-c4bcd242938c | signoff | AUTHORITY HOLDPOINT
b95736b8-44ff-477c-befa-155538f3489f | checkpoint | 4.2 - Concrete Joint Materials
e25d7a42-be9c-573f-9e6b-1a7f0ad15b26 | note | Acceptance / Conformance Criteria - Dowel bars (rounds), mesh, reinforcing, formwork sections, plate edging, and crack inducers installed full length of slab as per drawings.
5edb6aea-4915-59ff-8c57-0966bb3cd2e7 | note | ○ Joint fillers and sealants supplied as per drawing. Joint seal with Dow Corning 888 silicone joint sealant (grey) or equivalent approved. Test for surface adhesion as part of construction trial.
5981f9cd-035f-5b2b-abca-417709058d55 | note | ○ Sealant colour to match colour of jointing mortar
6f75e70e-d26f-519c-b09b-d81afe22a236 | note | Standard / Specification - Aurecon Civil Spec; Section 10.3 AS/NZS 4671
365801a9-460a-54a1-881e-2909266c94a9 | note | Verifying Document - Initial products / alternatives to be proposed
80c36d93-fc42-5023-9903-f7b3304e50d8 | note | Frequency - Mill certs and material supply records
ef8d9a54-9d89-57fb-8b5a-5aacd0b904da | note | Verification Activity: Activity - W
fee1d988-de27-5150-9b96-d3716ca96e7b | note | Verification Activity: By - SE
ee87b9e4-c623-5975-a341-80bfe24c5319 | note | MSQA (Blank as req.) - I
0fab5218-a618-4700-bef8-dd04a3207f48 | checkpoint | 4.3 - Construction Trial
28db4b24-f995-5723-a95e-5756cd3e2768 | note | Acceptance / Conformance Criteria - Construction trial of at least 3No. adjacent slabs prior to main slab construction. QA checks incorporated in Pre Pour and Post Pour Inspection submitted for Engineer's Approval of the construction quality; placing, compaction and finishing
c99f9697-952f-54bf-b90b-7c33af118ef2 | note | Standard / Specification - Aurecon Civil Spec; Section 10.6.3
85b9e25d-8e2b-5ff6-8c33-c7d30ece8b97 | note | Verifying Document - Three adjacent slabs, prior to commencement
179972d6-cdd2-5f10-abc9-73cf1e4b64ba | note | Frequency - QA Sheet, Photos
32af2f74-e2d3-5900-af99-8170a53df55e | note | Verification Activity: Activity - H
ae978a02-6282-5c52-80de-87a351cc8308 | note | Verification Activity: By - SE
58dbd000-a47a-5b22-bbcc-ccb5563a103c | note | Engineer Rep Signature (Blank as req.) - H
6117b6c4-d76d-576d-8cb3-40dd948aea60 | note | MSQA (Blank as req.) - H
d6963372-c768-4a64-931c-b940eb5eaa95 | signoff | AUTHORITY HOLDPOINT
6eb80252-0220-42b4-8d89-6142120eff25 | checkpoint | 4.4 - Pre‐pour inspection
35524765-a8b9-5fb2-a5af-1df2a908ba82 | note | Acceptance / Conformance Criteria - Engineer to be notified 24 hours prior pour, and pre pour inspection records to be readily available for inspection upon request.
d736f9fc-0c03-5052-9bd1-f44b9cdee370 | note | Standard / Specification - Civil Spec Section 10.4.1
a32ff1d5-fcf0-5982-a931-c48f36ff9048 | note | Verifying Document - Pre Pour Inspection for each section
5b5a64bb-f827-5238-9998-9e80b5fe0a0a | note | Verification Activity: Activity - H
d4f509db-0304-5ce6-a5bb-117a936b4e48 | note | Verification Activity: By - SE
ef9fea80-b99b-5fc2-8e85-3830e80dc6dc | note | Engineer Rep Signature (Blank as req.) - W
a9f8ea0f-68e2-54a7-bb3b-8528be0d97c4 | note | MSQA (Blank as req.) - I
0fe5cb47-c24b-4fe7-bb64-a4da828d9144 | signoff | AUTHORITY HOLDPOINT
6714c6c7-a46e-4848-81dc-db352d20c76d | section | SECTION 5 - CONSTRUCTION ACTIVITY
0b47ba1a-fe4a-4437-a040-f27eeed8323d | checkpoint | Subgrade preparation
91326c99-23e3-51f6-ae77-2e4400efeb1b | note | Acceptance / Conformance Criteria - Subgrade to be prepared as per ITP-003
c250c608-87ed-5326-a3c4-4b1f06f60e84 | note | ○ Subgrade to be +0/-30mm
8b62c3a3-4b50-59d6-b60a-6460f16e1adf | note | ○ CIV Clegg ≥ 10 CIV
3b7afcda-56d0-529c-ba4e-13443d2dfef8 | note | ○ All utility conduits to be lowered to below Subgrade level unless written authorisation from the Engineer received.
7b2e2653-204f-5bbf-9931-b23f066161b5 | note | ○ Proof roll to be undertaken with a Fully loaded 6 wheeler truck (10 tonnes) to check for any visible deflection. Where deflection is noted the Engineer is to be notified.
23438097-b661-5827-8311-1814e0e6b65c | note | Standard / Specification - Aurecon Civil Spec 6.1
0fc78dfb-0962-5291-b1ae-f8c6a4a81c9f | note | Verifying Document - Clegg dipsheet and visual onsite inspection by Aurecon Engineer
6b9ad27b-b936-525f-b673-bbf75086cdd8 | note | Frequency - 1 Clegg per 10m and Site observation pass by Aurecon engineer
4d3c9f61-3796-53aa-a75a-a1218601c68b | note | Verification Activity: Activity - H
31c6599c-7745-5c78-a383-6de8fe0e946d | note | Verification Activity: By - SE
1b0ceabc-a83c-50b9-8862-b17751f189e0 | note | Engineer Rep Signature (Blank as req.) - R
1ade5b3a-e6f2-519d-bcc9-824e939c9c02 | note | MSQA (Blank as req.) - W
3a06be08-d779-4785-a5d7-d9d5903d5bf2 | signoff | AUTHORITY HOLDPOINT
d8dca54e-1a66-42ba-b27a-30ba09d552ab | checkpoint | Lean Mix appliciation
8bfb9ebb-6e1a-550d-8873-14a71da67ac1 | note | Acceptance / Conformance Criteria - Lean mix to have Minimum 28 day crompressive strength of 5Mpa and not greater than 10Mpa
0d00a96f-a17e-589f-9922-f7fd11508dc7 | note | ○ Lean mix to be not to be placed in temperatures exceeding 30 degrees in the shade.
e45fd777-6663-530d-b0f7-fc9a0f937188 | note | ○ Lean mix layer to have micro cracking induced through means of rolling prior to placement of PQC layer. As per DN1211-Aurecon-RFI-R-0102
9d2494f3-ba62-5375-a04a-9a681ddfad56 | note | ○ 200 Micro thick Polythene sheeting to be placed overlapping beneath concrete slabs
20a7e465-9553-5dd5-b61a-74f21aca7f2b | note | Standard / Specification - Aurecon Civil Spec 10.3
f96b392e-297e-5029-a70d-e4a44f07bf55 | note | Verifying Document - Photos of Polythene sheeting
606617a7-b5b6-528c-a4fe-4917a9eadf8c | note | Frequency - Once during
df2750e3-bce4-557b-a214-7b8a9da36b61 | note | Verification Activity: Activity - H
f82d4b5c-8f0c-59ce-85bc-ca3a6a4d7f53 | note | Verification Activity: By - SE
ee2e7ba4-76e3-57ad-8a72-33c8429cae7f | note | Engineer Rep Signature (Blank as req.) - R
9e93416b-15a9-5fff-a721-f8b590feb7dc | note | MSQA (Blank as req.) - W
f6f89a66-430d-4032-9fa1-847ebf903ad9 | signoff | AUTHORITY HOLDPOINT
6b5cfbcb-2181-4407-abc0-f7ad2c9619fc | checkpoint | 5.1 - Concrete Placement
813c1708-502c-5fe6-aafe-e79a15259d99 | note | Acceptance / Conformance Criteria - Maximum temperature of 30°C when placed
1bf5fe32-4c9a-5a5f-ae0a-070d6eed3645 | note | Survey pins set for level control and stringline checked prior to pour.
bca4e1f1-7a8d-56ba-97b7-52a4653334a7 | note | Concrete to vibrated in‐situ to ensure good compaction, especially at joints. Concrete depth to be no less than design thickness and FL within tolerance of +/‐5mm Post‐compaction and screeding; Light broom finished at right angles to direction of traffic. Exposed aggregate finish as specified on architectural drawings (refer spec)
f760f74c-bc7f-50ba-ae35-d3065623b2eb | note | Standard / Specification - Aurecon Civil Spec Section 10.5.3
bb8f7ac5-5459-5247-a6ad-16c0b2c25b01 | note | Verifying Document - Stringline checks/Survey before and Post pour. On site review and QA sheet
45fa7bee-238c-5db6-9879-adcfb5c2f514 | note | Frequency - Before and During each pour lot
45df98a0-f1e4-5833-b67c-16783e0c4335 | note | Verification Activity: Activity - W
ba5985a6-735c-5621-9112-3c6e0e76d096 | note | Verification Activity: By - SV
034659a5-bf23-5170-b9e4-3a45a3626094 | note | MSQA (Blank as req.) - I
0c27da16-bace-47b0-920d-97c723226fe9 | checkpoint | 5.2 - Flexural Strength
49592f06-be64-5c6a-9ded-f075f693a570 | note | Acceptance / Conformance Criteria - The flexural strength of concrete produced shall be measured by testing 4No. flexural beams; 2No. at 7 days and 2No. 28 days.
42af1834-705f-52b4-a690-ae72f7016499 | note | ○ Testing results submitted to Engineer which to confirm minimum 4.8MPa achieved. Testing to be complete by IANZ lab.
8a3d908b-9911-530e-88b7-0d35be4ef28a | note | Standard / Specification - Aurecon Civil Spec; Section 10.5.8
b3068997-5cbd-5dff-a1d9-ceef102be5a0 | note | Verifying Document - QA Sheet, Truck dockets, IANZ Lab Reports
d664ccef-5d44-5a50-99a3-6f10d24baf2a | note | Frequency - Every 50m3 / daily
e029631f-82b2-5acf-9c96-849da1d9c025 | note | Verification Activity: Activity - W
b9a478e7-461e-5550-bc09-b3e9d86ed5d3 | note | Verification Activity: By - SE
d074585a-014d-50b3-a8c0-e79588137ce3 | note | Engineer Rep Signature (Blank as req.) - R
2f77e650-cef1-5c34-a4da-d15b8eaf933b | note | MSQA (Blank as req.) - R
341253a1-b317-4f91-826e-7225a6518ee5 | section | SECTION 6 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
16113e2d-3ec5-4320-a22a-ed3ee921f1ec | checkpoint | 6.1 - Concrete density testing
5645c6c9-c6f2-5137-b1e8-f98402a4e936 | note | Acceptance / Conformance Criteria - Acceptance of pavement with respect to density shall be based upon the results of density tests carried out on flexural test beams, and on 6 cores with 28 days of age cut from a pavement lot by the Contractor in accordance with AS1012.12.1. If the ratio of the core density to the average density of the flexural test beams exceeds 98.5%, then the lot shall be deemed to comply with density requirements. If the ratio of the core density to the average density of the flexural test beams is less than 97.0%, then the lot shall be deemed to be nonconforming with respect to density requirements. Testing to be complete by IANZ lab.
01020324-12cb-5536-8d41-be21d95c94c5 | note | Standard / Specification - Aurecon Civil Spec; Section 10.6.5
faae5975-af6d-5be7-9618-16cda660138e | note | Verifying Document - 6No. Cores from 1 lot at locations approved by the Engineer
ab68f00d-47cb-5da4-a9cf-3166bba88407 | note | Frequency - QA Sheet, IANZ Lab Reports
cd0034a3-e6ea-5ecd-943e-3f71e71fa28a | note | Verification Activity: Activity - W
04ac4f59-40de-52f8-af92-ac1215e75c2e | note | Verification Activity: By - PE
9e4ef93f-4f1e-58a4-b1bc-f7e8a2f036f6 | note | Engineer Rep Signature (Blank as req.) - R
5f78d8cf-022f-563d-b41c-b8407875a0b7 | note | MSQA (Blank as req.) - R
dab6c37c-256c-43c5-a1a3-8a6feecf69ff | checkpoint | 6.2 - Finish Tolerances
9d600d56-2f44-5896-bccd-98e6ba6de64f | note | Acceptance / Conformance Criteria - Concrete curing for at least 5 days. Form removal after at least 12 hours.
3001e57c-af2d-583c-8cce-3a123185e191 | note | ○ Post Pour Inspection to be submitted for Engineer's acknowledgement showing finished concrete is within tolerances (Surface Level +/‐5mm), and construction joints have been inspected prior to paving
957c221c-ba25-5d9f-8db4-9f43fc5bb0d2 | note | ○ Surface smoothness checked with 3.0m straight edge, no deviation greater than 3mm (5mm for LABI) to ensure no areas will pond water. Sawcut contraction joints 1/4 to 1/3 depth of slab and seal as per drawings (every 10m or as specified). Apply compressible joint filler at exposed faces as required for subsequent pours
b5e01b4c-c59b-5adc-abef-4a9bf1ae918b | note | Standard / Specification - Aurecon Civil Spec; Section 10.5.8
22443bcf-ddf7-579a-8412-b8f10f514167 | note | Verifying Document - Post Pour Inspection for each section, Survey corner of each slab and along crown at 300mm spacing
ed3ebff1-ec31-5150-83ac-40a247fbd74c | note | Frequency - As‐Built final surface, QA Sheet
c0823103-d771-5cc7-ae91-a90e6bdf7d41 | note | Verification Activity: Activity - H
481a5654-eadd-54b5-a83e-67aee170832f | note | Verification Activity: By - SV
41deb799-9ecb-5f4d-accb-e6a945cacad9 | note | Engineer Rep Signature (Blank as req.) - W
8167f7a0-4b80-5c24-b5a8-330f47c553ca | note | MSQA (Blank as req.) - H
3c8e7f1b-c548-40d3-9edf-2c3136c869a8 | signoff | AUTHORITY HOLDPOINT
4085a92a-8b83-4f5c-8d13-b448579b4bba | checkpoint | 6.3 - Architectural Finishing and Sealing
822f11a6-869d-5d68-a1ee-4c54cd5e7fa3 | note | Acceptance / Conformance Criteria - Light acid wash exposed concrete pavement surfaces with muriatic acid to remove stains and prep surface for sealing. Opportunity for architect/Engineers Rep to review clean surface prior to final sealing. Concrete pavements to be sealed with "MIS Stone Age Wetlook penetrating sealer", applied at per manufacturer's instructions
2b276526-cb8a-5e41-9231-ef6a2d100618 | note | Standard / Specification - Aurecon Civil Spec; Section 10.5.5,10.5.6
9298af91-f7e5-57b4-a831-501bb4c92816 | note | Verifying Document - Prior to final sealing
9d84e1cb-773c-53c8-9550-ec2287707934 | note | Frequency - Visual Check
81f5e72b-0d07-55b8-ac6b-8fd102c7e6dd | note | Verification Activity: Activity - W
6e796727-80c1-5d1d-8629-f6e653dde422 | note | Verification Activity: By - SE
2014e21c-8302-545e-91f0-9513cbb46270 | note | Engineer Rep Signature (Blank as req.) - I
712cbfa7-abf6-5c25-8aa7-3789509cc23f | note | MSQA (Blank as req.) - I
0ef4c03b-c28e-4e4e-ab61-35748059edbf | checkpoint | 6.4 - Survey Record
b8bc222f-8bb1-5ceb-8514-136c1fa1565b | note | Acceptance / Conformance Criteria - Installation of works under contract completed compliant in accordance with all relevant regulations, COP and standards
2e533d50-a82b-5b86-adc7-2becfb46bd46 | note | Standard / Specification - Design Specification / Downer
8073fdcf-1d10-542a-9526-2af85ec4b099 | note | Verifying Document - QA Checksheet, Redlines
8a99ac52-4021-5acc-9761-409a18ea0829 | note | Frequency - Post Construction
90702751-8bf4-54b9-a797-bb5c0bddc915 | note | Verification Activity: Activity - H
4af6f660-ee68-5202-bf4a-b3424bbff812 | note | Verification Activity: By - ENG
90bf9b09-b3e0-5a8c-b9e6-c838d31db08f | note | Engineer Rep Signature (Blank as req.) - H
3ed557c3-3193-5a70-9054-68f47b297959 | note | MSQA (Blank as req.) - R
8f92146e-2712-4e49-8550-cdd02264841f | signoff | AUTHORITY HOLDPOINT
b6d665c3-8745-4dd2-a929-04de13846f97 | checkpoint | 6.5 - Redline Drawings
12da008a-b65a-5569-816b-11e659a9d15c | note | Acceptance / Conformance Criteria - Ensure all items have been installed create a Redline Drawings for Asbuilt creation noting all changes with RFI numbers and departures in red pen
4bd7536a-09bd-548a-8834-0756baea5ec8 | note | Standard / Specification - Downer
f151ec1c-232d-552d-a92f-40ecb766ed27 | note | Verifying Document - Redlines
d1557d6e-45a2-597d-9f80-e6341ca94524 | note | Frequency - Post Construction
0e2547fd-5ce2-5158-af54-e8122f1473b6 | note | Verification Activity: Activity - H
1cd3a78a-9f7c-5a76-9726-f62ffcd4593d | note | Verification Activity: By - ENG
c507e408-de2b-59b2-9289-a9ae95be713c | note | Engineer Rep Signature (Blank as req.) - H
e8d5104d-6c17-5fe9-85c5-4d35599c1b5c | note | MSQA (Blank as req.) - R
0632df61-01f4-4462-a858-10d0fcf47271 | signoff | AUTHORITY HOLDPOINT
faf61e32-3780-4869-8000-8d777ee597eb | checkpoint | 6.6 - Defect, Snag and Punch List
719093ff-1bb6-5079-a1a6-3bd7ca64da98 | note | Acceptance / Conformance Criteria - Update the project defects, snag and punch list register
d3e5b5d3-3dcb-5426-aa4f-1d92cc765a31 | note | Standard / Specification - Downer
7e96b5f6-a15f-54dc-ae97-76744576fc83 | note | Verifying Document - Redlines
d9d8ddb2-3338-5877-9c54-22000a733580 | note | Frequency - Post Construction
3796302a-9ac2-572e-846a-04c6fc89c5f1 | note | Verification Activity: Activity - H
7120dcff-8b13-5715-b522-384a70c68844 | note | Verification Activity: By - ENG
e9540ac7-9fee-5f56-9fd2-399a3e356f66 | note | Engineer Rep Signature (Blank as req.) - H
1865e5bd-3170-50d9-b090-f728fcfe33a4 | note | MSQA (Blank as req.) - R
a4dd5cb8-b405-4c1d-916e-e7376e2a9fa7 | signoff | AUTHORITY HOLDPOINT
3944fffa-0d31-4933-b070-398df33de7f5 | section | SECTION 7 - SIGN OFF
92df2819-3b90-487e-9dbb-da66d1b6de91 | checkpoint | SIGN OFF
6f71fcab-3998-58e2-8d5c-bb0260c3d74e | button | Customer Release Granted: | Yes,No
d88e1fae-0df1-5435-9768-cf4497be4a54 | textbox | Acceptance/Conformance criteria - Certificate Number:
af935f06-5372-48b6-8f02-1d18f770eccd | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
d3b4e613-b9d1-52f5-8577-1aeddacbd9df | textbox | Contractor's Rep Name:
6dd63286-1fe5-57b8-966f-059f4a3c2e16 | textbox | Engineer's Rep. Name:
ff7807f0-82f3-5959-b58a-e2b2a5975fa9 | date | Date:
729bda6e-cfdc-4fc9-86cf-e56b6904b5da | signoff | Add Signature
773654b8-ccd0-4622-b37b-bef72a23ace8 | checklist | DN1211-010 ITP Concrete for Minor Structures and Incidental Works Rev 0 | itp | DN1211-010 ITP Concrete for Minor Structures and Incidental Works Rev 0
622b2438-a268-4028-8b80-e25d57bb7b7a | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
892256e5-635e-4ba9-8b12-79ef7e07649e | checkpoint | 3.01.01 - Construction Pack
4a8023c5-7efb-5322-899d-40ffefd8f89c | note | Acceptance/Conformance criteria - Submit a Construction Pack including a Methodology and JSEA to the Engineer before works
016c94ef-6848-57de-9612-ac4cfc228a06 | note | Standard/Specification - Downer
b769fa44-d0e7-5e86-8e75-9bc6b50235de | note | Verifying Document - Construction Pack
08ddacc5-f8f6-56b4-bc23-e6ecf3d5ab79 | note | Frequency - Submit 5 days prior to commencement of works
dd893bd7-2003-5ab8-851a-962fee109d27 | note | Verification Activity: Activity - H
01136fb3-300c-5941-9463-ab9f70533979 | note | Verification Activity: By - PE
16ecc41b-6104-5588-8061-35d7a41d31fb | note | MSQA - R
1f78f9a1-4dd8-498a-b1b4-4f4fdbebb367 | checkpoint | 3.02.02 - Survey Setout
f07b6764-1290-55cd-b897-8780b845f8a7 | note | Acceptance/Conformance criteria - Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed.
7eeed186-dc5a-5519-8fdc-dbcae135231d | note | Standard/Specification - Downer
df08e0e8-efac-5ad9-9eb2-3cee9cfdb2f5 | note | Verifying Document - Survey Records
00d61209-73db-564a-9ea6-a0e3ec87390e | note | Frequency - Prior to Works
aec87e12-da4a-50e4-bddf-00d2014d1562 | note | Verification Activity: Activity - H
5c7d3bd4-acc4-5041-9e9d-69fc25ad920d | note | Verification Activity: By - SV
8fb4ba75-8093-411f-896a-f5f4795205c1 | checkpoint | 3.01.02 - Service Location
e1531bf5-a884-53f8-92bc-e440c3465945 | note | Acceptance/Conformance criteria - Complete the Excavation permit process to identify, locate and protect all services.
d3281e11-9d4e-54b9-bd57-f41526e2e7e8 | note | Standard/Specification - Downer
7b288ba4-b8a7-5850-8d6b-980bbfb3d7bc | note | Verifying Document - Excavation Permit
54b79b4c-41fc-5827-8119-bd242a297d43 | note | Frequency - Prior to Excavation
fddf8601-ff7c-50b3-84f5-a17570ba2219 | note | Verification Activity: Activity - H
45d1f44e-5dba-5cd6-a71d-14ce4dde8eff | note | Verification Activity: By - SE
3a77263c-bac2-487a-825b-9f677f0b50d0 | checkpoint | 3.02.03 - Internal Permits
5a57005e-1559-53ab-833a-bbb107de5c9d | note | Acceptance/Conformance criteria - Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc.
85444a20-f331-5a00-b4ce-d862c4d22011 | note | Standard/Specification - Downer
14cac2f7-d153-5022-b8dc-9bc3a2b68f86 | note | Verifying Document - Internal Permits
bb8384cf-c36a-55b8-876c-edcabbabe181 | note | Frequency - Prior to Excavation
91083ccf-e70c-50c3-a14e-a41f512572ff | note | Verification Activity: Activity - H
a4fe0e9a-190e-5608-8d79-91ba7c7d7961 | note | Verification Activity: By - SE
f26fbc0b-809f-4260-8c2e-a8813fa10628 | checkpoint | 3.01.03 - External Permits
0773d4f6-1944-531b-a009-10a577705036 | note | Acceptance/Conformance criteria - Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc.
2101e6b3-b346-570c-8e98-afa38fc531b4 | note | Standard/Specification - Downer
9412a2cd-99fa-577e-abeb-c7dc118495fd | note | Verifying Document - External Permits
cdfa5487-4abd-5996-9fc3-1b9089f2d0de | note | Frequency - Prior to Excavation
3b509c5d-5679-56f7-af14-6f04c9ec23f3 | note | Verification Activity: Activity - H
24b7528c-9e51-5ab5-ac7d-055f1f279e7a | note | Verification Activity: By - PE
52c50d47-9186-5d5f-a154-efdaf3a822dd | note | MSQA - R
1ac81670-3c84-4137-ad20-c4cde6ca3f05 | checkpoint | 3.02.04 - Approved Construction Drawings
ce060d30-a432-5d71-8617-f1f6871e24b5 | note | Acceptance/Conformance criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
7bba1412-4185-5c6b-b775-1d00d0970ffb | note | Standard/Specification - Downer
9e74153f-628c-5c49-92eb-b8c789ba94e0 | note | Verifying Document - IFC Drawings
33b0854d-94cf-5f55-84cb-8de71621a009 | note | Frequency - Prior to works start
00bb9a9c-ebed-5026-a4f8-423c7e857bdd | note | Verification Activity: Activity - H
b111b76e-577a-5001-aea9-94a5b4bfba04 | note | Verification Activity: By - PE
44b2ec36-6e68-463c-8cd4-ff7f24786a75 | section | SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
e65e08b8-801f-4aae-bd04-4c4be996eff5 | checkpoint | 4.01.01 - Mix Design
6f29ddf7-5f7c-5810-8490-0c505fa5fd45 | note | Acceptance/Conformance criteria - Typical structures ‐Confirm supply of 'high grade' 20MPaconcrete; 19mm max aggregate size.
b68c85c3-ab23-5c43-a0b6-94b6b824ec79 | note | General site concrete
73d7cc22-4e58-5242-a4bf-ee1950718859 | note | ○ 10MPa Where specified ondrawings, use marine grade concrete
6f256e90-6bfe-5a33-8c6e-3c9f167f8f47 | note | ○ 30MPa The Contractor shallensure that the readymix supplier can provide mix designinformation andstrength testingrecords on request.
bf23ff68-2109-5982-82c9-a8c63f03ed1f | note | Standard/Specification - Aurecon Civil Spec Section 14.6
4d998f4e-ad4d-57b7-ba01-a78baefaf788 | note | Verifying Document - Mix Design Report Approval
bd64bc60-5ca8-598a-a290-17082da7b114 | note | Frequency - Upon Request / prior to Use
c700dcda-9da7-598b-8820-5728603c6cc6 | note | Verification Activity: Activity - H
6aca4692-92ec-50ff-ba89-a0adb1f5b131 | note | Verification Activity: By - PE
145f82ea-a1e2-5fbf-a32b-9d6c0ec86de1 | note | Engineer Rep Signature - R
4ad54ec5-a519-5ca8-a04d-bb87c962846d | note | MSQA - R
bc77ac5f-cbc2-45f4-a4c2-d71e605d78dc | checkpoint | 4.01.02 - Motar
e316f605-d1e4-5bd3-9e6b-b1da94f3504a | note | Acceptance/Conformance criteria - Consisting of two parts fine, sharp, well graded sand to one part dry cementMix by hand or mixer in small qunatities,use within 30 minutes
03a22fa1-af97-5985-8ee5-fcf5cc4d7727 | note | Standard/Specification - Aurecon Civil Spec Section 14.6.5
9e50c1cd-7459-5567-a8b4-092bdc767b73 | note | Verifying Document - In process check
513eb805-1e48-5b33-82bd-ab5948a19874 | note | Frequency - Prior to each pour
ce379b64-9ca3-5a9c-b845-2a8ef6850052 | note | Verification Activity: Activity - I
15725fb7-f315-5d67-b454-37af919b4b1f | note | Verification Activity: By - PE
0a7a52ce-c2ff-42be-91d5-7dfec78dae58 | checkpoint | 4.01.03 - Reinforcement
5754e492-6d17-56d8-8273-4160dc988509 | note | Acceptance/Conformance criteria - Reinforcement andembedded items cut, bent (cold) andaccurately placed asshown on design drawings. At least30mm cover to all reinforcing +5mm/‐0mmBar spacing as per drawings +/‐ 10mmBend locations as perdrawings +/‐5mm
d90ef18e-01b1-5578-8f45-cbbc0bcd371d | note | Standard/Specification - Aurecon Civil Spec Section 14.6.7, AS/NZS 4671
bcefc48d-4878-56c7-9c85-a03cf3fec629 | note | Verifying Document - In process check
015fb55e-b05a-5b0e-aa14-86df900ee31a | note | Frequency - Prior to each pour
47079d23-4450-503e-af8b-ce8fb7a79c22 | note | Verification Activity: Activity - I
8c360f37-9514-519c-9b09-dfeb789d8a72 | note | Verification Activity: By - PE
ef8aaf48-59f2-552f-b692-99bdb6cdb223 | note | Engineer Rep Signature - R
7fec4fe9-fa9b-4a3f-9ecb-e42d3a309097 | section | SECTION 5 – CONSTRUCTION ACTIVITY – CONCRETE INSTALLATION
9f2901f2-c9c8-49b1-80fd-fccc8d1b55db | checkpoint | 5.01.01 - Pre Pour Inspection Concrete Placement
be0be8fc-c113-5565-8622-4eb77110c468 | note | Acceptance/Conformance criteria - Notify Engineer for inspection of formwork 24 hours prior to pour forinspection
a4ca186f-f821-59ce-9027-8af30a2437b4 | note | Verifying Document - QA Sheet
c7667a4f-9e60-55e8-906e-28fd28b83c2a | note | Frequency - Prior to each pour
434d97fc-9998-5676-b3c0-b7548eb7a5af | note | Verification Activity: Activity - H
2b39dbcb-5416-599c-8bf6-a714c4fd07f0 | note | Verification Activity: By - SE
9e0558b3-6811-5084-ab94-5b03befea03f | note | Engineer Rep Signature - I
f0ce640d-14b4-5ced-80e0-9d2ffa79a482 | note | MSQA - I
c715e96e-1ce4-458a-93c2-fe322c35139d | checkpoint | 5.01.02 - Pour Plan
b7764a51-86dd-5f07-984b-a7b72d9fc767 | note | Acceptance/Conformance criteria - Place concrete and construction joints as per design drawings Exposed surfaces: F4 formed finish (or F5 if specified), U2 screeded finish Slabs: U3 trowel finish for internal slabs, U5 textured forexternal slabs
13adc547-4bc5-5a97-813a-bc1e22250fbe | note | ○ Delivery dockets dated and showing the concrete supplier and design strength shall be collected and held for every pour. Record location and date of each pour
13ae81e8-aaaa-5737-9665-97074ab44b46 | note | Standard/Specification - NZS 3124
983fda1a-e3bf-5445-8c5f-dbb53d2142ca | note | Verifying Document - QA Sheet Delivery Dockets
fe20b649-0ffc-5357-8633-f7647e725893 | note | Frequency - For Each Pour
84654cdb-d6f7-511b-ac81-6012ef18bec0 | note | Verification Activity: Activity - W
59b62bd1-e9be-5d65-9687-77d36cf8a9c9 | note | Verification Activity: By - SE
44fd9742-845b-5112-b82a-59544d714ba1 | note | Engineer Rep Signature - R
43db9f80-73e3-54dc-bc65-c04a36c4f544 | note | MSQA - R
d28432ed-f860-400c-84f8-47449c53ed92 | checkpoint | 5.01.03 - Testing
ce373514-50b6-5d91-b1a0-7225cf3c6df3 | note | Acceptance/Conformance criteria - Slump test during pour to check workability of concrete or as directed by Engineer 3 cylinder tests taken for each pour. Slump target as per mix design 120 mm when measured at the point of delivery to site.
6e2aabf0-df1a-56ec-819e-07c7dbe5a6b1 | note | Standard/Specification - Aurecon Civil Spec; Section 14.7.12, NZS 3112
f1bab556-6f74-5d36-8f2a-b1f8b05b001c | note | Verifying Document - QA Sheet, UCS Test Report
7b9ed90d-6c1a-57ba-80ed-8b421cacb0f2 | note | Frequency - Each pour / every 75m3 (one sample for pours less than 75m3)
4c9c7f76-1193-503f-8589-6685ec24c0be | note | Verification Activity: Activity - H
224d1046-f2a3-5acf-a5fd-32b425f802e4 | note | Verification Activity: By - SE
9c30573f-8bad-5f48-831d-fd366c50a6e0 | note | Downer Signature - H
10627c03-b062-5f27-9193-d72666cd85ba | note | Engineer Rep Signature - R
689daee3-0199-52a6-a1d6-b93a87e60d63 | note | MSQA - R
2b90febc-ea53-4836-b1a1-71f249ffa509 | signoff | AUTHORITY HOLDPOINT
e93acb74-d2df-40a7-aa48-a426116ec26d | checkpoint | 5.01.04 - Independent Testing
0c64d66e-652e-5191-92f3-baf9ee9cd48f | note | Acceptance/Conformance criteria - The Engineer's Rep may request site samples/cores for independent testing of fresh or cured concrete to review the grading, mix design, strength and thickness.
de536963-d09b-5630-8a9d-f4a7e6907d8f | note | Verifying Document - IANZ Lab Report
8e35e34f-9d36-50ee-86d4-6d32940260f2 | note | Frequency - Upon Request
e6a9cf62-e6f1-5296-b64e-95bcfc09ed32 | note | Verification Activity: Activity - W
761acbc2-a99e-5ac7-b244-3f91958fdd69 | note | Verification Activity: By - SE
8e7f0dc7-f06e-5535-84fd-52817e21abbe | note | Engineer Rep Signature - R
9c37305b-4a15-5fa3-8720-c7ccb3f5d283 | note | MSQA - R
cc1c554f-bcef-4561-904d-db1680c85c0e | section | SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
42515b02-ef7b-40f5-b150-33e1148c7091 | checkpoint | 6.01.01 - Construction Record Compilation
9aeaed43-0483-5191-82df-54ddbfdcf012 | note | Acceptance/Conformance criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
6700efc3-f786-56f1-ad55-7c9ace4666cc | note | Standard/Specification - Downer
2107edea-a3f4-5810-9df1-c78087f1c181 | note | Verifying Document - Records
f8e8249d-a232-5de7-be4d-54b1a7f4f84d | note | Frequency - Post construction
2fd13370-31e9-51bc-b4d1-a5fdf7ddd15f | note | Verification Activity: Activity - H
ca842d43-3f59-5dca-947c-6dc4042524ab | note | Verification Activity: By - SE
9333d873-7061-54b0-b3cb-e0dd34e550ca | note | Engineer Rep Signature - R
9fb4f35e-f9d7-59fe-92e8-6d9b433f7791 | note | MSQA - R
4683034b-813c-49cb-b645-e8b084dda74c | checkpoint | 6.01.02 - Survey Records
d2b61a3f-7cbb-558d-9620-240fd5434c2c | note | Acceptance/Conformance criteria - Ensure all items have been surveyed and records are assembled for asbuilting
127f3b87-1e8e-5465-a7b2-54e5a47f7c83 | note | Standard/Specification - Downer
d8d44068-8eba-586b-bf15-079dda7a6388 | note | Verifying Document - Records
e762692c-de24-5a53-b406-63c0ce267feb | note | Frequency - Post construction
a57b0a99-9572-5705-a658-23547269a38f | note | Verification Activity: Activity - H
cdd50653-4aab-5355-a419-2cdb4daf5612 | note | Verification Activity: By - SV
e9e681eb-cae8-5017-9336-44771768b6c0 | note | Engineer Rep Signature - R
c6643a22-dd58-5d32-815d-354c9a729f23 | note | MSQA - R
1f04b71f-e557-4366-b742-ef058f0c7830 | checkpoint | 6.01.03 - Redline Drawings
8aa4de9c-4f31-5b9d-a730-7f9dc6ac77be | note | Acceptance/Conformance criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen/RFI reference
8f2b043f-d880-52fe-805e-06d5da5ce194 | note | Standard/Specification - Downer
631d74a3-e7c8-5374-bec6-33f06f26679c | note | Verifying Document - Redlines
98c8e754-b52f-541b-9e46-ddd7311eab45 | note | Frequency - Post construction
48e9b07a-b52b-5cae-ba41-36425372402e | note | Verification Activity: Activity - H
70b9a925-5001-56a3-b47f-b830e0a9b03c | note | Verification Activity: By - PE
8826964a-c74d-52e7-9433-6d48d1283ebd | note | Engineer Rep Signature - R
ce6b6f57-51ad-5d9e-be35-904d03256665 | note | MSQA - R
1bcf1d21-9866-4b83-98fd-ae6d3aed74ae | checkpoint | 6.01.04 - Defect, Snag and Punch List
f5860d29-c37a-58ed-83fc-f40ad8fc22dc | note | Acceptance/Conformance criteria - Update the project Defect, Snag and Punch List Register
252f89f9-1c90-577c-9acb-3ebff19a06a2 | note | Standard/Specification - Downer
ef361d0e-c4b3-5430-a87c-7f06dbd1852a | note | Verifying Document - Register
0189ca1b-1561-5a10-9fc2-4868d8ac9468 | note | Frequency - Post construction
11d0a072-4c9c-5cbb-8788-26c9ae37e5ad | note | Verification Activity: Activity - H
9726a5ce-d579-54d0-869e-8ae1bf8f73d2 | note | Verification Activity: By - PE
0e6567a3-2144-5c65-b43e-330e866fae7e | note | Engineer Rep Signature - R
ef12084e-1709-5a49-9fae-8e026a43606f | note | MSQA - R
789e8b38-917a-4504-8c6a-c7b789a53165 | checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
d5722433-a345-55e9-99f7-807dfa75a753 | textbox | Contractor's Rep Name:
aae54303-3add-54bb-bd75-14b9beccc422 | textbox | Engineer's Rep. Name:
67c3b565-93f8-568e-8f31-9037d92b7e76 | date | Date:
f75058fb-14d4-4b4d-acb4-944831c490ef | signoff | Add Signature
2a108de0-5d9c-405e-9e6c-1391f1b63163 | checklist | DN1211-CHK-001 Stormwater Drainage Quality Check Sheet | itp | DN1211-CHK-001 Stormwater Drainage Quality Check Sheet
d01bb0fa-981b-4257-b668-0f306a57ced6 | section | Materials
6375d497-c66c-411e-8e65-c821b8b7516d | checkpoint | Materials available and comply with specs (all materials)
dfc8a7fb-9923-5c27-ab86-aa4f27b84d37 | note | Comments - Sent to design engineer for review
f6ee3ef9-4655-4f4c-bcb1-e4cedf653d21 | section | Excavation
0b2aaef9-f488-4320-87f8-d16be8f71521 | checkpoint | Has the permit to excavate been completed
750d7c78-b56c-5cb2-bb08-c5151c3d8e64 | note | Comments - Services clearly identified (Both KR and DNZ)
a6249c29-bb87-56cd-91d7-a48b6f7b4d2d | note | ○ NUO standover on site if required
d8cf0920-849b-480e-a28a-bf2ab731bd04 | checkpoint | Set out complete
930f5fc4-91b2-5173-a32d-64345a7d446d | note | Comments - As per IFC Civil Drawings
17db364a-cf29-4213-ae66-a65ce559eecf | checkpoint | Protection of existing pipelines / utilities
ee79636b-9caf-4166-b768-2003fcef790e | checkpoint | Trench excavation to line, level and grade
512a44a1-88a9-5741-9f63-a507ff58d3ef | note | Comments - Every 10m
2b2fba20-fd9c-59ba-afa1-b1a91256db76 | note | ○ To lines, levels, gradient as shown on drawings
7df5fb38-572f-5308-95ab-c719b6df0de7 | note | ○ Sufficient width to permit installation, pipes minimum 100mm from trench wall
baa05405-c473-587e-96c1-0f64f1998c9d | note | ○ Width ,<600mm greater than pipe diameter
e5eb6bee-37c3-4fa7-b723-fd04ed8cacf9 | checkpoint | Trench excavation open length
33bda56c-2426-5500-b59c-bc83f26e5e24 | note | Comments - Not to exceed manhole length or 30m
3937519b-92a6-4ac0-a3cd-3433a30edbef | checkpoint | Materials removed and stock piled
99d6f212-7bdd-49d3-830e-175cac2ad942 | checkpoint | Bottom of trench foundation condition
f519ec45-2b30-524b-9b68-a830e6114c9f | note | Comments - Water ingress kept below bedding level
ea4cb0fe-ca55-576d-8ade-ebc14a5ab7fa | note | ○ Subgrade suitable for pipe laying
c8031554-cb2f-4a91-a18c-38150db3c5b7 | checkpoint | Over excavation required?
ded950d0-d587-5819-859c-1277ed1a653e | note | Comments - Engineer to be notified and approval received prior to undercut.
a0666b6e-f2f0-491e-bc07-8b9486f6c50f | signoff | HOLD POINT
ba394402-0b3b-4be8-9340-f1f9fd577a76 | section | Pipe Installation
a5f16f4e-ea65-4c6c-a76b-23bc4488bf77 | checkpoint | Hold point
aacd42fe-5b5e-5540-b8ca-2456368f2aaf | note | Comments - Engineer to be notified 24hrs prior to pipe laying
51add03e-2fcc-42ee-942b-162ce3bcfcac | signoff | HOLD POINT
65dd0300-17c3-4d8f-8f2b-278ff1bf8536 | checkpoint | Pipes transported to site , stored and lifted correctly to prevent damage
67eec2f8-b35f-465d-94a7-b04f9409d473 | checkpoint | Trench shield/Benched/battered
78ef0102-6181-5c8e-a32f-eafebfb34949 | note | Comments - If the trench is deeper than 1.5m
ff0fad76-9676-42eb-b206-45b8cfac80f3 | checkpoint | Line and level
5fe3b340-7fda-5832-96d1-b61bd7280c20 | note | Comments -
f06b8532-63b4-5735-8061-8b03398cc5f0 | textbox | Design:
e0b070e2-0f92-558e-a6d2-7510a13edaec | textbox | Achieved:
89e23c3e-aa4b-4d5b-b6c5-76b82ab003bc | checkpoint | Cleanliness and condition
79980bda-084a-5b83-99b1-6440a99602aa | note | Comments - Internal pipe and joints clean and free of dirt/debris
b7c9b724-65cc-5179-bb1a-e22f9c1312c5 | note | ○ Pipe condition inspected prior to backfilling
a91200ca-46c1-4c73-a4b7-0717a9b850a9 | checkpoint | Bedding and Haunching
370a2d05-8021-5929-a27c-b05ff0fd7fdb | note | Comments - AP<12 granular bedding material
9ee42627-75d2-5549-a1b6-262140f60db6 | note | ○ Clegg hammer tests (every 10m, min CIV 12)
316fcf5e-34e6-5ced-8047-7d2358042d97 | note | ○ Clegg Results:
84c6155d-2fc0-4699-8b47-4d0804851837 | checkpoint | Temporary capping of end of pipes
c4ebc408-9d1d-4018-afc7-14aa947b6edb | checkpoint | Backfill Placement
008a00f8-0ff1-5c52-a338-b35d96e96f3e | note | Comments - AP>40 granular bedding material
6288a32c-3e7d-523a-b0ba-d38a38a19780 | note | ○ Clegg hammer tests (every 10m, min CIV 25)
91d3d9aa-9de7-55fc-b183-e5c2df6731f9 | note | ○ Compacted in 200mm layers
a72828a9-2355-5256-8dde-0a4d7e9da188 | textbox | Clegg Results:
71395699-e98e-4c69-aa04-981879084797 | section | Manhole Installation
e92be3b1-1d0f-4238-8b40-153b93563954 | checkpoint | Alignment
32ae0601-296b-510e-9fb8-2e91758f7cb8 | note | Comments - Correct position (<50mm)
495de50c-8582-5a2b-a913-7c00c3b82bf5 | note | ○ Vertical
b43608b4-ee23-47ff-b835-b6204482687e | checkpoint | Bedding
4c8de7d6-de0e-5e9e-9b92-108286954e9b | note | Comments - Bedding material – min 150mm
3b0086bb-6939-5ef4-939b-ba1eda95e5e9 | note | ○ Clegg hammer tests (min CIV 12)
80bfd47f-05ed-5264-82b7-477b14419e81 | textbox | Clegg Results:
c8a5e9a8-cc24-4372-b29b-9167c21c5496 | checkpoint | Backfill Placement
df912de1-e683-5890-86d2-53a5cb241474 | note | Comments - AP>40 granular bedding material
7f8874d1-dd27-570f-8e4a-6f88e16b89a4 | note | ○ Clegg hammer tests (min CIV 25)
895ce9b5-c603-51da-94c3-38a48789aea1 | note | ○ Compacted in 200mm layers
726aabc2-a1e4-5d4a-94bc-059d0499bdec | textbox | Clegg Results:
5b273b34-232e-46fa-a213-21ea23e7f3e0 | checkpoint | Penetrations
a974ae65-477e-531f-8343-5c3388ae2d75 | note | Comments - Formed by cutting or drilling prior to knocking section out
81a53eb7-2d6d-46fa-9816-835dfee8e2ee | checkpoint | Pipe Ends
26aa13a1-4872-5b92-a366-2efac5679c24 | note | Comments - Finished approx. 50mm beyond inside wall
f83d50ae-c99d-5c09-9a8d-238b788841a1 | note | ○ Plastered with cement mortar or encased in benching concrete
47d8195e-e8da-4630-8ec7-58d0147515b6 | checkpoint | Corbels
7354aa82-1834-5050-88d2-369a4606c285 | note | Comments - Pipes haunched and surrounded by concrete by >200mm from manhole
b8a83028-f4c4-4cdf-9942-7ba34e706d68 | checkpoint | Benching
210fcd71-94fd-51a3-834f-5816bd719a9a | note | Comments - Smooth finish, graded to channel, in accordance with drawings
b272941b-fe4c-4a30-b891-b42dc5e6353e | checkpoint | Works completed as per design requirements and work area is ready to be handed over for sign-off
12d4a07d-7860-45c0-8701-8b6e8747b438 | signoff | Signed by Sub contractor Representative
645d8739-1e43-4519-9a72-77d5102eed3f | checkpoint | Final Approvals
f0fae84f-1101-57e3-9a4d-2af8502b247d | textbox | DNZ Check - Name:
a7496307-ebff-5601-932a-0c785cf07fa3 | date | DNZ Check - Date:
eaba1159-b424-5fdb-9f05-e1dbb65424bb | textbox | Engineer / Consultant - Name:
60f0f80b-2b22-5876-b492-fe8a7412ff73 | date | Engineer / Consultant - Date:
8e383c3e-00df-4eb5-a377-bb108e0aa8dd | signoff | Sign-Off
5f433e59-776e-4e8a-bf0e-cb809e243ac2 | checklist | Documents & Photos |  | Documents & Photos
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
dd77a1e6-4546-407a-bdc7-2fb24ca37b74 | checkpoint | Please upload the relevant document(s) / photos and press PASS.