## ITP - Wastewater
INSPECTION & TEST PLAN - Waste Water Reticulation Upgrade
[6 empty] | Hold Point (H) |  | Review | Prepared By | Signature | Date
[6 empty] | Witness (W) |  | Prepared By | Josh Welch |  | 2025-08-01
|  | Kaikohe Wastewater Reticulation Upgrade |  |  |  | Submit (S) |  | Reviewed By | Gerrie van der Linde |  | 2025-08-01
[6 empty] | Perform (P) |  | Approved by
Accept (A)
Location
Contract Details | Contract Name |  |  |  |  | Text Box
| Contract Number |  |  |  |  | Text Box
Location | Location of Works |  |  |  |  | Text Box
TASK | SPECIFICATION REFERENCE | TEST/TASK REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL | Client | COMMENTS
Preconstruction
Precondition Survey | Wastewater Specification B.2.11.2.2 | Visual inspection. | UCCL | Prior to starting on site. Survey conducted of all surfaces, footpaths, kerbs, driveways and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works. | Survey documents submitted to Engineer. | P, F, NA, Attachment
Materials Quality | FNDC Approved Materials List - Wastewater and Stormwater | Visual check for approved materials, quality and condition. | UCCL | On arrival to site, prior to using materials. | Materials meet specifications or otherwise approved by Engineer. Delivery dockets. Photos. | P, F, NA, Attachment
Survey Setout | Wastewater Specification B.2.11.2.4 | Survey set out. | UCCL | Prior to commencing each stage of work. | Survey set out as per IFC drawings. | P, F, NA, Attachment |  | Check all MHs for levels, prior to constructing drainage lines, they must verify the inverts and locations of existing manholes as part of the inspection and testing process
Service Location | Wastewater Specification B.2.11.4.2 | Locate underground services within work area. | UCCL | Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services. |  | P, F, NA, Attachment
Installation
Material Properties (Bedding) | Wastewater Specification B.7.5.1.9 | AP20 Grading curve to be submitted to Engineer for approval. | UCCL Haigh Workman | Prior to using bedding material on site. PE bedding, pipe surround and haunching shall be AP20 in accordance with AS/NZS 2566. | Bedding grading curve accepted by Engineer. | P, F, NA, Attachment
| NTC020 | Aggregate Testing Frequency | UCCL Haigh Workman | PSD (Grading): 1 test per 500m3 Estimated requirement: 2 tests for ~1080m3 | Bedding material test certificates accepted by Engineer. | P, F, NA, Attachment
Material Properties (Subbase - AP65) | FNDC Engineering Standards 3.3.2 | Subbase material meets FNDC Engineering Standards | UCCL Haigh Workman | Prior to using subbase material on site. | Subbase material test certificates accepted by Engineer. | P, F, NA, Attachment
| NTC020 | Aggregate Testing Frequency | UCCL Haigh Workman | PSD (Grading): 1 test per 2000m3 Estimated requirement: 8 tests for ~15,853m3 | Subbase material test certificates accepted by Engineer. | P, F, NA, Attachment
Material Properties (Basecourse - AP40) | FNDC Engineering Standards 3.3.2 | Bascourse material meets FNDC Engineering Standards | UCCL Haigh Workman | Prior to using basecourse material on site. | Basecourse material test certificates accepted by Engineer. | P, F, NA, Attachment
| NTC020 | Aggregate Testing Frequency | UCCL Haigh Workman | PSD (Grading): 1 test per 1000m3 Estimated requirement: 4 tests of each type for ~3240m3 | Subbase material test certificates accepted by Engineer. | P, F, NA, Attachment
Pipe and Rubber Rings | Wastewater Specification B.7.8.3 | Visual inspection | UCCL | Visual inspection prior to use (clean and free from defects). | Photographs. | P, F, NA, Attachment
Pipeline Installation (PVC) | Wastewater Specification B.7.8 and B.7.9 FNDC Engineering Standards Sheet 31 | Visual inspection Pipeline installed to correct alignment, grade and level | UCCL | On completion of installation of each length of pipe, prior to backfilling. Throughout installation of pipeline. Horizontal alignment +100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe. | As-built drawings. Photographs. | P, F, NA, Attachment
Stainless Steel Pipe Bridge | Wastewater Specification 'Package 3 - Bisset - Pipe Bridges Specification | Visual inspection Pipe installed as per specification to correct alignment, grade and level | UCCL | On completion of installation of each pipe bridge. Horizontal alignment + 100mm. Vertical tolerance +/- 10% of the design grade for each section of pipe. | As-built drawings. Photographs. | P, F, NA, Attachment
Manhole Installation and Backfill | Wastewater specification B.7.9 | Visual inspection. Manhole checks including position, haunching, steps and sealed joints. | UCCL | On completion of manhole installation. | Falls through manholes are to be within +5mm of design levels. Maximum deviation from vertical (manholes/chambers) shall be 10mm per metre. | P, F, NA, Attachment
Pipe Bedding | Wastewater Specification B.3.4.1 FNDC Engineering Standards Sheet 31 | Visual inspection. Compaction test on top of bedding. | UCCL | Bedding installed as per specifications. | Photographs. Compaction test results. | P, F, NA, Attachment
Pipe Backfill (Outside of Carriageway) | Wastewater Specification B.3.6.3 FNDC Engineering Standards Sheet 31 | Visual inspection. Compaction test on top of GAP65. | UCCL | On completion of GAP65 layer. On completion of ordinary backfill. | Photographs. Compaction test results. | P, F, NA, Attachment
Subbase | Wastewater Specification B.3.6 and B.3.7 FNDC Engineering Standards 3.3.3.3 and Sheet 31 | Visual inspection NDM testing | UCCL | NDM testing on completion of subbase layer, prior to installing basecourse. Backfill and compaction completed as per specifications. | Compaction records. Photographs. | P, F, NA, Attachment
Basecourse | Wastewater Specification B.3.6.2 FNDC Engineering Standards 3.3.3.4 and Sheet 31 | Visual inspection NDM testing | UCCL Haigh Workman | NDM testing on completion of basecourse layer, prior to sealing. Basecourse installed as per FNDC Engineering Standards, and NZTA B/02. | Compaction records. Photographs. | Hold Point P, F, NA, Attachment
Detection Tape | Wastewater Specification B.7.5.1.6 FNDC Engineering Standards 5.3.3.1.2 | Visual inspection | UCCL | "Sewerage" detection tape laid directly above all wastewater pipelines. | Photographs. | P, F, NA, Attachment
Pipeline Testing | Wastewater Specification B.7.9.1 | Air test | UCCL Haigh Workman | Each section of pipeline is to be tested by 'Air Test', including Lunden junctions. | Drop in pressure shall not exceed 25mm over a period of 5 minutes. | Hold Point P, F, NA, Attachment
Manhole Testing | Wastewater Specification B.7.9.1 | Visual inspection. Water test. | UCCL | Visual inspection of each manhole prior to backfilling. Water test after backfill. | Drop in level shall not exceed 5mm in 10 minutes. | Hold Point P, F, NA, Attachment
Wastewater House Connections | Wastewater Specification B.7.8.10 | Visual inspection. Survey. | UCCL | On completion of each connection. | Photographs. As-built drawings. | P, F, NA, Attachment
Reinstate Driveways | Wastewater Specification B.3.8.5 | Visual inspection | UCCL | On completion of wastewater installation. Driveways reinstated in the same material and to the same standard as existing prior to works. | Photographs. | P, F, NA, Attachment
Reinstate Footpaths | Wastewater Specification B.3.8.5 | Visual inspection | UCCL | On completion of wastewater installation. Footpaths reinstated in the same material and dimensions as existing footpath, and constructed to FNDC Standards. | Photographs. | P, F, NA, Attachment
Reinstate Kerb and Channel | Wastewater Specification B.8.5 | Visual inspection | UCCL | Kerb and channel profiles match existing. Concrete has minimum 28-day strength of 25MPa. | Photographs. | P, F, NA, Attachment
Concrete Pour | Wastewater Specification B.4.4.2 | Prepour inspection | UCCL Haigh Workman | Prior to pouring concrete. | Pre-pour inspection checklist. Photographs. | P, F, NA, Attachment
Asphaltic Concrete Layer (DG10) | NZTA M10 Specification | As per NZTA M10 Specification | UCCL | On completion of the pavement surface. | Test results submitted to Engineer. Photographs. | P, F, NA, Attachment
Post Construction
As-Built Drawings | Wastewater Specification B.2.18.1 | As-built records and coordinate data | UCCL | Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion. Final as-builts issued prior to Final Completion. | As-builts submitted to the Engineer for approval. | P, F, NA, Attachment
CCTV | Wastewater Specification B.2.18.2 | CCTV video survey to the National Standards | UCCL | On completion of the installation of each pipeline with backfill to the top of the pipe. | CCTV results submitted to Engineer for approval. | P, F, NA, Attachment
RAMM Information | Wastewater Specifcation B.2.18.3 | RAMM information | UCCL | RAMM information submitted to the Engineer on completion of works. | RAMM information submitted to the Engineer. | P, F, NA, Attachment