## ITP - Water Reticulation
INSPECTION & TEST PLAN - Water Reticulation
[6 empty] | Hold Point (H) | Review | Prepared By | Signature | Date
[6 empty] | Witness (W) | Prepared By | Josh Welch |  | 2025-08-01
|  | Kaikohe Water Supply and Reticulation Upgrade |  |  |  | Submit (S) | Reviewed By | Gerrie van der Linde |  | 2025-08-01
[6 empty] | Perform (P) | Approved by
Accept (A)
Location
Contract Details | Contract Name |  |  |  |  | Text Box
| Contract Number |  |  |  |  | Text Box
Location | Location of Works |  |  |  |  | Text Box
TASK | SPECIFICATION REFERENCE | TEST/TASK REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA |  | COMMENTS
Preconstruction
Precondition Survey | Water Specification B.2.11.2.2 | Visual inspection | UCCL | Prior to starting on site. Survey conducted of all surfaces and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works. | Survey documents submitted to Engineer. | P, F, NA, Attachment
Materials Quality | FNDC Approved Materials List - Water Services | Visual check for approved materials, quality and condition. | UCCL | On arrival to site, prior to using materials. | Materials meet specifications or otherwise approved by Engineer. Delivery dockets. Photos. | P, F, NA, Attachment
Survey Setout | Water Specification B.2.11.2.4 | Survey set out. | UCCL | Prior to commencing each stage of work. Engineer to be notified if any concerns | Survey set out as per IFC drawings. | P, F, NA, Attachment
Service Location | Water Specification B.2.11.4.2 | Locate underground services within work area. | UCCL | Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services. |  | P, F, NA, Attachment
Installation
Material Properties (Bedding) | Water Specification B.5.5.1.13 | GAP20 grading curve to be submitted to Engineer for approval | UCCL Haigh Workman | Prior to using bedding material on site. PE bedding, pipe surround and haunching shall be GAP20 in accordance with AS/NZS 2566. | Bedding grading curve accepted by Engineer. | P, F, NA, Attachment
| NTC020 | Aggregate Testing Frequency | UCCL Haigh Workman | PSD (Grading): 1 test per 500m3 Estimated requirement: 2 tests for ~1080m3 | Bedding material test certificates accepted by Engineer. | P, F, NA, Attachment
Material Properties (Subbase) | FNDC Engineering Standards 3.3.2 | Subbase material meets FNDC Engineering Standards | UCCL Haigh Workman | Prior to using subbase material on site. | Subbase material test certificates accepted by Engineer. | P, F, NA, Attachment
| NTC020 | Aggregate Testing Frequency | UCCL Haigh Workman | PSD (Grading): 1 test per 2000m3 Estimated requirement: 8 tests for ~15,853m3 | Subbase material test certificates accepted by Engineer. | P, F, NA, Attachment
Material Properties (Basecourse) | FNDC Engineering Standards 3.3.2 | Basecourse material meets FNDC Engineering Standards | UCCL Haigh Workman | Prior to using basecourse material on site. | Basecourse material test certificates accepted by Engineer. | P, F, NA, Attachment
| NTC020 | Aggregate Testing Frequency | UCCL Haigh Workman | PSD (Grading): 1 test per 1000m3 Estimated requirement: 4 tests of each type for ~3240m3 | Subbase material test certificates accepted by Engineer. | P, F, NA, Attachment
Pipe | Water Specification B.5.8.3 | Visual inspection | UCCL | Visual inspection prior to use (clean and free from defects). | Photographs. | P, F, NA, Attachment
Test Welds (Butt Welding) | Water Specification B.5.10.2.2 | Laboratory testing | UCCL Haigh Workman | Three butt welded joints and one section of virgin pipe shall be tested in accordance with ISO 13953. One test weld for every 10 lengths of pipe laid. | Weld test results submitted to Engineer. | P, F, NA, Attachment
Welded Joints (Butt Welding) | Water Specification B.5.10.2.1 | Visual inspection | UCCL | On completion of each butt weld. Weld inspection checklist. Weld data log. | Weld inspection checklist submitted for each butt weld. Weld data log submitted for each weld. | P, F, NA, Attachment
Welded Joints (EF Welding) | Water Specification B.5.10.2.1 | Visual inspection | UCCL | On completion of each EF weld. Weld inspection checklist. | Weld inspection checklist submitted for each EF weld. | P, F, NA, Attachment
Pipeline Installation (PE) | Water Specification B.6.4.5 and B.6.4.6 | Visual inspection Pipeline installed to correct alignment, grade and level | UCCL | On completion of installation of each length of pipe, prior to backfilling. Horizontal alignment tolerance + 100mm. Vertical alignment tolerance + 100mm. Valves on centreline of pipe permissible vertical deviation of +50mm. | As-built drawings. Photographs. Changes to horizontal or vertical alignment to be agreed with Engineer pror | P, F, NA, Attachment
Valve Installation (including Chambers if required) | Water Specification B.5.8.4 and B.5.9 FNDC Engineering Standards 6.2.8 | Visual inspection | UCCL | Installed as per specifications. | Photographs. As-built drawings. | P, F, NA, Attachment
Valve Boxes and Markings | FNDC Engineering Standards 6.2.8.5, and Sheet 48 | Visual inspection | UCCL | On completion of installation. Valve marker posts and kerb markings as per FNDC standard. | Photographs. | P, F, NA, Attachment
Hydrants | Water Specifcation B.5.8.4 FNDC Engineering Standards 6.2.9.1 | Visual inspection | UCCL | Installed as per specificationsand IFC drawings. | Photographs. As-built drawings. | P, F, NA, Attachment
Hydrant Boxes and Markings | FNDC Engineering Standards 6.2.9.3, and Sheet 48 | Visual inspection | UCCL | On completion of installation. Hydrant marker posts and kerb markings as per FNDC standard. | Photographs. | P, F, NA, Attachment
Air Release Valves | Water Specifcation B.5.5.1.11 FNDC Engineering Standards Sheet 51 | Visual inspection | UCCL | On completion of installation. Air valves installed to specification | Photographs. As-built drawings. | P, F, NA, Attachment
Thrust Blocks | FNDC Engineering Standards 6.2.3.8, and Sheet 50 | Visual inspection | UCCL | On completion of the thrust block installation, prior to backfilling. | Photographs. | P, F, NA, Attachment
Pipe Bedding | Water Specification B.3.4.1 FNDC Engineering Standards Sheet 31 | Visual inspection | UCCL | Bedding installed as per specifications. | Photographs. | P, F, NA, Attachment
Pipe Backfill (Outside of Carriageway) | Water Specification B.3.3.2 | Visual inspection | UCCL | On completion of backfill. Trench backfilled with original sound material from the trench. | Photographs. | P, F, NA, Attachment
Subbase | Water Specification B.3.5.2 FNDC Engineering Standards 3.3.3.3 and Sheet 31 | Visual inspection NDM testing | UCCL | NDM testing on completion of subbase layer, prior to installing basecourse. Backfill and compaction completed as per specifications. | Compaction records. Photographs. | P, F, NA, Attachment
Basecourse | Water Specification B.3.5.2 FNDC Engineering Standards 3.3.3.4 and Sheet 31 | Visual inspection NDM testing | UCCL Haigh Workman | NDM testing on completion of basecourse layer, prior to sealing. Basecourse installed as per FNDC Engineering Standards, and NZTA B/02. | Compaction records. Photographs. | Hold Point P, F, NA, Attachment
Detection Tape and Tracer Wire | Water Specification B.5.5.1.6 FNDC Engineering Standards 6.3.2.4 and Sheet 31 | Visual inspection and electrical continuity testing |  | On completion of installation. A blue metallic detection tape labelled 'Water' shall be laid directly above all new non-metallic watermains. Tracer cable (2.5mm²) shall be attached to pipe wall at maximum 3.0m intervals. | Electrical continuity test results provided to Engineer. | P, F, NA, Attachment
Pressure Testing of Pipes | Water Specification B.5.10.1 FNDC Engineering Standards 6.3.3.2 | Pressure test of PE pipeline | UCCL, FNDC, Haigh Workman | On completion of installation of PE pipeline, after sufficent backfill has been placed to prevent movement. Pressure test as per FNDC Engineering Standard. | Test results submitted to Engineer. | Hold Point P, F, NA, Attachment
Flushing and Disinfection | Water Specifcation B.5.12.3 FNDC Engineering Standards 6.3.4 | Visual inspection (flushing) Chlorination and testing | UCCL, FNDC, Haigh Workman | On completion of pressure test, prior to connection. Flushing and chlorination/testing completed as per specifications. Results meet FNDC specification. | Test results provided to Engineer for approval prior to connection. | Hold Point P, F, NA, Attachment
Connection to Existing Watermains | Water Specification B.5.12.4 FNDC Engineering Standards 6.3.5 | Watermain connection | UCCL, FNDC, Haigh Workman | Connection to be completed after instruction from Engineer. Note from FNDC Engineering Standard - "Only the FNDC's Reticulation Maintenance Contractor may undertake the connection". | Photographs. | Hold Point P, F, NA, Attachment
Service Connections | FNDC Engineering Standards 6.3.2.2 and Sheet 46 | Water connection | UCCL | Connection to be completed after instruction from Engineer. | Photographs. As-built drawings. | P, F, NA, Attachment
Reinstate Driveways | Water Specification B.3.7.6 | Visual inspection | UCCL | On completion of wastewater installation. Driveways reinstated in the same material and to the same standard as existing prior to works. | Photographs. | P, F, NA, Attachment
Reinstate Footpaths | Water Specification B.3.7.6 | Visual inspection | UCCL | On completion of wastewater installation. Footpaths reinstated in the same material and dimensions but constructed to FNDC Footpath Standards. | Concrete dockets. Photographs. | P, F, NA, Attachment
Reinstate Kerb and Channel | Water Specification B.3.7.6 | Visual inspection | UCCL | Replacement kerb and channel profiles match line and level of existing kerb and channel. Concrete has minimum 28-day strength of 25MPa. | Photographs. | P, F, NA, Attachment
Concrete Pour (Stuctural - Pipe Bridge Footings, Commercial Driveways) | Water Specification B.4.4.2 | Prepour inspection | UCCL Haigh Workman | Prior to pouring concrete. | Pre-pour inspection checklist. Concrete dockets. Photographs. | P, F, NA, Attachment
Concrete Pour (Non-Structural - Footpaths, Residential Driveways) | FNDC Engineering Standards Sheets 12, 17 and 18 | Visual inspection | UCCL | Prior to pouring concrete. | Pre-pour inspection checklist. Concrete dockets. Photographs. | P, F, NA, Attachment
Asphaltic Concrete Layer (DG10) | NZTA M10 Specification | As per NZTA M10 Specification | UCCL | On completion of the pavement surface. | Test results submitted to Engineer. Photographs. | P, F, NA, Attachment
Grout Filling of Redundant Watermains | Water Supply Drawings Notes, No. 20.1 and 20.2 | Redundant watermains to be grout filled and remain in place. Remove redundant valve boxes, signs etc. | UCCL | Grout filling on completion of new pipelines. | Grouting record. Photographs. | P, F, NA, Attachment
Post Construction
As-Built Drawings | Water Specifcation B.2.18.1 | As-built drawings meet FNDC specification | UCCL | Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion. Final as-builts issued prior to Final Completion. | As-buiilts submitted to the Engineer for approval. | P, F, NA, Attachment
RAMM Information | Water Specification B.2.18.2 | RAMM information | UCCL | RAMM information submitted to the Engineer on completion of works. | RAMM information submitted to the Engineer. | P, F, NA, Attachment