## Master List Templates
Id | Type | Name | Values | Prompting Name
65334946-7ad1-40ae-94fa-2e6946071ac2 | checklist | Upload Attachments |  | Upload Attachments
6da6f498-e18e-4121-84fe-5cd5ddfb8d03 | section | Details
abd1894c-f4ca-4bd7-adb7-c536eb29dab6 | checkpoint-no-value | Upload Attachments

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
552c8471-d33e-46f8-aba8-0f35e6e6eb96 | checklist | Air Valve ITC |  | Air Valve ITC
0bbe9b75-8bcc-4ed9-89f0-ce08ffb5a4ba | section | Location
f158bb68-b97e-471a-9904-df676f47ec17 | checkpoint | Air Valve Location
7a8254e7-02d3-5262-9721-03563e28bd9a | textbox | Chainage or property location of Air Valve
1aaf6db4-e866-5e0c-94a7-4fbf0a1d06c1 | date | Date of Installation
d90c0487-dbb5-4717-9000-59b10dbe48d5 | checkpoint | Air Valve is installed to line and level of the specifications and IFC drawings
5a17ff3d-9784-4edf-b43e-90bf12e20da8 | section | Air Valve Installation
80917e30-e0ae-4f07-8f1f-30e82575b8de | checkpoint | Air Valve Details
97ba2a0d-496b-515d-8684-35453b42331d | textbox | Air Valve Make/Model
65b94401-ee16-598a-ab4d-550d9a19bf21 | tickbox | Air Valve is 50mm double purpose, if not select other
032720e4-f02a-5a04-9368-cdb93be11524 | textbox | Other - specify
31dc4b23-bf5c-42fd-865b-9ae9c3bf4ff6 | checkpoint | Valve Size
5b302408-fef1-5484-8382-b425c7f5c8ab | tickbox | Valve size is 50mm DI peet or SS ball valve, If not select other
afee0bac-7f0f-5e86-8799-e0bc0e430915 | textbox | Other - specify
79010397-fba4-408b-b7c7-bb481d3c2295 | checkpoint | Bolts - All bolts below ground are SS and protected with Denso, Mastic and Polytape
6990e313-7470-4185-a4de-9f1dffdf78bd | section | Reinstatement
36beee72-ffe2-4bee-9ab2-6e8e35f59003 | checkpoint | Manhole Riser
8ce12525-017a-566a-ae73-b8f6779fcf3b | tickbox | 1050 Manhole riser with heavy duty manhole lid used, if not select other
5b47ea98-9643-54c3-9730-118aa6b70659 | textbox | Other - Specify
7ddf94d2-8ede-4e40-80a5-76b5bb4b830c | checkpoint | Reinstatement
8bfbd313-ca68-52a8-9535-041e12007e87 | tickbox | Manhole lid is set flush with the surrounding ground levels
fa3cccbe-2ae6-4935-9e66-2b2ef3b4ac8b | section | Post Construction and Handover
64497d1a-5f63-4411-9022-dcda69a9c8b4 | checkpoint | Final Inspection - Installation of Air Valve complies with IFC drawings, specifications and FNDC Standards
ba09b838-7bbd-55bd-ae81-e9ce8abee2fb | date | Date
7438f8c1-c5ee-44b2-bca6-f69e5ddf8db4 | checklist | Hydrant ITC |  | Hydrant ITC
338e31ea-a0f8-461c-bb49-b2556a606467 | section | Location
7740b790-2f31-4663-ad6c-7b1462ae0794 | checkpoint | Location
217074cd-3a84-59b5-a7c2-5133214d54bf | textbox | Chainage or property location of Hydrant
47997a12-f560-5709-8e99-d77ce6c4ad04 | date | Date of Installation
a27fc907-3d7a-4ca7-b58c-c802f59dcd02 | checkpoint | Hydrant is installed to line and level of the specifications and IFC drawings
bddf8f64-4b68-44e5-9648-135f2cf10de9 | section | Hydrant Installation
eb22de11-dd6f-46c0-8523-213b338bbe47 | checkpoint | Hydrant Installation
18231480-ef3e-588c-956b-2d436d2ab188 | textbox | Hydrant Make/Model
56b2d4b6-fb3b-5430-a578-12e0685c1b76 | textbox | Hydrant size
bda4689a-aaab-4e58-a7bb-8d58b1f6431e | checkpoint | All bolts below ground are SS and protected with Denso, Mastic and Polytape
f6000432-1ab1-4b2c-ad22-6f79e5e544af | section | Reinstatement
bd0966aa-64ca-4dc7-9ea4-5543f508558c | checkpoint | Reinstatement
96f0af6c-36d5-585e-a3f6-9e1e84b2c914 | tickbox | Hydrant Box installed to FNDC standards with the long side parallel to the direction of the main pipe
6c0c201e-5bec-5b84-82f7-ee583d2b55eb | tickbox | Marker peg installed with SV labelled, protruding 600mm from the surrounding ground
dfad7dd3-94cb-565a-991c-99cf164d12cf | tickbox | Blue RPM installed in carriageway, including yellow triangle marker and yellow kerb marking
77a9fc28-fa4d-5bde-8fad-0a2d093c8c20 | tickbox | Hydrant box is set flush with the surrounding ground levels
f3ffa063-7c23-4a1c-89d3-11084669ed38 | section | Post Installation
aa821e25-75f5-4f15-aa1d-4b8e75353c01 | checkpoint | Post Installation
d0d3975e-c604-5e37-b432-bb9f489b683c | date | Installation of Hydrant complies with IFC drawings, specifications and FNDC Standards
f3c43d33-bd74-434a-a38f-41166f1645fe | signoff | Final Inspection
4c4ca7d1-6bff-4810-bc1a-a59a5d5bcb66 | checklist | ITC - Pipeline Installation |  | ITC - Pipeline Installation
8fc5b704-3101-4878-804e-31042a11894a | section | Location & Contract Details
a08debc2-e617-40ba-b980-fb005e1d5260 | checkpoint | Contract Details
3fbfc6d5-5653-5a65-a3b3-057000a31e6b | textbox | Contract Name
b2312427-55cd-552b-bcf8-0302599f6012 | textbox | Contract Number
1252dc9e-b97f-4d31-aa0e-c7778cea3adb | checkpoint | Location
090224dc-ae31-5952-9efa-58267742062b | textbox | Location of Works
6c67d0ba-bbf2-5540-88ea-f972aaca0555 | textbox | Pipeline Identifier
f32d588a-0b00-562a-9279-429ac58279e4 | textbox | Installer
29e5eb31-d3df-4da9-a234-b7fb1fadf97a | section | Pipeline Details
e4d2f4a7-de2e-4caa-a658-c58cc85cc786 | checkpoint | Pipeline Details
813b6094-cb36-5cbe-921c-f5649f062e0c | textbox | Pipe Size
c943b7fb-6bdb-5cb5-9c30-2a47670d01d9 | textbox | Pipe Material
8db32fa0-ef0a-563e-802b-e9ee8deaa7f8 | textbox | Pipe RL Upstream conforms with the tolerances of the manhole inlet and outlets
3413f070-00da-54d6-9a47-75cc780e3cfa | textbox | Pipe RL Downstream conforms with the tolerances of the manhole inlet and outlets
e116b336-4bb9-51cf-8f2e-81fe2f7ab4ad | textbox | Design Grade
bc050394-2098-53d5-9942-4b6a52762b2c | textbox | Installed Grade has been installed within +/-10% of design grade
7e8ec738-9bdc-4491-8048-cf9e8faa7fac | checkpoint | Pipline grades and levels installed within tolerances
e5ba39e5-1311-5efa-844f-be1eb11fa763 | note | Attachment for sketch of inlets and outlets
bf4d8057-3713-4c0c-a03d-8251c67535bf | section | Pipeline Installation
725b0181-c54c-4d57-b189-dc24aa9ed9db | checkpoint | Survey setout completed including RL
d902bfe6-ab3c-4206-98cd-25621484a888 | checkpoint | Offsets by drainlayer checked and correct
1d8cb493-33e1-49b5-a31e-09cb0303c24f | checkpoint | Excavation completed to correct depth
80e5b78c-0ea2-4f15-88d4-fb5ffa0a710e | checkpoint | Subgrade meets specification
7c3af7af-6010-4a4d-9b97-673971aabd2c | checkpoint | Blinding placed to correct level
060044d5-d15b-445a-ba02-957d8334bb86 | checkpoint | Hardfill & surfacing layers installed meet specification
37f24f7d-28bd-4401-91fe-4ae64b2d38cd | section | Post Construction
b138ef55-6720-4ccb-8c49-62edeeb51bc6 | checkpoint | Pressure testing meets the specification
c824b703-a510-4145-98af-409323f36698 | checkpoint | As-Builts have been picked up of pipeline
45246672-ecff-419c-85ee-2ff079e60595 | signoff | Pipeline has been checked and Inspected
08481f6f-74f4-4ca9-92aa-a44f6b669fcb | checklist | ITC – MH Installation |  | ITC – MH Installation
35b1e971-f4b8-4db3-bc6b-70e184e77e40 | section | Location & Contract Details
92a2e2c4-29bb-4951-b271-c73b686e710a | checkpoint | Contract Details
d008d068-98b1-5617-8e99-1a12604921db | textbox | Contract Name
64d373c0-4f18-5b49-8bf3-41bf375ba8c4 | textbox | Contract Number
9469d25d-167d-4157-8158-9418f70bf930 | checkpoint-no-value | Location
3e8c8a8b-b940-57dd-968d-58f956fdd74b | textbox | Location of Works
f4764cf6-0074-5a9e-8d67-002c487f1bba | textbox | Manhole Number/Identifyer
2d67d76a-0211-4a46-8037-08acf8137001 | checkpoint-no-value | Manhole Details
6131bcce-4a39-5dfc-839f-91a88e5fc1be | textbox | Manhole size
67e01d83-9c21-5240-a09c-64d69fda1c03 | textbox | Lid Thickness
183009fa-ef92-428f-a967-f1edab8a5037 | section | Manhole Installation
84430911-ba41-4a66-9cf8-c89c6cf1f2aa | checkpoint | Survey setout completed including RL
23efc6b5-7fec-40b3-a7f9-cd4b9a389cdb | checkpoint | Offsets by drainlayer checked and correct
171766b6-02fe-4384-afed-baa36189bd47 | checkpoint | Excavation completed to correct depth
23e9db26-ae72-475b-83f3-a0f35f2f48bb | checkpoint | Subgrade meets specification
6407d036-56c1-440f-bfd0-0de9e8e1810e | checkpoint | Hardfill layer installed and meets specification
bccbf677-9812-4c45-b67f-beb4b8a66302 | checkpoint | Blinding placed to correct level
21c986b2-d663-4346-8b9a-7b862e8b60dd | checkpoint | Manhole horizontal position within tolerance
c690e6d7-fa27-4026-b954-cba7c8f60750 | checkpoint | Manhole verticle position within tolerance
9d9dbecd-94b5-4bfe-9a46-8f49ed7936a0 | checkpoint | Manhole installed plumb and within tolerance
0300af72-7662-53c0-a0f9-c42fab67b135 | note | Attachment for sketch of inlets and outlets
853f3a6a-1a06-46c2-bf34-31a12598ca34 | checkpoint | Cover and frame opening folds flat in the direction of traffic flow
849c2a51-ac64-4f44-801a-d1cdf4bd5b61 | checkpoint | Cover and frame opening conforms with surrrounding surfaces
088a734f-2bbb-4651-972f-a64c8521cfe4 | section | Inlet/Outlet Pipes
ae1b16ad-b494-4cd2-8dc5-be69ca853e80 | checkpoint | Pipe starters installed as per specification
3e8a89ce-e58a-46c9-84ed-c08741db806e | checkpoint | Pipe haunching completed as per specification
cb1ff4f7-54e6-4599-9dd4-875ac5f8b057 | checkpoint | Bottom of manhole finished as per specification
2172f74d-fdfe-4b03-8b4a-f74e337746d3 | checkpoint | Internal fall as per specification
f0878841-72ef-481a-a590-e9455d2383a1 | checkpoint | Outlet invert level within tolerance
73d07938-c1db-4e8f-aaeb-f0c73bfd3fb3 | checkpoint | Inlet 1 invert level within tolerance
3ed1e34e-775f-4403-9b72-c90dde794b66 | checkpoint | Inlet 2 invert level within tolerance
f7aa8783-0fd0-49e0-8d11-d05ace14423a | checkpoint | Inlet 3 invert level within tolerance
94ba1bc3-a5a2-40a5-b9d4-1c5c8ccf5cc8 | checkpoint | Inlet 4 invert level within tolerance
4d669aa1-adc7-43b8-bc1c-8f1d2f476006 | section | Post Construction
9b5f935a-ef9b-4be1-ba0c-e32eb71d87a5 | checkpoint | Low pressure hydraulic testing of manhole undertaken. The level of water in the manhole shall not drop more than 5mm in 10 minutes
36290237-6cbc-47fa-a8d6-5b08cc7a9dc8 | checkpoint | As-Builts have been picked up of manhole and laterals
117f9fb6-cba3-47d3-8368-eb297c0cbf5a | signoff | Manhole has been checked and Inspected
2b800225-08ec-4710-a599-23bd2e28fa95 | checklist | ITC Concrete Prepour |  | ITC Concrete Prepour
5b4663fa-cafa-45a5-8527-1a6564e3700b | section | Preconstruction
588c238b-bd07-4059-b655-1b673578e6c3 | checkpoint | Design Drawings
b0350f76-4be9-5e68-bb59-7b6a3acc1e96 | textbox | Contract Name
7d52c904-5b5d-5fc2-ab11-dcbf5045e2b6 | textbox | Contract Number
6964b63d-28e0-5055-b7f9-7137df1b8872 | textbox | Location
6cd69f1f-4470-5cab-b9cb-09ce905de837 | textbox | Lot Number
34207596-8afb-5a92-8c72-4b4ad55528b2 | textbox | Description of Pour
941a6844-f02c-4d7d-be3a-773165d0e9c7 | checkpoint | Issued for Construction Drawings available
93b8815d-f20b-4aab-9ec8-34deb739c9c4 | section | Compaction
c16a8743-1886-4b0c-97ce-8fca8fe7b41a | checkpoint | Compaction Test Taken and Results Attached
7d033bb4-9726-41cb-b13e-64bd446713f7 | section | Construction - Formwork
6a903c99-2bbe-4aef-a71e-49dc24b489bb | checkpoint | Formwork/ Moulds Braced and Secure
cd3ab2b0-9f42-461d-a99e-cb91df69ce43 | checkpoint | Dimensional Check Completed
419ae552-2eb7-4279-8c03-6b1ccee2ed44 | checkpoint | Formwork/ Moulds Within Tolerances
5a25d508-db0e-4426-9462-dedec8ac3b72 | checkpoint | Formwork/ Mould Surfaces in Good Condition
a8236af0-ef60-4533-bab9-2dbb606ff248 | checkpoint | Chamfers in Place as Per IFC/ Shop Drawings
9d26e034-1761-4e93-bf2b-1ef1a92dd985 | checkpoint | Formwork/ Mould Release agent Used
ac4f1491-ebd0-43af-b8a3-cbf4b3621d36 | checkpoint | Construction Joints Allowed For
56453090-51ab-4d69-a0b7-dfa572777233 | checkpoint | Penetrations Set Out as Per IFC/ Shop Drawings
029d6bb3-7e7c-4e6e-8c79-92a6b3a2961e | checkpoint | Cast In Hardware as Per IFC/ Shop Drawings
368d4a89-5a2f-4a47-bc26-4e5212780d2e | checkpoint | Surface Finish Meets Specification
868ff756-3efe-4f07-b594-7d37850097b2 | section | Steel Reinforcing
612bc572-4967-4329-b56b-16ca4dcd2d2e | checkpoint | Reinforcing Braced and Secure
012789ce-6000-49a4-920e-a66d1ddd5647 | checkpoint | Dimensional Checks Completed
98f89ba4-ac45-4090-ac02-ce4102d95053 | checkpoint | Bar Diameters as Per IFC/ Shop Darwings
e7099761-b003-4bbb-8479-fc3fb47a4272 | checkpoint | No. of Bars as Per IFC/ Shop Drawings
2829d24e-c8ef-4f74-aae0-8d54a6f0be8c | checkpoint | Bar Spacings as Per IFC/ SHop Drawings
55629fe6-4333-44c3-a10e-568e1d8c514c | checkpoint | Cover as Per IFC/ Shop Drawings
2c8f5f77-2e19-4fc3-9d66-6df49632280b | checkpoint | Lap Lengths as Per Specifications
d900d51c-38cb-4013-9aa0-019112503621 | checkpoint | Lifting Hardware as Per IFC/ Shop Drawings
1cc857f9-b4ec-4fcb-8c7f-a966a49e0708 | section | Concrete
e01cc0c2-9e89-4ebc-a536-2e20153aab2d | checkpoint | Concrete as Per Approved Mix Design
8a5b0997-ff15-476f-8ec2-3a99e0af2c61 | textbox | Oxide Added
25dd2abf-d468-54e1-8de2-acfcd8d53131 | textbox | Strength Required
354c2d95-fd6e-4cd1-9a5c-669ae501f6a8 | checkpoint | Slump Tests Undertaken
05268cdb-15f7-48c3-910d-fd8c4e5b14d3 | checkpoint | Test Cylinders Taken
58ea518b-b074-4fa8-9fa5-8fc6e425800a | checkpoint | Surface Finish as Per Specifications
82dc4b12-1e00-4631-8095-f683a7a06923 | checkpoint | Construction Joints Allowed For
77f58b44-39ba-4ef6-abdc-5eeb4b1e9a8a | checkpoint | Additional Curing Measures Required
387078fc-5fa3-4040-8fce-8f3dec9a08b8 | checkpoint | Client / Engineer Inspection Required
1d6f9694-3b80-40e5-b182-1d72bbc45ea5 | section | Pre-Pour Checked and Accepted
fdc128ca-5b35-43ad-955c-36ccf4152d75 | checkpoint | Prepour Checked and Inspected
64537df3-7b18-5113-8c45-3f78cbac1a5d | date | Date of Inspection
9651e4ff-722e-41e9-89c6-ccc62aa33ca5 | signoff | Holdpoint
5e4e66db-28c5-4385-a29b-72883c484b33 | checklist | ITP - Wastewater Reticulation Upgrade | itp | ITP - Wastewater Reticulation Upgrade
b847a8c4-ed90-4d41-b501-5b1d2074d28a | section | Preconstruction
4fe935ca-f389-4506-8b96-ab00f577de3b | checkpoint | Precondition Survey
bd66c0ce-e903-5873-9619-d9ab82e0dec7 | note | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.2.2
f559c34a-d32e-5a81-a31c-cee83f78617b | note | TEST/TASK REQUIRED: Visual inspection.
293d9359-9dea-5f7a-ab1b-459ac908a3a3 | note | INSPECTION BY: UCCL
0bcd1806-723b-54fa-823b-d80e8bad99bb | note | TASK TIMING OR TASK FREQUENCY : Prior to starting on site.
85ac4fb7-ce65-5442-8a5f-47c300193322 | note | ○ Survey conducted of all surfaces, footpaths, kerbs, driveways and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works.
b93ae04a-7116-5f57-a157-f9de53a62cad | note | ACCEPTANCE CRITERIA: Survey documents submitted to Engineer.
5480be1a-5b58-41d9-b12a-5fd7da21a823 | checkpoint | Materials Quality
a3cf3166-a365-5fcf-9a40-744752d27f54 | note | SPECIFICATION REFERENCE: FNDC Approved Materials List - Wastewater and Stormwater
ac370e05-2a00-563d-83d5-0e02f714c22c | note | TEST/TASK REQUIRED: Visual check for approved materials, quality and condition.
df1de97a-4fcc-5652-8857-8b10abbd647d | note | INSPECTION BY: UCCL
2252ff34-1b6f-544b-8599-1dc38041bacf | note | TASK TIMING OR TASK FREQUENCY : On arrival to site, prior to using materials.
738524aa-7396-5f54-881b-ea57d2c7a246 | note | ACCEPTANCE CRITERIA: Materials meet specifications or otherwise approved by Engineer.
5ccb10e9-db30-56e1-9f34-a3dc1a3a0f55 | note | ○ Delivery dockets.
735a1a97-dc10-5314-a3a6-57291fe56a61 | note | ○ Photos.
b81c709e-e529-4d3b-9c05-d886dd20e06e | checkpoint | Survey Setout
2e843113-e085-5846-934a-7d3c7cf49b42 | note | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.2.4
3e30c637-594d-58b2-a915-8e0b998114e6 | note | TEST/TASK REQUIRED: Survey set out.
35805cf3-3350-59ce-a883-7b2c2b37a6b6 | note | INSPECTION BY: UCCL
39867e5e-6b50-55fd-a9e6-07fbfc706be0 | note | TASK TIMING OR TASK FREQUENCY : Prior to commencing each stage of work.
a59cf9b9-dfbc-5c36-b09c-72b12c76bade | note | ACCEPTANCE CRITERIA: Survey set out as per IFC drawings.
a2b5c72a-6c94-5393-87ba-646f56671bc9 | note | COMMENTS: Check all MHs for levels, prior to constructing drainage lines, they must verify the inverts and locations of existing manholes as part of the inspection and testing process
eff5c604-77db-466d-b26f-f716ec87cdc2 | section | Installation
a08b5a34-c1a1-4067-b149-5b0b4258ca0b | checkpoint | Service Location
c02bddef-2613-5290-bac6-4f9bad61a617 | note | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.4.2
b5f1566a-c350-5254-ae25-33950d541dca | note | TEST/TASK REQUIRED: Locate underground services within work area.
7481bedf-f7d8-5c30-9c4b-f27148541686 | note | INSPECTION BY: UCCL
42add012-851a-55c8-8fc6-3a764c451d42 | note | TASK TIMING OR TASK FREQUENCY : Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services.
6e8fa7eb-9717-419b-9fe3-b0ee294d3cbf | checkpoint | Material Properties (Bedding)
536d35ee-940e-55f8-ade5-c84d6b19c2b2 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.5.1.9
80a5b32a-b2d8-5bbf-ada5-5e6f81ce7c34 | note | TEST/TASK REQUIRED: AP20 Grading curve to be submitted to Engineer for approval.
4ff17fb8-b538-5603-a729-9622fa816399 | note | INSPECTION BY: UCCL
1bdcdf41-bfdc-5f37-b72e-27c1f5a1c1c0 | note | ○ Haigh Workman
f67105c7-d443-5fba-a02d-04bdfb04247d | note | TASK TIMING OR TASK FREQUENCY : Prior to using bedding material on site.
20f545b0-3b4d-5f40-a881-2216385f3786 | note | ○ PE bedding, pipe surround and haunching shall be AP20 in accordance with AS/NZS 2566.
fda81553-4de7-5cc8-b3e6-6a336372d018 | note | ACCEPTANCE CRITERIA: Bedding grading curve accepted by Engineer.
9f953b3e-161c-4d3c-878c-5225c8da055e | checkpoint | Material Properties (Subbase - AP65)
71bddfc6-773b-53b0-b704-e58597bf33a6 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
1fbca303-3c4b-5fc9-8c1e-1326633fa5ea | note | TEST/TASK REQUIRED: Subbase material meets FNDC Engineering Standards
c57505cc-15e7-5f70-a60b-04d148b4c11f | note | INSPECTION BY: UCCL
e637fc48-c4da-59bd-9d64-024fd4914a18 | note | ○ Haigh Workman
a2003e0a-4f8f-52b6-bd94-a2bbfc57db90 | note | TASK TIMING OR TASK FREQUENCY : Prior to using subbase material on site.
01af1c3e-c159-59ca-9d47-86241038b195 | note | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
a22c3390-90d0-4792-b362-f0046b0d7f59 | checkpoint | Material Properties (Basecourse - AP40)
2bbbdcf8-8183-591a-bda7-74a09e9cbb7a | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
14c80a63-ac5e-5c94-ba72-2859e3c5afc4 | note | TEST/TASK REQUIRED: Bascourse material meets FNDC Engineering Standards
afb969c0-35f7-57c6-b7f4-df08d3296726 | note | INSPECTION BY: UCCL
0ecb82ef-86b7-544a-8846-e976772c8dcc | note | ○ Haigh Workman
db65a52c-934e-5e32-b865-08de4037cd79 | note | TASK TIMING OR TASK FREQUENCY : Prior to using basecourse material on site.
70d4c4c6-0b06-5338-a9a0-056dd639c013 | note | ACCEPTANCE CRITERIA: Basecourse material test certificates accepted by Engineer.
22422f1c-3712-4051-b82c-33181e604198 | checkpoint | Pipe and Rubber Rings
0c1e6815-ab2e-520d-a441-d6e546932fd7 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.8.3
029871ab-10f3-59e0-b86e-f34b3b339e70 | note | TEST/TASK REQUIRED: Visual inspection
53c70e58-5199-5047-bda7-a79f83dce63f | note | INSPECTION BY: UCCL
2744f0a4-81eb-5e32-8eaf-425aac49f954 | note | TASK TIMING OR TASK FREQUENCY : Visual inspection prior to use (clean and free from defects).
318ca5e8-18f1-5f2d-92f0-53db9b9cf301 | note | ACCEPTANCE CRITERIA: Photographs.
bc378fdf-da9f-4c76-b714-750c52e4ab1d | checkpoint | Pipeline Installation (PVC)
749243ee-34b5-5995-b830-9c961f9c2728 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.8 and B.7.9
66f6c4dc-8f42-56c9-8d8c-76e7746b2b07 | note | ○ FNDC Engineering Standards Sheet 31
5506bac0-dae7-5291-a937-2feb26244a2c | note | TEST/TASK REQUIRED: Visual inspection
28ba8c56-70e8-527a-a2d2-f1fe104aa59c | note | ○ Pipeline installed to correct alignment, grade and level
89643c42-3aa2-58a7-8ffd-b74b4d55d079 | note | INSPECTION BY: UCCL
325353b7-be48-5ed4-b9d8-49abee16ae5a | note | TASK TIMING OR TASK FREQUENCY : On completion of installation of each length of pipe, prior to backfilling.
cc1589cc-de19-5a34-88ca-f5a5f3fd5db6 | note | ○ Throughout installation of pipeline.
fb1694a8-72ea-5590-957b-20500a95d4c0 | note | ○ Horizontal alignment +100mm.
8fb38f66-4503-5450-8f3b-1bd9503f8e90 | note | ○ Vertical tolerance +/- 10% of the design grade for each section of pipe.
99459b7c-ae9d-5013-bdd1-451c9c0d33e8 | note | ACCEPTANCE CRITERIA: As-built drawings.
5c9bd0fc-e9d3-5ebf-b24c-2c0f65fed836 | note | ○ Photographs.
84acdcab-881e-4c45-baba-098e3bfed2e0 | checkpoint | Stainless Steel Pipe Bridge
2fe92968-ba0e-59fa-8902-ff8a0cbcc4ff | note | SPECIFICATION REFERENCE: Wastewater Specification 'Package 3 - Bisset - Pipe Bridges Specification
b60ce7d1-f6fb-53ca-9552-99595bd30645 | note | TEST/TASK REQUIRED: Visual inspection
bdcf408e-9054-5a79-95a1-31a9f0576b7f | note | ○ Pipe installed as per specification to correct alignment, grade and level
de517692-06fc-515c-b0b2-067cdeda2c43 | note | INSPECTION BY: UCCL
e0438dde-9acf-5214-9f65-fedab7e3b234 | note | TASK TIMING OR TASK FREQUENCY : On completion of installation of each pipe bridge.
aeb9f2be-401b-5e52-8049-ca2ee6582968 | note | ○ Horizontal alignment + 100mm.
d13082db-b15c-5d11-8b57-37ebc8a3c93e | note | ○ Vertical tolerance +/- 10% of the design grade for each section of pipe.
cc981ce1-3f12-58c4-ba80-7934a9ab4e15 | note | ACCEPTANCE CRITERIA: As-built drawings.
423cbc19-c15e-50b9-8ebb-629bd83556b8 | note | ○ Photographs.
7a3bbbe8-d950-4bc0-9020-4f0dc84a99af | checkpoint | Manhole Installation and Backfill
5f26376c-6144-519b-a051-7f9e9822f58c | note | SPECIFICATION REFERENCE: Wastewater specification B.7.9
cd2637e4-e6b8-55e2-b900-8e0ddbef0332 | note | TEST/TASK REQUIRED: Visual inspection.
82c1a646-2d7d-5bc4-8f56-3ecb43c44b85 | note | ○ Manhole checks including position, haunching, steps and sealed joints.
c11d4c1b-4710-5096-a005-89846838fa9e | note | INSPECTION BY: UCCL
ce4fe9c4-2851-5757-8b8e-445ccaff928a | note | TASK TIMING OR TASK FREQUENCY : On completion of manhole installation.
0a837178-26e9-549b-ba04-36c6f089a8dc | note | ACCEPTANCE CRITERIA: Falls through manholes are to be within +5mm of design levels.
d74722e4-df09-59b6-8962-0f4e15144cf3 | note | ○ Maximum deviation from vertical (manholes/chambers) shall be 10mm per metre.
4e59abb2-02e6-483b-8ec0-5b6894163948 | checkpoint | Pipe Bedding
6542f910-b71d-57c3-a734-17b3db6de290 | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.4.1
d11a9348-97c0-5c95-becc-71c37d75bb52 | note | ○ FNDC Engineering Standards Sheet 31
2411d266-892c-5777-a721-2f6d0fcc089d | note | TEST/TASK REQUIRED: Visual inspection.
da5e670c-b628-5cb8-a71a-f9e83a2c794d | note | ○ Compaction test on top of bedding.
7b0fcc35-e1b7-5d59-9249-a0ac762792fc | note | INSPECTION BY: UCCL
ee410fae-81a0-5829-9842-4d189de6f810 | note | TASK TIMING OR TASK FREQUENCY : Bedding installed as per specifications.
3ef67abe-3390-569a-b15a-2f1d4375cc7d | note | ACCEPTANCE CRITERIA: Photographs.
b18222b6-73bd-56f5-b0a3-b63083b63ed4 | note | ○ Compaction test results.
0a8ec505-ba0b-4db6-91a6-4e931c6b7b24 | checkpoint | Pipe Backfill (Outside of Carriageway)
48228d76-72bc-5f48-851f-3770220625f7 | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.6.3
891c4bf5-f1e1-507f-899e-aee23eaa01bf | note | ○ FNDC Engineering Standards Sheet 31
21ab72df-b4db-55e1-8306-7ec7353ba42f | note | TEST/TASK REQUIRED: Visual inspection.
875e2757-7e66-5e56-b896-5463bf3a41d9 | note | ○ Compaction test on top of GAP65.
2d4af9e6-9237-5f58-9192-aa1fbdd89c80 | note | INSPECTION BY: UCCL
9388d803-7443-5dc7-af2d-55a321be59ed | note | TASK TIMING OR TASK FREQUENCY : On completion of GAP65 layer.
d81fea9b-b94b-537b-8387-995b6db8fde2 | note | ○ On completion of ordinary backfill.
390e27cb-b2e5-5998-8bc2-a071f31985e3 | note | ACCEPTANCE CRITERIA: Photographs.
4e37bf94-d58c-5503-b7a0-4716d953a1e2 | note | ○ Compaction test results.
5db2b47d-e676-4784-9f0c-8ae910d7c694 | checkpoint | Subbase
5a445aeb-f7a0-5a30-aace-f84c30c7e4ec | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.6 and B.3.7
3d52e053-11f7-557f-9cd2-659156b1dc4a | note | ○ FNDC Engineering Standards 3.3.3.3 and Sheet 31
6d3c8178-ba7a-514e-adb9-ff88e7653c4f | note | TEST/TASK REQUIRED: Visual inspection
19861efe-0c99-50da-8dee-6545b4cc622d | note | ○ NDM testing
74b256a3-a7d0-527f-bba9-5e4623980e6c | note | INSPECTION BY: UCCL
76a6e342-acf1-53cd-96ad-65857e45e446 | note | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of subbase layer, prior to installing basecourse.
2ad91036-e2e7-5f16-a04e-c27a20efb9d4 | note | ○ Backfill and compaction completed as per specifications.
19ba96bf-544d-5f79-9368-1452dc297f86 | note | ACCEPTANCE CRITERIA: Compaction records.
dcde4283-8680-5cae-abe3-f5d1e87da129 | note | ○ Photographs.
0220ab7a-2724-4d70-a90b-7be790bf6f47 | checkpoint | Basecourse
3001dcea-0ddd-5812-9c38-39ece578e501 | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.6.2
f936b9e9-8641-5bfc-8f46-fd6bf31da307 | note | ○ FNDC Engineering Standards 3.3.3.4 and Sheet 31
e3e53da3-8a99-581d-b1f4-2bd6eb61c887 | note | TEST/TASK REQUIRED: Visual inspection
63c4dfe8-30ca-5890-9f6f-a951e6aa3502 | note | ○ NDM testing
42c0d5a6-9bb0-53a2-ad11-5f4a406a765f | note | INSPECTION BY: UCCL
ccce277e-10f9-5856-95c2-2ff5a4d32c12 | note | ○ Haigh Workman
d405cb00-2244-5022-b84b-49a2225f20ad | note | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of basecourse layer, prior to sealing.
386d9fb8-3e56-5984-b250-53b604c35211 | note | ○ Basecourse installed as per FNDC Engineering Standards, and NZTA B/02.
4ee7bc09-6ccc-52ac-9b5f-7201be0cab3a | note | ACCEPTANCE CRITERIA: Compaction records.
9545072e-585c-5f44-80ac-893b493cf8d3 | note | ○ Photographs.
bfc3d791-d767-421b-a2c9-1ef933ba7b2b | signoff | HOLD POINT
9eed3e82-7318-425a-bcf7-e693dc323ad0 | checkpoint | Detection Tape
d6fee34e-a693-5cd5-ad90-1c2c112e2812 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.5.1.6
aaad6024-cce3-5bdd-97ff-6af3da2ee1e8 | note | ○ FNDC Engineering Standards 5.3.3.1.2
8fd4b92a-6e92-5ef8-b73d-dcbf40f8b7d7 | note | TEST/TASK REQUIRED: Visual inspection
b17f35fe-532c-536a-b800-eb97a845262e | note | INSPECTION BY: UCCL
5d91a7b7-f5e0-546c-8f5a-3a1da86a8ba0 | note | TASK TIMING OR TASK FREQUENCY : "Sewerage" detection tape laid directly above all wastewater pipelines.
ba20a863-0096-5e46-aaaf-53f72e6a4753 | note | ACCEPTANCE CRITERIA: Photographs.
e3376aea-9613-4273-903b-d0cd0b03c41c | checkpoint | Pipeline Testing
31c1dd6c-bc02-5507-8db2-0b5fc4e6422d | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.9.1
573b5ebb-3a2d-5074-adb6-dd13603de5bd | note | TEST/TASK REQUIRED: Air test
cf0386e4-995b-5282-9e5f-b167f65f00cf | note | INSPECTION BY: UCCL
c3dcebbe-889f-5bbd-8183-7f8745abd11a | note | ○ Haigh Workman
d35d735e-e6f4-58f0-8274-b2445fc8aebf | note | TASK TIMING OR TASK FREQUENCY : Each section of pipeline is to be tested by 'Air Test', including Lunden junctions.
401ac030-cd03-5e6a-a6b1-7ed3ce1ccacf | note | ACCEPTANCE CRITERIA: Drop in pressure shall not exceed 25mm over a period of 5 minutes.
ca645913-0faa-4512-9674-ccd47b6f4408 | signoff | HOLD POINT
99c025c8-db94-4494-bae4-1b29f9090cde | checkpoint | Manhole Testing
4a715836-95e6-5f4e-b062-d018f092fc58 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.9.1
2962de14-4fdb-5722-b778-0b71f71d5c9d | note | TEST/TASK REQUIRED: Visual inspection.
338bc316-41cf-5e83-b161-1972dee95bd1 | note | ○ Water test.
20b9be33-671f-5c15-a1b1-dfd9b6e364b2 | note | INSPECTION BY: UCCL
cf4f00bd-5787-5f67-ab4c-b96d9331fb42 | note | TASK TIMING OR TASK FREQUENCY : Visual inspection of each manhole prior to backfilling.
b073a74e-a368-524e-8ddd-efc6a2154833 | note | ○ Water test after backfill.
8106f2d0-051f-5789-9ee8-7df50c9d967a | note | ACCEPTANCE CRITERIA: Drop in level shall not exceed 5mm in 10 minutes.
ea6706bf-e28e-4dca-a710-5fa988d99000 | signoff | HOLD POINT
a11c4627-09ba-419d-974a-b3eeacab669c | checkpoint | Wastewater House Connections
a968e89e-1105-5b01-be2f-dd0166b58905 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.8.10
9054dc0a-0e16-554c-9525-609b3721ccb2 | note | TEST/TASK REQUIRED: Visual inspection.
462d83e3-54b1-5b4e-ab16-608961301ad5 | note | ○ Survey.
a76a22bd-d66f-5661-9f5a-d3c963eb103a | note | INSPECTION BY: UCCL
06ab8b88-5cd0-5fa8-a34c-cde9659c6734 | note | TASK TIMING OR TASK FREQUENCY : On completion of each connection.
7a173ba6-109f-5757-bdd3-57dea0dede04 | note | ACCEPTANCE CRITERIA: Photographs.
832d037e-4550-58e6-a9ea-828b8d1cf6e7 | note | ○ As-built drawings.
d14c90af-2d85-46e4-b008-bf6928032ccc | checkpoint | Reinstate Driveways
03d82803-d499-50cd-9dbe-5b33d94d8571 | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.8.5
2488e35e-a4bf-5ae2-9c37-4cdbd315dd23 | note | TEST/TASK REQUIRED: Visual inspection
c75cff61-d89c-557c-a8f4-e24761a92b73 | note | INSPECTION BY: UCCL
4ce6edce-9e82-53f9-9d4c-7c134080ca51 | note | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
62077835-461d-5f14-b5eb-07b11880900d | note | ○ Driveways reinstated in the same material and to the same standard as existing prior to works.
edc5db91-80d6-514c-a1c3-6a57ecb7ef2a | note | ACCEPTANCE CRITERIA: Photographs.
28bca8b0-62db-4b75-a8f2-a701bf60c263 | checkpoint | Reinstate Footpaths
2df11296-f6e0-5ade-8831-fafcd4df401c | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.8.5
32dedfe0-401f-5562-a007-bc3605ec14c7 | note | TEST/TASK REQUIRED: Visual inspection
61c02b3d-f849-5946-bcae-d0dc6b58ef89 | note | INSPECTION BY: UCCL
77fb6831-ac6e-5306-83d7-13f52a68db95 | note | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
99adc8a7-4e0a-5f00-b5fd-d8cb3657a8cd | note | ○ Footpaths reinstated in the same material and dimensions as existing footpath, and constructed to FNDC Standards.
fcab2043-1863-5d73-bdb8-daca1821bfbb | note | ACCEPTANCE CRITERIA: Photographs.
f334a94a-8fa2-4657-abd2-d01627556dae | checkpoint | Reinstate Kerb and Channel
f340eb37-eac9-583c-9116-5ac5d9ae8a0a | note | SPECIFICATION REFERENCE: Wastewater Specification B.8.5
f9033f89-b3a3-52df-a955-db6dc78655f1 | note | TEST/TASK REQUIRED: Visual inspection
c9ebed99-f029-54a9-9284-2b74740a3fca | note | INSPECTION BY: UCCL
60e296e4-b0df-52a0-999f-8e9e249fcf40 | note | TASK TIMING OR TASK FREQUENCY : Kerb and channel profiles match existing.
f771ba8e-3629-5769-9bc3-9421bac3ec94 | note | ○ Concrete has minimum 28-day strength of 25MPa.
feae7d67-3040-5934-9aa0-4cc3c5e9ec1d | note | ACCEPTANCE CRITERIA: Photographs.
c03f8494-8a9d-4440-b2e9-1073895e2d11 | checkpoint | Concrete Pour
91dccf55-7c3b-5162-a1a3-ca1111057222 | note | SPECIFICATION REFERENCE: Wastewater Specification B.4.4.2
7d595de0-0c7e-58e6-83fc-908b80aba36c | note | TEST/TASK REQUIRED: Prepour inspection
71e900bc-e2ec-5427-a58d-5a05d7c6d847 | note | INSPECTION BY: UCCL
44c42b60-ccea-5b35-b503-3d83a02a3f6b | note | ○ Haigh Workman
ca2670dc-6056-530c-823e-cf931772f9f6 | note | TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete.
099cbc4d-3ad5-5082-bafd-9f88c30b8b7a | note | ACCEPTANCE CRITERIA: Pre-pour inspection checklist.
e27128f4-251d-5a5d-9c35-02135460cd76 | note | ○ Photographs.
f7ada8db-2ce9-42c8-aa87-8d4c3c5d7511 | checkpoint | Asphaltic Concrete Layer (DG10)
94a44cfb-1a8b-5acb-b9ca-e3b2e4f99e51 | note | SPECIFICATION REFERENCE: NZTA M10 Specification
e0bf0021-7a74-51b3-b8d9-93e6667591fe | note | TEST/TASK REQUIRED: As per NZTA M10 Specification
e56a7889-a825-5e49-8143-22f33b47a914 | note | INSPECTION BY: UCCL
0cb0849a-8554-592f-85b4-6c518bc32d90 | note | TASK TIMING OR TASK FREQUENCY : On completion of the pavement surface.
25765812-775a-52c1-9d34-3045870d68bb | note | ACCEPTANCE CRITERIA: Test results submitted to Engineer.
0cc452c4-7e40-5f3b-8a36-e7e8a97840e2 | note | ○ Photographs.
a753b28c-100f-4114-a17a-e8ff6d45b641 | section | Post Construction
0e6a036d-3190-4368-8940-cb51166bd55d | checkpoint | As-Built Drawings
e1b9af54-7983-559a-b25c-16fc57a861c5 | note | SPECIFICATION REFERENCE: Wastewater Specification B.2.18.1
37c186ab-1dec-5186-bc0e-203f61f5fbd3 | note | TEST/TASK REQUIRED: As-built records and coordinate data
08440565-fcf9-51f5-a00a-3eb3a038f364 | note | INSPECTION BY: UCCL
c65659af-49a0-5a0f-b910-fdcb6b4f6cab | note | TASK TIMING OR TASK FREQUENCY : Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion.
fb5865aa-16f8-541a-b77d-6dd450e0cac3 | note | ○ Final as-builts issued prior to Final Completion.
89a51099-025c-5e67-a8c0-8d281cef24b8 | note | ACCEPTANCE CRITERIA: As-builts submitted to the Engineer for approval.
d02b0afc-712e-4ddc-9bbd-2b43bb42dae2 | checkpoint | CCTV
1caea204-bee6-52f6-abdc-1d8326ec4f49 | note | SPECIFICATION REFERENCE: Wastewater Specification B.2.18.2
d72523d9-b0ab-5f89-818d-7b26fd5d1c4d | note | TEST/TASK REQUIRED: CCTV video survey to the National Standards
f32162ef-3801-56da-8bff-e34fd6f66be2 | note | INSPECTION BY: UCCL
8e746ac0-363e-5995-84da-efa82d7e3f07 | note | TASK TIMING OR TASK FREQUENCY : On completion of the installation of each pipeline with backfill to the top of the pipe.
942eab34-e40b-5faf-aff2-4ba2134119fe | note | ACCEPTANCE CRITERIA: CCTV results submitted to Engineer for approval.
a2f1d806-93c8-4c51-8b1c-68b3bf42e925 | checkpoint | RAMM Information
7a0ec8b6-c11d-55d9-b549-a8ceb636c46c | note | SPECIFICATION REFERENCE: Wastewater Specifcation B.2.18.3
fe731bd0-d052-5b7c-92bc-35f1ffaa5e4a | note | TEST/TASK REQUIRED: RAMM information
51cee11a-e294-5613-80a5-2c8d4cef4c97 | note | INSPECTION BY: UCCL
373be550-9e5f-5eb7-959c-587a940906d4 | note | TASK TIMING OR TASK FREQUENCY : RAMM information submitted to the Engineer on completion of works.
c241db5b-10b3-56b3-85c1-6577e95a65ca | note | ACCEPTANCE CRITERIA: RAMM information submitted to the Engineer.
ed6cc460-ac9e-4eff-93ee-ec2affcdc29b | checklist | ITP - Water Reticuation | itp | ITP - Water Reticuation
c99ae8fd-074c-43b9-bf73-fc0fabd4c9f5 | section | Preconstruction
1fb82105-91e6-41a6-b8bf-972ca3a2061c | checkpoint | Precondition Survey
845fac82-7fea-5366-8599-9bffcbb1b3ff | note | SPECIFICATION REFERENCE: Water Specification B.2.11.2.2
5b231f43-a8ba-55c8-8ff5-d032ee20e393 | note | TEST/TASK REQUIRED: Visual inspection
b8d89ab6-f4cd-529b-a581-9dae213db4a0 | note | INSPECTION BY: UCCL
75036255-26c5-5d06-92cf-fbb09694b4b2 | note | TASK TIMING OR TASK FREQUENCY : Prior to starting on site.
95d97d7e-aaf2-5fae-aafd-dac6e0702775 | note | ○ Survey conducted of all surfaces and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works.
007ae91e-c560-5cef-9fb8-d366c485fccb | note | ACCEPTANCE CRITERIA: Survey documents submitted to Engineer.
686b7475-7366-41d9-87cd-984bcbe9b1d0 | checkpoint | Materials Quality
ad7fec6b-5240-5956-a854-8baf0de219b9 | note | SPECIFICATION REFERENCE: FNDC Approved Materials List - Water Services
dcf853e2-ed9c-508a-86e5-440caf41b7ef | note | TEST/TASK REQUIRED: Visual check for approved materials, quality and condition.
5a5825f1-c7a1-5aea-aa20-69f8d0499a49 | note | INSPECTION BY: UCCL
8c089a9b-a39c-5bf1-b529-f1ff7f2d80f4 | note | TASK TIMING OR TASK FREQUENCY : On arrival to site, prior to using materials.
bb8d2e08-d396-5444-b420-6d28fa75f44d | note | ACCEPTANCE CRITERIA: Materials meet specifications or otherwise approved by Engineer.
17fd7059-05fb-517d-87e6-5b86f760dee3 | note | ○ Delivery dockets.
1c37c735-4658-5389-b26b-831e73d75c4b | note | ○ Photos.
2221bce0-50ff-43a7-9ded-bd650c2907b2 | checkpoint | Survey Setout
1da70ff8-a83b-526c-bde1-b5d63c558480 | note | SPECIFICATION REFERENCE: Water Specification B.2.11.2.4
9d02915b-5a93-5e32-b51e-90f5b94d292e | note | TEST/TASK REQUIRED: Survey set out.
c3479be1-bc74-56ed-a47b-362dc1098678 | note | INSPECTION BY: UCCL
759025ce-8b5e-5d1c-b713-b238d6260bd8 | note | TASK TIMING OR TASK FREQUENCY : Prior to commencing each stage of work.
135aa476-ef8c-5935-af2a-daffa9169462 | note | ○ Engineer to be notified if any concerns
5844cd2a-58ba-5804-b30d-40ac9d445ce5 | note | ACCEPTANCE CRITERIA: Survey set out as per IFC drawings.
20480e7f-a136-4664-a9df-a40ab467352b | checkpoint | Service Location
01ba9c58-6cf4-50e9-95d0-a18b14fa7e08 | note | SPECIFICATION REFERENCE: Water Specification B.2.11.4.2
c150305c-0deb-574f-8fba-d72786acef4a | note | TEST/TASK REQUIRED: Locate underground services within work area.
b4aafe7b-a78d-51de-ae06-cb5f4ec7c349 | note | INSPECTION BY: UCCL
bb26e057-af88-5673-b83d-e3a5a2c91c6f | note | TASK TIMING OR TASK FREQUENCY : Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services.
4b506942-8585-5ccd-8453-a18727788aa0 | note | ACCEPTANCE CRITERIA:
3bafc20e-fc38-4102-9a8d-67b4de0461ad | section | Installation
5aa0b962-8fc3-4c8b-b7de-5a08d2324274 | checkpoint | Material Properties (Bedding)
2e46aa5f-5399-53c6-8ea7-f1e2439750fc | note | SPECIFICATION REFERENCE: Water Specification B.5.5.1.13
a50b9401-5ff4-595b-9252-d47de78dc2fc | note | TEST/TASK REQUIRED: GAP20 grading curve to be submitted to Engineer for approval
adaec7a2-de12-56cd-b48f-16610f561aaf | note | INSPECTION BY: UCCL
3f58d0ad-6fc6-5ea0-8e3d-1d7fe63b925c | note | ○ Haigh Workman
b4459f87-1776-5531-8cdf-0ca8cf744be7 | note | TASK TIMING OR TASK FREQUENCY : Prior to using bedding material on site.
8cff7680-6601-59b9-8149-d2bf77b4235d | note | ○ PE bedding, pipe surround and haunching shall be GAP20 in accordance with AS/NZS 2566.
3710be17-f406-5f05-946b-7262fbdd58c0 | note | ACCEPTANCE CRITERIA: Bedding grading curve accepted by Engineer.
36fea487-4001-4231-9c02-d50f7731c287 | checkpoint | Material Properties (Subbase)
452c8aec-ae02-5136-b09b-95cf8146d271 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
114def64-700b-5088-b3d8-9a2c52da53eb | note | TEST/TASK REQUIRED: Subbase material meets FNDC Engineering Standards
215bd4b8-df09-5777-a28a-2cdd19cfb0c9 | note | INSPECTION BY: UCCL
586ae9e2-1696-5ee9-8c02-87ea0bfe4f51 | note | ○ Haigh Workman
3e0175f6-fa74-5c96-b723-1971d840c087 | note | TASK TIMING OR TASK FREQUENCY : Prior to using subbase material on site.
d0610e90-7675-57b1-9148-652b8d9b0ec1 | note | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
1756e81c-c7a0-4933-a7bb-848241d41ffd | checkpoint | Material Properties (Basecourse)
60863e98-16ae-51be-bd0e-ca8d5fe6c2da | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
33817821-ae38-5b67-9672-657745d656cb | note | TEST/TASK REQUIRED: Basecourse material meets FNDC Engineering Standards
d759e3e4-42c1-527a-9bd0-dd68fed17eb8 | note | INSPECTION BY: UCCL
abc577b8-d353-5998-8b7e-78efb912a089 | note | ○ Haigh Workman
5fbd3687-f4b2-5268-bf2c-8b553c179fcc | note | TASK TIMING OR TASK FREQUENCY : Prior to using basecourse material on site.
df4d7fd0-8e18-5a34-9fa3-77bc6d6f0c71 | note | ACCEPTANCE CRITERIA: Basecourse material test certificates accepted by Engineer.
6694e172-3d1c-46d2-945d-2d03d00cb6bd | checkpoint | Pipe
06a32790-7a1b-54f8-b374-3cf534a1def0 | note | SPECIFICATION REFERENCE: Water Specification B.5.8.3
07c3fe25-47b3-53f7-a4f5-fbe82ada175b | note | TEST/TASK REQUIRED: Visual inspection
15ed7b3e-a2a0-536f-88d5-b895da8dd60c | note | INSPECTION BY: UCCL
0840673d-a901-54b3-a47a-10c640145f33 | note | TASK TIMING OR TASK FREQUENCY : Visual inspection prior to use (clean and free from defects).
7d579e27-5c7e-5ac7-8254-38e0fe91401a | note | ACCEPTANCE CRITERIA: Photographs.
24ee523b-375b-431e-80b8-13b9a2894ac6 | checkpoint | Test Welds (Butt Welding)
978ed83a-fe46-5fd4-9ad5-fd57dab2fcfd | note | SPECIFICATION REFERENCE: Water Specification B.5.10.2.2
0a60a3e1-4844-59b0-9379-309e6c771c27 | note | TEST/TASK REQUIRED: Laboratory testing
244940d2-4c51-5341-94d6-ca586f30d386 | note | INSPECTION BY: UCCL
8f089677-da87-576b-9177-912478b31965 | note | ○ Haigh Workman
25de6d57-89e6-593b-a97c-992b8ec5aa42 | note | TASK TIMING OR TASK FREQUENCY : Three butt welded joints and one section of virgin pipe shall be tested in accordance with ISO 13953.
85a516fa-4006-5b98-b86e-1d894368e848 | note | ○ One test weld for every 10 lengths of pipe laid.
35c481fe-b142-5245-89b4-544f19d62032 | note | ACCEPTANCE CRITERIA: Weld test results submitted to Engineer.
689c61ca-4c0f-4532-91c9-8f8ddcc92b6e | checkpoint | Welded Joints (Butt Welding)
13751480-ae35-5fb2-b516-d35ba16fc767 | note | SPECIFICATION REFERENCE: Water Specification B.5.10.2.1
ce36c2f4-6d45-5f87-b46b-61d771dc89aa | note | TEST/TASK REQUIRED: Visual inspection
4ff61144-edde-5222-b605-53cdb6a594df | note | INSPECTION BY: UCCL
476a4616-54c9-597f-9ea5-143ddb4e2e4f | note | TASK TIMING OR TASK FREQUENCY : On completion of each butt weld.
01021c8d-2336-52d9-a2af-abe290a3a361 | note | ○ Weld inspection checklist.
145f4130-f4af-5c8c-9819-c107e8ee41b3 | note | ○ Weld data log.
1319dd5c-456e-5791-bb46-17dfe3136f19 | note | ACCEPTANCE CRITERIA: Weld inspection checklist submitted for each butt weld.
0b9291b7-28be-592d-873d-199579e7a7a1 | note | ○ Weld data log submitted for each weld.
ffb37357-5ab4-4c45-a537-8f4229d4be28 | checkpoint | Welded Joints (EF Welding)
06447b36-b181-5d6e-9321-53c1ef44d5cd | note | SPECIFICATION REFERENCE: Water Specification B.5.10.2.1
74eec366-d184-50ff-ac22-bed7f317695d | note | TEST/TASK REQUIRED: Visual inspection
2285d7b8-d9b3-5b05-87fb-6c0b53582cd3 | note | INSPECTION BY: UCCL
dfce0c0f-0034-5b0d-ae1e-11e9658c4676 | note | TASK TIMING OR TASK FREQUENCY : On completion of each EF weld.
bcee6051-5dc3-5cb6-92f0-02a3d0483dbd | note | ○ Weld inspection checklist.
c4cef3ee-a6fc-5ea6-865c-abe63e5d8e21 | note | ACCEPTANCE CRITERIA: Weld inspection checklist submitted for each EF weld.
61fd87fb-60cc-4f61-9b3d-7e889b4bd36a | checkpoint | Pipeline Installation (PE)
06d77b32-dc0d-54f0-8d7b-b2e4277a9303 | note | SPECIFICATION REFERENCE: Water Specification B.6.4.5 and B.6.4.6
f920959e-ec78-59e0-98c8-ef3813d97ac7 | note | TEST/TASK REQUIRED: Visual inspection
c7f9c317-fd95-52cd-b1b4-0bb7020b5628 | note | ○ Pipeline installed to correct alignment, grade and level
bef2f3da-65bd-5370-8448-1ba9d5d2732d | note | INSPECTION BY: UCCL
673925d7-a66a-5d90-b7ad-cc57c4ff25b1 | note | TASK TIMING OR TASK FREQUENCY : On completion of installation of each length of pipe, prior to backfilling.
e02f6f26-46c6-5a1e-b424-beaa511c29b1 | note | ○ Horizontal alignment tolerance + 100mm.
29160c39-4b8f-55b2-b7eb-07320ef1eccd | note | ○ Vertical alignment tolerance + 100mm.
ae70c0da-e02c-5e8f-b70f-f3b48b492707 | note | ○ Valves on centreline of pipe permissible vertical deviation of +50mm.
4c142f3a-61f6-5c71-9941-47be9385032d | note | ACCEPTANCE CRITERIA: As-built drawings.
8422a77e-a249-5c1c-bc2c-327b57bdf49f | note | ○ Photographs.
a51bc7ea-39d2-5540-845b-997bd6f9315b | note | ○ Changes to horizontal or vertical alignment to be agreed with Engineer pror
1f6c404c-b682-4648-b561-aba47aba65ab | checkpoint | Valve Installation (including Chambers if required)
c5a0d313-124b-549b-9748-1445512a127f | note | SPECIFICATION REFERENCE: Water Specification B.5.8.4 and B.5.9
a65476ca-7f85-5c08-bded-23ed81d46def | note | ○ FNDC Engineering Standards 6.2.8
db602973-9b5c-5c76-8d93-5039f9d1ff4f | note | TEST/TASK REQUIRED: Visual inspection
a8a71081-fb1c-51c2-8ed7-d4e5c77e8afc | note | INSPECTION BY: UCCL
79454c71-4cf5-5441-af66-08a658be74b0 | note | TASK TIMING OR TASK FREQUENCY : Installed as per specifications.
e47d476e-ebb5-5ab9-9f79-3cd44af35aeb | note | ACCEPTANCE CRITERIA: Photographs.
31a06a15-f1ea-547c-8bb9-bfca0a50733f | note | ○ As-built drawings.
6923020b-778d-4f36-9d73-fd57ab0d168b | checkpoint | Valve Boxes and Markings
102bd963-2b13-5e6b-9f58-a9d49f8c1a92 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.2.8.5, and Sheet 48
9db768b7-de69-530b-a11b-f6daeaa6852e | note | TEST/TASK REQUIRED: Visual inspection
32790ba7-07d7-5325-8d94-c225aed468eb | note | INSPECTION BY: UCCL
5d39fd5f-b3cc-5639-8c29-30402c21d266 | note | TASK TIMING OR TASK FREQUENCY : On completion of installation.
958b6913-6e56-5f2b-bf54-47d52d7a3e1a | note | ○ Valve marker posts and kerb markings as per FNDC standard.
dc9a8da5-75df-528a-938a-f7d4e294c31a | note | ACCEPTANCE CRITERIA: Photographs.
f1e87706-b5dc-42a1-8334-e08aa36c2a51 | checkpoint | Hydrants
36ba94e3-1513-5541-9af1-6abda7b69d4e | note | SPECIFICATION REFERENCE: Water Specifcation B.5.8.4
ffc563ed-a314-5385-8c72-99e2dff43b80 | note | ○ FNDC Engineering Standards 6.2.9.1
43be9a44-15a4-5919-8f2e-eb5f0e173bd5 | note | TEST/TASK REQUIRED: Visual inspection
854f125b-1dc5-5f5e-a4f3-476844820555 | note | INSPECTION BY: UCCL
3caeabba-3229-5681-b36f-2ea69c9309eb | note | TASK TIMING OR TASK FREQUENCY : Installed as per specificationsand IFC drawings.
e90fa78e-4b34-57fe-9ea1-254c3a0ce742 | note | ACCEPTANCE CRITERIA: Photographs.
9e91129e-8d18-541f-80b9-7b623a43c4da | note | ○ As-built drawings.
6904223d-9fbb-4929-9e99-1305ef3bc4b3 | checkpoint | Hydrant Boxes and Markings
6ad88165-8584-588f-956f-62f97d0d1b8f | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.2.9.3, and Sheet 48
7d6c7dde-7ec5-538c-b226-83be4c7370fa | note | TEST/TASK REQUIRED: Visual inspection
5de38c6f-44c2-5274-919f-e9ee194ed450 | note | INSPECTION BY: UCCL
bfd6888e-ff17-51b6-b811-7ec11c8053eb | note | TASK TIMING OR TASK FREQUENCY : On completion of installation.
8cb28e5c-48ba-57f8-8109-ff15c0fccdfe | note | ○ Hydrant marker posts and kerb markings as per FNDC standard.
b6c06a88-c741-564a-bc4c-6a0381436d3a | note | ACCEPTANCE CRITERIA: Photographs.
d534b51c-af03-4ebf-b06b-ed31e3022214 | checkpoint | Air Release Valves
8fd4e6bf-b5f8-51f7-8ff0-865e3b695519 | note | SPECIFICATION REFERENCE: Water Specifcation B.5.5.1.11
3476974b-9b4f-56bc-888e-67a6f2778e94 | note | ○ FNDC Engineering Standards Sheet 51
7bda0259-5671-585d-9dcd-0cc87abaf8cf | note | TEST/TASK REQUIRED: Visual inspection
634a1ec2-4724-5a24-9676-357a2978267e | note | INSPECTION BY: UCCL
770bb539-e4ed-5b51-b8aa-3263f83d5819 | note | TASK TIMING OR TASK FREQUENCY : On completion of installation.
cd45e37a-3687-589c-9c12-dbcbafb21698 | note | ○ Air valves installed to specification
623c5c39-af5e-5e11-b8d8-0edac3eb91aa | note | ACCEPTANCE CRITERIA: Photographs.
e8483ca2-3ce6-5ec2-8941-9889e005b601 | note | ○ As-built drawings.
dbde0589-fc0e-4483-817a-a89889a1699c | checkpoint | Thrust Blocks
ee0362a8-63dd-5f2d-83bf-77e6c0b24783 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.2.3.8, and Sheet 50
54b59261-15b4-5948-9c18-9cfc92570c55 | note | TEST/TASK REQUIRED: Visual inspection
9dc16f4d-bad9-5a54-9e40-b5e0bbdb1589 | note | INSPECTION BY: UCCL
a08fd3af-d7cb-5dd2-b28f-9248730a51c8 | note | TASK TIMING OR TASK FREQUENCY : On completion of the thrust block installation, prior to backfilling.
6269d21d-67f8-5f83-8f00-0851bf7ecf43 | note | ACCEPTANCE CRITERIA: Photographs.
2f58fccf-6c17-4b29-892c-f549b3a1c6fc | checkpoint | Pipe Bedding
802ac9cf-e234-560d-a69e-ea8d59967df4 | note | SPECIFICATION REFERENCE: Water Specification B.3.4.1
960576ed-7924-51f5-bc18-048f69cff3a4 | note | ○ FNDC Engineering Standards Sheet 31
b02995e5-639b-5a2e-9083-2dbdb3c04c56 | note | TEST/TASK REQUIRED: Visual inspection
63c21588-6d8d-555c-8f42-c8d98fd644e7 | note | INSPECTION BY: UCCL
e223787c-490f-5451-b9f4-ef704d39f1e7 | note | TASK TIMING OR TASK FREQUENCY : Bedding installed as per specifications.
fc50cc7b-58ee-5169-97df-d097aabee4d9 | note | ACCEPTANCE CRITERIA: Photographs.
ed2f5e6f-f8f9-455c-bac4-d5c2ef066c3a | checkpoint | Pipe Backfill (Outside of Carriageway)
9f9a3ec7-9e90-5dc1-9c11-575ce76a5040 | note | SPECIFICATION REFERENCE: Water Specification B.3.3.2
f2478267-3230-526c-a5ff-39a529185f1d | note | TEST/TASK REQUIRED: Visual inspection
4d53c71f-15e2-5e78-8e2b-bc19a9d5f3e4 | note | INSPECTION BY: UCCL
5b03035a-d8e1-5158-9cec-4896d7593354 | note | TASK TIMING OR TASK FREQUENCY : On completion of backfill.
977a08d1-6a9e-5987-9af4-b73300472281 | note | ○ Trench backfilled with original sound material from the trench.
1d5c9ef3-d6d0-5e7e-8f01-72c48b6c0375 | note | ACCEPTANCE CRITERIA: Photographs.
f5dd5307-6312-4eb7-acac-874ff555a6e9 | checkpoint | Subbase
8abcb380-b7f9-5b05-8bd8-b2aec4c61b92 | note | SPECIFICATION REFERENCE: Water Specification B.3.5.2
93c4b7d8-a8b4-51e8-8ec5-bde33459a346 | note | ○ FNDC Engineering Standards 3.3.3.3 and Sheet 31
cb414140-bfdb-5f8c-8f0b-1a4afaf84225 | note | TEST/TASK REQUIRED: Visual inspection
b33a9f2f-8008-5446-a989-d6a2cb45c881 | note | ○ NDM testing
da42b502-ff75-57fb-a99a-0b78be089bd3 | note | INSPECTION BY: UCCL
b0a8aff6-c48c-5333-b6b4-39e11fdcd0a7 | note | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of subbase layer, prior to installing basecourse.
d1c47ff5-03a5-5e07-9a72-a69a0b3af09a | note | ○ Backfill and compaction completed as per specifications.
86377d3f-4eb0-58ee-8a16-9b2f501f15eb | note | ACCEPTANCE CRITERIA: Compaction records.
fe0eea5d-680d-528d-ab9c-7cfae20196c7 | note | ○ Photographs.
f2ae13db-12aa-4a38-8a4f-39070d63ba10 | checkpoint | Basecourse
8185ce8a-4353-51e9-867b-e7e20fc56797 | note | SPECIFICATION REFERENCE: Water Specification B.3.5.2
49abcf0c-3f5f-52ea-bc6d-b135fa3d04b5 | note | ○ FNDC Engineering Standards 3.3.3.4 and Sheet 31
03924241-d6b4-5c0d-827e-ffd42f0ac60d | note | TEST/TASK REQUIRED: Visual inspection
1868ce27-300b-5a13-a124-6ce015268fca | note | ○ NDM testing
014914e6-e910-5d52-8621-cf10cfa45329 | note | INSPECTION BY: UCCL
aac49ef3-33de-51a3-afff-b03ecee91c5c | note | ○ Haigh Workman
9c7c0c06-8f09-50e6-8527-f4349b0394b7 | note | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of basecourse layer, prior to sealing.
cccb9f23-334b-5dc3-90d5-2c7d2208a386 | note | ○ Basecourse installed as per FNDC Engineering Standards, and NZTA B/02.
8e09a4d7-6e5a-5ab7-b89d-0df2dc6d2995 | note | ACCEPTANCE CRITERIA: Compaction records.
3bf80ad2-a35e-59ec-922a-117e4b1079c7 | note | ○ Photographs.
ed564e93-f175-471e-85d6-7b7b0762ad36 | signoff | HOLD POINT
de061462-ff7a-484d-9999-3b91c664b611 | checkpoint | Detection Tape and Tracer Wire
26ac2289-a457-57d3-b135-777ef6ad3c53 | note | SPECIFICATION REFERENCE: Water Specification B.5.5.1.6
ce62eed9-8e1c-5e70-84b2-4c9f769d7f3e | note | ○ FNDC Engineering Standards 6.3.2.4 and Sheet 31
d891a075-69ab-5980-9926-a4845f1a19ff | note | TEST/TASK REQUIRED: Visual inspection and electrical continuity testing
62f15166-b889-50e5-aaf6-38207b7154a3 | note | INSPECTION BY:
8aa568a8-f9a8-58b0-8e62-316901b49dea | note | TASK TIMING OR TASK FREQUENCY : On completion of installation.
d77073a5-72e1-5ae3-aa2e-22156766e15f | note | ○ A blue metallic detection tape labelled 'Water' shall be laid directly above all new non-metallic watermains.
ebcce3f0-d5b5-5a67-9791-e246a5150f50 | note | ○ Tracer cable (2.5mm²) shall be attached to pipe wall at maximum 3.0m intervals.
1499d515-c6ce-5f7a-a3e5-6a17a6496b55 | note | ACCEPTANCE CRITERIA: Electrical continuity test results provided to Engineer.
68811db4-41c2-4296-8d50-5915fb050f0d | checkpoint | Pressure Testing of Pipes
dd76ca5c-0198-5255-a3c8-39217bda84b2 | note | SPECIFICATION REFERENCE: Water Specification B.5.10.1
99584116-12ab-5d86-9cf7-f109f3ad76c1 | note | ○ FNDC Engineering Standards 6.3.3.2
ca694dc3-7f4e-5e81-8b40-5cf1ff560349 | note | TEST/TASK REQUIRED: Pressure test of PE pipeline
9c408a52-3a3e-57a2-82d3-b90925cf05a7 | note | INSPECTION BY: UCCL, FNDC,
19f2ea27-d2c2-5859-b4c0-68b1b3dc4749 | note | ○ Haigh Workman
68a7cd7f-7d19-5290-ab7d-ce3c4504918b | note | TASK TIMING OR TASK FREQUENCY : On completion of installation of PE pipeline, after sufficent backfill has been placed to prevent movement.
bd642279-8b76-5665-bce4-03d95fbeec25 | note | ○ Pressure test as per FNDC Engineering Standard.
138dea5d-d6e2-5fc8-9e50-ddc1b5b22eae | note | ACCEPTANCE CRITERIA: Test results submitted to Engineer.
f129dc70-7993-4960-899b-a0c44e8fa33e | signoff | HOLD POINT
d48641b8-9066-417d-97f1-17b7bed85712 | checkpoint | Flushing and Disinfection
2ea617cf-6004-558c-9664-27df17ca135e | note | SPECIFICATION REFERENCE: Water Specifcation B.5.12.3
36139394-ffbe-504a-b7ea-c063278ffddb | note | ○ FNDC Engineering Standards 6.3.4
6548b2b4-ea8b-5dbc-9370-61af6da5884d | note | TEST/TASK REQUIRED: Visual inspection (flushing)
da174ed0-ff35-5d7e-8229-a7b393fbaeb9 | note | ○ Chlorination and testing
738aef9c-9857-580f-aacb-812385455494 | note | INSPECTION BY: UCCL, FNDC,
009e3f97-c85a-5643-a8ef-9ff025b094a8 | note | ○ Haigh Workman
a6bb065d-dbae-5535-a1aa-f6548da646ca | note | TASK TIMING OR TASK FREQUENCY : On completion of pressure test, prior to connection.
36e8bbd5-3a2d-58f6-a63e-f73f9763eaec | note | ○ Flushing and chlorination/testing completed as per specifications. Results meet FNDC specification.
3bd88fbc-7a5d-5052-9eef-92ebb7ec3573 | note | ACCEPTANCE CRITERIA: Test results provided to Engineer for approval prior to connection.
adedacd8-7eec-486c-b90a-75d0749c7d94 | signoff | HOLD POINT
779004bb-461e-41db-8fcd-ad6640cb87a6 | checkpoint | Connection to Existing Watermains
c2a92230-3c1a-5138-88dc-2ac09f7ce06e | note | SPECIFICATION REFERENCE: Water Specification B.5.12.4
6bdce408-d04b-5848-980c-6ca4fdf4ad74 | note | ○ FNDC Engineering Standards 6.3.5
ae801d85-6615-5080-9627-73c47ae465fc | note | TEST/TASK REQUIRED: Watermain connection
7cfdd2df-6d46-52e8-b425-f3eb9d50e888 | note | INSPECTION BY: UCCL, FNDC,
54964bb3-35f6-59e9-9e91-c7609dcdb7f0 | note | ○ Haigh Workman
f57c2058-ba21-52b4-a306-87caba61c729 | note | TASK TIMING OR TASK FREQUENCY : Connection to be completed after instruction from Engineer.
d9720c3c-305e-5610-9256-b1d54bf04d00 | note | ○ Note from FNDC Engineering Standard - "Only the FNDC's Reticulation Maintenance Contractor may undertake the connection".
d4e0f585-e658-5d29-a4e4-8f0640600812 | note | ACCEPTANCE CRITERIA: Photographs.
e5a45a67-945f-4ed6-a99e-ad25c6fa155b | signoff | HOLD POINT
50863d16-c217-40b5-a101-c7d241c1a609 | checkpoint | Service Connections
8bbca392-2cd7-5b97-8389-0e7ceeb16cb6 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.3.2.2 and Sheet 46
ae89c28d-bc01-593a-b8c7-12f3d3faac4a | note | TEST/TASK REQUIRED: Water connection
59ad669e-ef93-5b26-ad84-acad5e54a01e | note | INSPECTION BY: UCCL
c7712371-44e3-5f5b-b9cb-8893657f08c1 | note | TASK TIMING OR TASK FREQUENCY : Connection to be completed after instruction from Engineer.
d6272425-5603-5daa-878d-ab0efcd759ba | note | ACCEPTANCE CRITERIA: Photographs.
13307cc2-771d-57af-a969-1d655c38632d | note | ○ As-built drawings.
9eb75241-14df-4beb-bd05-efb6f5bdb72c | checkpoint | Reinstate Driveways
2eb98d06-eba6-5c7d-8ca5-77a1594f0b0f | note | SPECIFICATION REFERENCE: Water Specification B.3.7.6
ba86964c-ccbd-5820-a612-1c3361f217ef | note | TEST/TASK REQUIRED: Visual inspection
60802251-784a-56b2-a068-d95fe2efe5e3 | note | INSPECTION BY: UCCL
b619a545-41be-5891-a0cc-240ff966a7af | note | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
a75ce16a-ffd3-55cd-a7e2-d269c701f090 | note | ○ Driveways reinstated in the same material and to the same standard as existing prior to works.
8fc235de-8cdf-538a-b16b-cfc1890c01c4 | note | ACCEPTANCE CRITERIA: Photographs.
e83bade3-48b5-496d-a865-e259c1a22a43 | checkpoint | Reinstate Footpaths
c3a36a8e-025b-508c-b5d9-c30b33eb7623 | note | SPECIFICATION REFERENCE: Water Specification B.3.7.6
4c7b8922-280e-50d3-be00-0a72366aca82 | note | TEST/TASK REQUIRED: Visual inspection
a140a0aa-3a42-51c9-b92a-2597728a82e9 | note | INSPECTION BY: UCCL
0b0167a3-ad7e-5d15-bf5b-d9d63e16564b | note | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
63d0bf9d-e548-5451-b924-320fa5029854 | note | ○ Footpaths reinstated in the same material and dimensions but constructed to FNDC Footpath Standards.
715eb443-5888-5277-933a-bda3bab9c9d7 | note | ACCEPTANCE CRITERIA: Concrete dockets.
a12d29a1-61c5-5f13-83f6-96fed9678349 | note | ○ Photographs.
ca41cbe4-7a19-4251-ac32-5ae3b92bf45f | checkpoint | Reinstate Kerb and Channel
ebecc12b-5291-527b-8c94-31978026bb2e | note | SPECIFICATION REFERENCE: Water Specification B.3.7.6
a4fb346d-14ec-5b65-9567-3e7fe565b7ad | note | TEST/TASK REQUIRED: Visual inspection
12a1dbde-50c3-5390-b091-e64085580eeb | note | INSPECTION BY: UCCL
eac07fc6-dcd0-5fb0-adf2-0ed5b755401d | note | TASK TIMING OR TASK FREQUENCY : Replacement kerb and channel profiles match line and level of existing kerb and channel.
79b97941-59ff-5a7f-9c90-08087fe4aee9 | note | ○ Concrete has minimum 28-day strength of 25MPa.
fd655c7b-c128-53e1-a248-3789889ea8b7 | note | ACCEPTANCE CRITERIA: Photographs.
f63750b4-54d6-40f6-9ac5-5d07d43172da | checkpoint | Concrete Pour (Stuctural - Pipe Bridge Footings, Commercial Driveways)
f18db20e-21c4-513d-8a1c-afafe7cc18f8 | note | SPECIFICATION REFERENCE: Water Specification B.4.4.2
93d887fa-4a3a-508e-84e9-11a404b0779f | note | TEST/TASK REQUIRED: Prepour inspection
3287ac22-f0c7-5e44-a2ab-b36ba7614904 | note | INSPECTION BY: UCCL
83c5b3ae-95a3-5884-a2cb-d623c3f56aad | note | ○ Haigh Workman
af847fd1-40fe-5e4c-91b2-a2cf58c0a8ad | note | TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete.
3b64facf-2d2c-5b45-8011-4941773d3c13 | note | ACCEPTANCE CRITERIA: Pre-pour inspection checklist.
d210cab6-9c76-5ae3-8307-d0b081461ddc | note | ○ Concrete dockets.
c03637d8-036e-511c-bfc4-55e9f1f5a61a | note | ○ Photographs.
8817445f-10bb-491e-a53a-89f18c92f147 | checkpoint | Concrete Pour (Non-Structural - Footpaths, Residential Driveways)
8e3a9bdc-eb6f-515f-9540-986701d83927 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards Sheets 12, 17 and 18
405de9c4-366d-5714-94c1-442582a60146 | note | TEST/TASK REQUIRED: Visual inspection
6d8dff0a-23e0-58d4-bd85-ad0c6870b47e | note | INSPECTION BY: UCCL
d4179f97-cc78-5f40-b373-7d4e8f471434 | note | TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete.
338d2a99-5347-5689-9af2-4df316704197 | note | ACCEPTANCE CRITERIA: Pre-pour inspection checklist.
9b811699-2405-5dfa-856b-5d82aa06fda5 | note | ○ Concrete dockets.
f5cd028c-1e17-5e6f-a4d7-4a90c4398df7 | note | ○ Photographs.
4e9fa573-228d-42db-8b9d-d759e73c2b13 | checkpoint | Asphaltic Concrete Layer (DG10)
fb9d1ad7-1993-5b0e-9221-347447816d42 | note | SPECIFICATION REFERENCE: NZTA M10 Specification
d7e93982-b1b0-5771-9ca3-84e94a1f4e5e | note | TEST/TASK REQUIRED: As per NZTA M10 Specification
353772aa-2a62-5721-84a8-bb86b7f78f99 | note | INSPECTION BY: UCCL
defeb214-9816-5155-a328-1f7b398fd444 | note | TASK TIMING OR TASK FREQUENCY : On completion of the pavement surface.
7a9c2614-e702-5573-a3d7-55d29d9831b4 | note | ACCEPTANCE CRITERIA: Test results submitted to Engineer.
3baccfa2-5f9d-5479-8132-0632857adb91 | note | ○ Photographs.
5d99da3f-2f78-4271-b1e4-875148fd36df | checkpoint | Grout Filling of Redundant Watermains
389138d6-3707-59b5-b744-ea85c196481a | note | SPECIFICATION REFERENCE: Water Supply Drawings Notes, No. 20.1 and 20.2
efd9264f-1a37-5c61-971a-d5d10ac3b435 | note | TEST/TASK REQUIRED: Redundant watermains to be grout filled and remain in place.
72021d4d-1a1c-534d-9408-f5a37427fb07 | note | ○ Remove redundant valve boxes, signs etc.
c49bde83-ecd5-5573-b769-2856eba8d96e | note | INSPECTION BY: UCCL
b3def3d2-9720-556b-bf94-2c57308c83a5 | note | TASK TIMING OR TASK FREQUENCY : Grout filling on completion of new pipelines.
185414d8-7484-5fe6-8e78-f22a07822ff9 | note | ACCEPTANCE CRITERIA: Grouting record.
8224f903-3705-5337-bbb8-59cef3890764 | note | ○ Photographs.
48732eed-cc2e-4489-8aca-16a35d93a5ff | section | Post Construction
5652c1fd-ff87-44f5-b361-6c77b27e80e6 | checkpoint | As-Built Drawings
f59e955d-0140-54ca-b7bd-7b22801dc660 | note | SPECIFICATION REFERENCE: Water Specifcation B.2.18.1
263c2ccb-6106-5d26-a3ba-19d31ca449c4 | note | TEST/TASK REQUIRED: As-built drawings meet FNDC specification
c9b35a5f-8f89-5980-b71b-ec195496b4f3 | note | INSPECTION BY: UCCL
7e761dcf-ceff-5e92-a236-9064a927c3ef | note | TASK TIMING OR TASK FREQUENCY : Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion.
e89ae773-3b4a-5139-926d-ea6b61f09351 | note | ○ Final as-builts issued prior to Final Completion.
71d34136-d67d-5fa5-80f3-fb5184911df8 | note | ACCEPTANCE CRITERIA: As-buiilts submitted to the Engineer for approval.
5aef8011-56fb-4015-b3ed-8157614dbad8 | checkpoint | RAMM Information
e65256d5-b43c-547f-b73e-9df7674e4ede | note | SPECIFICATION REFERENCE: Water Specification B.2.18.2
45483781-794d-519c-af86-16ee76a8c8b0 | note | TEST/TASK REQUIRED: RAMM information
1a23885e-6f60-5a93-9fd9-743e2d38adbb | note | INSPECTION BY: UCCL
0a3e252e-17ea-5e1d-821a-3da2696040b4 | note | TASK TIMING OR TASK FREQUENCY : RAMM information submitted to the Engineer on completion of works.
604e6982-56de-5e32-a770-ec87296af34d | note | ACCEPTANCE CRITERIA: RAMM information submitted to the Engineer.
1053089a-a875-4ab9-8730-04ec2efcace8 | checklist | Scour Valve ITC |  | Scour Valve ITC
710658d0-aad2-4a87-91c0-fcbbf7f58261 | section | Location
a57110a9-b18b-488e-ad35-222b264f61f1 | checkpoint | Location
511256bf-bbc3-571e-abac-70346be2c951 | textbox | Chainage or property location of Scour Valve
8ea172f5-0e07-5549-b3c1-0680b98aba1e | date | Date of Installation
34be656c-f0cd-46df-823c-1eb16f843362 | checkpoint | Scour Valve is installed to line and level of the specifications and IFC drawings
4f9d7d8b-90d8-4b48-b508-2cadb500b94b | section | Scour Valve Installation
e05a99de-2af0-491e-bbdc-f2d69f9dddb9 | checkpoint | Scour Valve Installation
dd9efd73-1944-547d-8c4f-87d4d95e2ee1 | textbox | Scour Valve Make/Model
ac4dbb80-7b80-5760-b423-33d3ed85a715 | textbox | Scour Valve size
5ca56f59-327e-5103-9cdd-13350a0f3a28 | dropdown | Valve closing direction | Clockwise,Anticlockwise
2eb16599-1697-53ec-a9dd-3e0f5507e683 | tickbox | Valve spindle finishes no more than 350mm below the valve box lid
98213ed1-edaa-4228-84f5-ca2235552b23 | checkpoint | All bolts below ground are SS and protected with Denso, Mastic and Polytape
5f53f7e2-17d1-451d-9561-efba7e26f1e3 | section | Reinstatement
dbd585c9-55fa-4035-8c10-04cc5fcef12d | checkpoint | Reinstatement
cf6a6d3b-fc83-5993-9209-e00ac5a8d987 | tickbox | Scour Valve manhole is a 1050 installed to IFC drawings/FNDC standards
580d706f-b32f-5792-99c7-55b98678328f | tickbox | Marker peg installed
b40c3bd9-9b3c-5eb5-b762-0742580c0009 | tickbox | Scour Valve box is set flush with the surrounding ground levels
cae7c0c5-1b73-40e7-bec5-858d5bdb6525 | section | Post Installation
63cdd95a-3ad8-4a1a-bf36-1397e743621d | checkpoint | Post Installation
85493271-fea3-553a-a985-8924007b4327 | date | Installation of Scour Valve complies with IFC drawings, specifications and FNDC Standards
937aa09e-3ab9-4f23-9dac-aefea307110c | signoff | Final Inspection
6ec89caf-0796-41ef-8545-26c53e265999 | checklist | Valve ITC |  | Valve ITC
ea0199ea-7199-470f-8ac2-7ccc6cbe46e8 | section | Location
c7d24f4a-db0c-4097-8b80-c62341c07fe2 | checkpoint | Location
b3be65cb-8c54-5fc9-b7b7-b943ca71d806 | textbox | Chainage or property location of valve/valve set
70bd3085-5e5b-5dd6-a4a1-74ce7ed367b9 | date | Date of Installation
17163f99-447e-41c4-b0c0-d111e41b4435 | checkpoint | Valve/valve set is installed to line and level of the specifications and IFC drawings
ff1dbef4-0541-56f7-90ed-447912f66513 | dropdown | How many valves are located in this set | 1,2,3,Other
2d425c1c-3efc-4d07-a705-53f739cfe3ce | section | Valve Installation
83d69499-132b-4c83-a4dd-241d2f6c018d | checkpoint | Valve Installation
0f74d81a-df23-5afb-8a96-7c115a6b3c2c | textbox | Valve Make/Model
a45e4402-83e6-517b-b635-682e54b7bdbf | textbox | Valve sizes
570b5e51-c676-53be-9592-61e4fd4527df | dropdown | Valve closing direction | Clockwise,Anticlockwise
f39a8fb3-e96e-5b5b-9471-f536e9f92b90 | tickbox | Valve spindle finishes no more than 350mm below the valve box lid
42a53aae-d0ac-51aa-abfc-89c27d7899ff | tickbox | Anchor/Thrust Blocks installed
1718b0cd-256c-412f-868c-47fec371bc78 | checkpoint | All bolts below ground are SS and protected with Denso, Mastic and Polytape
8a568392-4967-47ae-b78a-5fd23f2b029c | section | Reinstatement
74c70049-d8c7-490f-b8a8-909c91c01c11 | checkpoint | Reinstatement
5043eba1-b7e5-515c-81b6-b5a5fe4ac868 | tickbox | Valve Box installed to FNDC standards with the long side parallel to the direction of the main pipe
b0e4151f-208f-500e-85e7-83e0d06e0430 | tickbox | Marker peg installed with SV labelled, protruding 600mm from the surrounding ground
6bee1814-fd9e-57fb-84b5-f9bc970773cc | tickbox | Valve box is set flush with the surrounding ground levels
4b71059d-af7a-4e99-9eda-179c4fc2e704 | section | Post Installation
f5246d29-fb12-41a3-b5bc-814745c1c972 | checkpoint | Post Installation
4fd03572-ad4a-5fc2-b975-0ac29a74ad28 | date | Installation of valve complies with IFC drawings, specifications and FNDC Standards
02b1d731-0bcd-4bb6-b8c1-780dd17d1065 | signoff | Final Inspection