## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
5e4e66db-28c5-4385-a29b-72883c484b33 | checklist | ITP - Wastewater Reticulation Upgrade | itp | ITP - Wastewater Reticulation Upgrade
b847a8c4-ed90-4d41-b501-5b1d2074d28a | section | Preconstruction
4fe935ca-f389-4506-8b96-ab00f577de3b | checkpoint | Precondition Survey
bd66c0ce-e903-5873-9619-d9ab82e0dec7 | note | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.2.2
f559c34a-d32e-5a81-a31c-cee83f78617b | note | TEST/TASK REQUIRED: Visual inspection.
293d9359-9dea-5f7a-ab1b-459ac908a3a3 | note | INSPECTION BY: UCCL
0bcd1806-723b-54fa-823b-d80e8bad99bb | note | TASK TIMING OR TASK FREQUENCY : Prior to starting on site.
85ac4fb7-ce65-5442-8a5f-47c300193322 | note | ○ Survey conducted of all surfaces, footpaths, kerbs, driveways and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works.
b93ae04a-7116-5f57-a157-f9de53a62cad | note | ACCEPTANCE CRITERIA: Survey documents submitted to Engineer.
5480be1a-5b58-41d9-b12a-5fd7da21a823 | checkpoint | Materials Quality
a3cf3166-a365-5fcf-9a40-744752d27f54 | note | SPECIFICATION REFERENCE: FNDC Approved Materials List - Wastewater and Stormwater
ac370e05-2a00-563d-83d5-0e02f714c22c | note | TEST/TASK REQUIRED: Visual check for approved materials, quality and condition.
df1de97a-4fcc-5652-8857-8b10abbd647d | note | INSPECTION BY: UCCL
2252ff34-1b6f-544b-8599-1dc38041bacf | note | TASK TIMING OR TASK FREQUENCY : On arrival to site, prior to using materials.
738524aa-7396-5f54-881b-ea57d2c7a246 | note | ACCEPTANCE CRITERIA: Materials meet specifications or otherwise approved by Engineer.
5ccb10e9-db30-56e1-9f34-a3dc1a3a0f55 | note | ○ Delivery dockets.
735a1a97-dc10-5314-a3a6-57291fe56a61 | note | ○ Photos.
b81c709e-e529-4d3b-9c05-d886dd20e06e | checkpoint | Survey Setout
2e843113-e085-5846-934a-7d3c7cf49b42 | note | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.2.4
3e30c637-594d-58b2-a915-8e0b998114e6 | note | TEST/TASK REQUIRED: Survey set out.
35805cf3-3350-59ce-a883-7b2c2b37a6b6 | note | INSPECTION BY: UCCL
39867e5e-6b50-55fd-a9e6-07fbfc706be0 | note | TASK TIMING OR TASK FREQUENCY : Prior to commencing each stage of work.
a59cf9b9-dfbc-5c36-b09c-72b12c76bade | note | ACCEPTANCE CRITERIA: Survey set out as per IFC drawings.
a2b5c72a-6c94-5393-87ba-646f56671bc9 | note | COMMENTS: Check all MHs for levels, prior to constructing drainage lines, they must verify the inverts and locations of existing manholes as part of the inspection and testing process
eff5c604-77db-466d-b26f-f716ec87cdc2 | section | Installation
a08b5a34-c1a1-4067-b149-5b0b4258ca0b | checkpoint | Service Location
c02bddef-2613-5290-bac6-4f9bad61a617 | note | SPECIFICATION REFERENCE: Wastewater Specification B.2.11.4.2
b5f1566a-c350-5254-ae25-33950d541dca | note | TEST/TASK REQUIRED: Locate underground services within work area.
7481bedf-f7d8-5c30-9c4b-f27148541686 | note | INSPECTION BY: UCCL
42add012-851a-55c8-8fc6-3a764c451d42 | note | TASK TIMING OR TASK FREQUENCY : Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services.
6e8fa7eb-9717-419b-9fe3-b0ee294d3cbf | checkpoint | Material Properties (Bedding) (1)
536d35ee-940e-55f8-ade5-c84d6b19c2b2 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.5.1.9
80a5b32a-b2d8-5bbf-ada5-5e6f81ce7c34 | note | TEST/TASK REQUIRED: AP20 Grading curve to be submitted to Engineer for approval.
4ff17fb8-b538-5603-a729-9622fa816399 | note | INSPECTION BY: UCCL
1bdcdf41-bfdc-5f37-b72e-27c1f5a1c1c0 | note | ○ Haigh Workman
f67105c7-d443-5fba-a02d-04bdfb04247d | note | TASK TIMING OR TASK FREQUENCY : Prior to using bedding material on site.
20f545b0-3b4d-5f40-a881-2216385f3786 | note | ○ PE bedding, pipe surround and haunching shall be AP20 in accordance with AS/NZS 2566.
fda81553-4de7-5cc8-b3e6-6a336372d018 | note | ACCEPTANCE CRITERIA: Bedding grading curve accepted by Engineer.
| checkpoint | Material Properties (Bedding) (2)
| note | SPECIFICATION REFERENCE: NTC020
| note | TEST/TASK REQUIRED: Aggregate Testing Frequency
| note | INSPECTION BY: UCCL, Haigh Workman
| note | TASK TIMING OR TASK FREQUENCY : PSD (Grading): 1 test per 500m3
| note | ○ Estimated requirement: 2 tests for ~1080m3
| note | ACCEPTANCE CRITERIA: Bedding material test certificates accepted by Engineer.
9f953b3e-161c-4d3c-878c-5225c8da055e | checkpoint | Material Properties (Subbase - AP65) (1)
71bddfc6-773b-53b0-b704-e58597bf33a6 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
1fbca303-3c4b-5fc9-8c1e-1326633fa5ea | note | TEST/TASK REQUIRED: Subbase material meets FNDC Engineering Standards
c57505cc-15e7-5f70-a60b-04d148b4c11f | note | INSPECTION BY: UCCL
e637fc48-c4da-59bd-9d64-024fd4914a18 | note | ○ Haigh Workman
a2003e0a-4f8f-52b6-bd94-a2bbfc57db90 | note | TASK TIMING OR TASK FREQUENCY : Prior to using subbase material on site.
01af1c3e-c159-59ca-9d47-86241038b195 | note | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
| checkpoint | Material Properties (Subbase - AP65) (2)
| note | SPECIFICATION REFERENCE: NTC020
| note | TEST/TASK REQUIRED: Aggregate Testing Frequency
| note | INSPECTION BY: UCCL, Haigh Workman
| note | TASK TIMING OR TASK FREQUENCY : PSD (Grading): 1 test per 2000m3
| note | ○ Estimated requirement: 8 tests for ~15,853m3
| note | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
a22c3390-90d0-4792-b362-f0046b0d7f59 | checkpoint | Material Properties (Basecourse - AP40) (1)
2bbbdcf8-8183-591a-bda7-74a09e9cbb7a | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
14c80a63-ac5e-5c94-ba72-2859e3c5afc4 | note | TEST/TASK REQUIRED: Bascourse material meets FNDC Engineering Standards
afb969c0-35f7-57c6-b7f4-df08d3296726 | note | INSPECTION BY: UCCL
0ecb82ef-86b7-544a-8846-e976772c8dcc | note | ○ Haigh Workman
db65a52c-934e-5e32-b865-08de4037cd79 | note | TASK TIMING OR TASK FREQUENCY : Prior to using basecourse material on site.
70d4c4c6-0b06-5338-a9a0-056dd639c013 | note | ACCEPTANCE CRITERIA: Basecourse material test certificates accepted by Engineer.
| checkpoint | Material Properties (Basecourse - AP40) (2)
| note | SPECIFICATION REFERENCE: NTC020
| note | TEST/TASK REQUIRED: Aggregate Testing Frequency
| note | INSPECTION BY: UCCL, Haigh Workman
| note | TASK TIMING OR TASK FREQUENCY : PSD (Grading): 1 test per 1000m3
| note | ○ Estimated requirement: 4 tests of each type for ~3240m3
| note | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
22422f1c-3712-4051-b82c-33181e604198 | checkpoint | Pipe and Rubber Rings
0c1e6815-ab2e-520d-a441-d6e546932fd7 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.8.3
029871ab-10f3-59e0-b86e-f34b3b339e70 | note | TEST/TASK REQUIRED: Visual inspection
53c70e58-5199-5047-bda7-a79f83dce63f | note | INSPECTION BY: UCCL
2744f0a4-81eb-5e32-8eaf-425aac49f954 | note | TASK TIMING OR TASK FREQUENCY : Visual inspection prior to use (clean and free from defects).
318ca5e8-18f1-5f2d-92f0-53db9b9cf301 | note | ACCEPTANCE CRITERIA: Photographs.
bc378fdf-da9f-4c76-b714-750c52e4ab1d | checkpoint | Pipeline Installation (PVC)
749243ee-34b5-5995-b830-9c961f9c2728 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.8 and B.7.9
66f6c4dc-8f42-56c9-8d8c-76e7746b2b07 | note | ○ FNDC Engineering Standards Sheet 31
5506bac0-dae7-5291-a937-2feb26244a2c | note | TEST/TASK REQUIRED: Visual inspection
28ba8c56-70e8-527a-a2d2-f1fe104aa59c | note | ○ Pipeline installed to correct alignment, grade and level
89643c42-3aa2-58a7-8ffd-b74b4d55d079 | note | INSPECTION BY: UCCL
325353b7-be48-5ed4-b9d8-49abee16ae5a | note | TASK TIMING OR TASK FREQUENCY : On completion of installation of each length of pipe, prior to backfilling.
cc1589cc-de19-5a34-88ca-f5a5f3fd5db6 | note | ○ Throughout installation of pipeline.
fb1694a8-72ea-5590-957b-20500a95d4c0 | note | ○ Horizontal alignment +100mm.
8fb38f66-4503-5450-8f3b-1bd9503f8e90 | note | ○ Vertical tolerance +/- 10% of the design grade for each section of pipe.
99459b7c-ae9d-5013-bdd1-451c9c0d33e8 | note | ACCEPTANCE CRITERIA: As-built drawings.
5c9bd0fc-e9d3-5ebf-b24c-2c0f65fed836 | note | ○ Photographs.
84acdcab-881e-4c45-baba-098e3bfed2e0 | checkpoint | Stainless Steel Pipe Bridge
2fe92968-ba0e-59fa-8902-ff8a0cbcc4ff | note | SPECIFICATION REFERENCE: Wastewater Specification 'Package 3 - Bisset - Pipe Bridges Specification
b60ce7d1-f6fb-53ca-9552-99595bd30645 | note | TEST/TASK REQUIRED: Visual inspection
bdcf408e-9054-5a79-95a1-31a9f0576b7f | note | ○ Pipe installed as per specification to correct alignment, grade and level
de517692-06fc-515c-b0b2-067cdeda2c43 | note | INSPECTION BY: UCCL
e0438dde-9acf-5214-9f65-fedab7e3b234 | note | TASK TIMING OR TASK FREQUENCY : On completion of installation of each pipe bridge.
aeb9f2be-401b-5e52-8049-ca2ee6582968 | note | ○ Horizontal alignment + 100mm.
d13082db-b15c-5d11-8b57-37ebc8a3c93e | note | ○ Vertical tolerance +/- 10% of the design grade for each section of pipe.
cc981ce1-3f12-58c4-ba80-7934a9ab4e15 | note | ACCEPTANCE CRITERIA: As-built drawings.
423cbc19-c15e-50b9-8ebb-629bd83556b8 | note | ○ Photographs.
7a3bbbe8-d950-4bc0-9020-4f0dc84a99af | checkpoint | Manhole Installation and Backfill
5f26376c-6144-519b-a051-7f9e9822f58c | note | SPECIFICATION REFERENCE: Wastewater specification B.7.9
cd2637e4-e6b8-55e2-b900-8e0ddbef0332 | note | TEST/TASK REQUIRED: Visual inspection.
82c1a646-2d7d-5bc4-8f56-3ecb43c44b85 | note | ○ Manhole checks including position, haunching, steps and sealed joints.
c11d4c1b-4710-5096-a005-89846838fa9e | note | INSPECTION BY: UCCL
ce4fe9c4-2851-5757-8b8e-445ccaff928a | note | TASK TIMING OR TASK FREQUENCY : On completion of manhole installation.
0a837178-26e9-549b-ba04-36c6f089a8dc | note | ACCEPTANCE CRITERIA: Falls through manholes are to be within +5mm of design levels.
d74722e4-df09-59b6-8962-0f4e15144cf3 | note | ○ Maximum deviation from vertical (manholes/chambers) shall be 10mm per metre.
4e59abb2-02e6-483b-8ec0-5b6894163948 | checkpoint | Pipe Bedding
6542f910-b71d-57c3-a734-17b3db6de290 | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.4.1
d11a9348-97c0-5c95-becc-71c37d75bb52 | note | ○ FNDC Engineering Standards Sheet 31
2411d266-892c-5777-a721-2f6d0fcc089d | note | TEST/TASK REQUIRED: Visual inspection.
da5e670c-b628-5cb8-a71a-f9e83a2c794d | note | ○ Compaction test on top of bedding.
7b0fcc35-e1b7-5d59-9249-a0ac762792fc | note | INSPECTION BY: UCCL
ee410fae-81a0-5829-9842-4d189de6f810 | note | TASK TIMING OR TASK FREQUENCY : Bedding installed as per specifications.
3ef67abe-3390-569a-b15a-2f1d4375cc7d | note | ACCEPTANCE CRITERIA: Photographs.
b18222b6-73bd-56f5-b0a3-b63083b63ed4 | note | ○ Compaction test results.
0a8ec505-ba0b-4db6-91a6-4e931c6b7b24 | checkpoint | Pipe Backfill (Outside of Carriageway)
48228d76-72bc-5f48-851f-3770220625f7 | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.6.3
891c4bf5-f1e1-507f-899e-aee23eaa01bf | note | ○ FNDC Engineering Standards Sheet 31
21ab72df-b4db-55e1-8306-7ec7353ba42f | note | TEST/TASK REQUIRED: Visual inspection.
875e2757-7e66-5e56-b896-5463bf3a41d9 | note | ○ Compaction test on top of GAP65.
2d4af9e6-9237-5f58-9192-aa1fbdd89c80 | note | INSPECTION BY: UCCL
9388d803-7443-5dc7-af2d-55a321be59ed | note | TASK TIMING OR TASK FREQUENCY : On completion of GAP65 layer.
d81fea9b-b94b-537b-8387-995b6db8fde2 | note | ○ On completion of ordinary backfill.
390e27cb-b2e5-5998-8bc2-a071f31985e3 | note | ACCEPTANCE CRITERIA: Photographs.
4e37bf94-d58c-5503-b7a0-4716d953a1e2 | note | ○ Compaction test results.
5db2b47d-e676-4784-9f0c-8ae910d7c694 | checkpoint | Subbase
5a445aeb-f7a0-5a30-aace-f84c30c7e4ec | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.6 and B.3.7
3d52e053-11f7-557f-9cd2-659156b1dc4a | note | ○ FNDC Engineering Standards 3.3.3.3 and Sheet 31
6d3c8178-ba7a-514e-adb9-ff88e7653c4f | note | TEST/TASK REQUIRED: Visual inspection
19861efe-0c99-50da-8dee-6545b4cc622d | note | ○ NDM testing
74b256a3-a7d0-527f-bba9-5e4623980e6c | note | INSPECTION BY: UCCL
76a6e342-acf1-53cd-96ad-65857e45e446 | note | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of subbase layer, prior to installing basecourse.
2ad91036-e2e7-5f16-a04e-c27a20efb9d4 | note | ○ Backfill and compaction completed as per specifications.
19ba96bf-544d-5f79-9368-1452dc297f86 | note | ACCEPTANCE CRITERIA: Compaction records.
dcde4283-8680-5cae-abe3-f5d1e87da129 | note | ○ Photographs.
0220ab7a-2724-4d70-a90b-7be790bf6f47 | checkpoint | Basecourse
3001dcea-0ddd-5812-9c38-39ece578e501 | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.6.2
f936b9e9-8641-5bfc-8f46-fd6bf31da307 | note | ○ FNDC Engineering Standards 3.3.3.4 and Sheet 31
e3e53da3-8a99-581d-b1f4-2bd6eb61c887 | note | TEST/TASK REQUIRED: Visual inspection
63c4dfe8-30ca-5890-9f6f-a951e6aa3502 | note | ○ NDM testing
42c0d5a6-9bb0-53a2-ad11-5f4a406a765f | note | INSPECTION BY: UCCL
ccce277e-10f9-5856-95c2-2ff5a4d32c12 | note | ○ Haigh Workman
d405cb00-2244-5022-b84b-49a2225f20ad | note | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of basecourse layer, prior to sealing.
386d9fb8-3e56-5984-b250-53b604c35211 | note | ○ Basecourse installed as per FNDC Engineering Standards, and NZTA B/02.
4ee7bc09-6ccc-52ac-9b5f-7201be0cab3a | note | ACCEPTANCE CRITERIA: Compaction records.
9545072e-585c-5f44-80ac-893b493cf8d3 | note | ○ Photographs.
bfc3d791-d767-421b-a2c9-1ef933ba7b2b | signoff | HOLD POINT
9eed3e82-7318-425a-bcf7-e693dc323ad0 | checkpoint | Detection Tape
d6fee34e-a693-5cd5-ad90-1c2c112e2812 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.5.1.6
aaad6024-cce3-5bdd-97ff-6af3da2ee1e8 | note | ○ FNDC Engineering Standards 5.3.3.1.2
8fd4b92a-6e92-5ef8-b73d-dcbf40f8b7d7 | note | TEST/TASK REQUIRED: Visual inspection
b17f35fe-532c-536a-b800-eb97a845262e | note | INSPECTION BY: UCCL
5d91a7b7-f5e0-546c-8f5a-3a1da86a8ba0 | note | TASK TIMING OR TASK FREQUENCY : "Sewerage" detection tape laid directly above all wastewater pipelines.
ba20a863-0096-5e46-aaaf-53f72e6a4753 | note | ACCEPTANCE CRITERIA: Photographs.
e3376aea-9613-4273-903b-d0cd0b03c41c | checkpoint | Pipeline Testing
31c1dd6c-bc02-5507-8db2-0b5fc4e6422d | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.9.1
573b5ebb-3a2d-5074-adb6-dd13603de5bd | note | TEST/TASK REQUIRED: Air test
cf0386e4-995b-5282-9e5f-b167f65f00cf | note | INSPECTION BY: UCCL
c3dcebbe-889f-5bbd-8183-7f8745abd11a | note | ○ Haigh Workman
d35d735e-e6f4-58f0-8274-b2445fc8aebf | note | TASK TIMING OR TASK FREQUENCY : Each section of pipeline is to be tested by 'Air Test', including Lunden junctions.
401ac030-cd03-5e6a-a6b1-7ed3ce1ccacf | note | ACCEPTANCE CRITERIA: Drop in pressure shall not exceed 25mm over a period of 5 minutes.
ca645913-0faa-4512-9674-ccd47b6f4408 | signoff | HOLD POINT
99c025c8-db94-4494-bae4-1b29f9090cde | checkpoint | Manhole Testing
4a715836-95e6-5f4e-b062-d018f092fc58 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.9.1
2962de14-4fdb-5722-b778-0b71f71d5c9d | note | TEST/TASK REQUIRED: Visual inspection.
338bc316-41cf-5e83-b161-1972dee95bd1 | note | ○ Water test.
20b9be33-671f-5c15-a1b1-dfd9b6e364b2 | note | INSPECTION BY: UCCL
cf4f00bd-5787-5f67-ab4c-b96d9331fb42 | note | TASK TIMING OR TASK FREQUENCY : Visual inspection of each manhole prior to backfilling.
b073a74e-a368-524e-8ddd-efc6a2154833 | note | ○ Water test after backfill.
8106f2d0-051f-5789-9ee8-7df50c9d967a | note | ACCEPTANCE CRITERIA: Drop in level shall not exceed 5mm in 10 minutes.
ea6706bf-e28e-4dca-a710-5fa988d99000 | signoff | HOLD POINT
a11c4627-09ba-419d-974a-b3eeacab669c | checkpoint | Wastewater House Connections
a968e89e-1105-5b01-be2f-dd0166b58905 | note | SPECIFICATION REFERENCE: Wastewater Specification B.7.8.10
9054dc0a-0e16-554c-9525-609b3721ccb2 | note | TEST/TASK REQUIRED: Visual inspection.
462d83e3-54b1-5b4e-ab16-608961301ad5 | note | ○ Survey.
a76a22bd-d66f-5661-9f5a-d3c963eb103a | note | INSPECTION BY: UCCL
06ab8b88-5cd0-5fa8-a34c-cde9659c6734 | note | TASK TIMING OR TASK FREQUENCY : On completion of each connection.
7a173ba6-109f-5757-bdd3-57dea0dede04 | note | ACCEPTANCE CRITERIA: Photographs.
832d037e-4550-58e6-a9ea-828b8d1cf6e7 | note | ○ As-built drawings.
d14c90af-2d85-46e4-b008-bf6928032ccc | checkpoint | Reinstate Driveways
03d82803-d499-50cd-9dbe-5b33d94d8571 | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.8.5
2488e35e-a4bf-5ae2-9c37-4cdbd315dd23 | note | TEST/TASK REQUIRED: Visual inspection
c75cff61-d89c-557c-a8f4-e24761a92b73 | note | INSPECTION BY: UCCL
4ce6edce-9e82-53f9-9d4c-7c134080ca51 | note | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
62077835-461d-5f14-b5eb-07b11880900d | note | ○ Driveways reinstated in the same material and to the same standard as existing prior to works.
edc5db91-80d6-514c-a1c3-6a57ecb7ef2a | note | ACCEPTANCE CRITERIA: Photographs.
28bca8b0-62db-4b75-a8f2-a701bf60c263 | checkpoint | Reinstate Footpaths
2df11296-f6e0-5ade-8831-fafcd4df401c | note | SPECIFICATION REFERENCE: Wastewater Specification B.3.8.5
32dedfe0-401f-5562-a007-bc3605ec14c7 | note | TEST/TASK REQUIRED: Visual inspection
61c02b3d-f849-5946-bcae-d0dc6b58ef89 | note | INSPECTION BY: UCCL
77fb6831-ac6e-5306-83d7-13f52a68db95 | note | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
99adc8a7-4e0a-5f00-b5fd-d8cb3657a8cd | note | ○ Footpaths reinstated in the same material and dimensions as existing footpath, and constructed to FNDC Standards.
fcab2043-1863-5d73-bdb8-daca1821bfbb | note | ACCEPTANCE CRITERIA: Photographs.
f334a94a-8fa2-4657-abd2-d01627556dae | checkpoint | Reinstate Kerb and Channel
f340eb37-eac9-583c-9116-5ac5d9ae8a0a | note | SPECIFICATION REFERENCE: Wastewater Specification B.8.5
f9033f89-b3a3-52df-a955-db6dc78655f1 | note | TEST/TASK REQUIRED: Visual inspection
c9ebed99-f029-54a9-9284-2b74740a3fca | note | INSPECTION BY: UCCL
60e296e4-b0df-52a0-999f-8e9e249fcf40 | note | TASK TIMING OR TASK FREQUENCY : Kerb and channel profiles match existing.
f771ba8e-3629-5769-9bc3-9421bac3ec94 | note | ○ Concrete has minimum 28-day strength of 25MPa.
feae7d67-3040-5934-9aa0-4cc3c5e9ec1d | note | ACCEPTANCE CRITERIA: Photographs.
c03f8494-8a9d-4440-b2e9-1073895e2d11 | checkpoint | Concrete Pour
91dccf55-7c3b-5162-a1a3-ca1111057222 | note | SPECIFICATION REFERENCE: Wastewater Specification B.4.4.2
7d595de0-0c7e-58e6-83fc-908b80aba36c | note | TEST/TASK REQUIRED: Prepour inspection
71e900bc-e2ec-5427-a58d-5a05d7c6d847 | note | INSPECTION BY: UCCL
44c42b60-ccea-5b35-b503-3d83a02a3f6b | note | ○ Haigh Workman
ca2670dc-6056-530c-823e-cf931772f9f6 | note | TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete.
099cbc4d-3ad5-5082-bafd-9f88c30b8b7a | note | ACCEPTANCE CRITERIA: Pre-pour inspection checklist.
e27128f4-251d-5a5d-9c35-02135460cd76 | note | ○ Photographs.
f7ada8db-2ce9-42c8-aa87-8d4c3c5d7511 | checkpoint | Asphaltic Concrete Layer (DG10)
94a44cfb-1a8b-5acb-b9ca-e3b2e4f99e51 | note | SPECIFICATION REFERENCE: NZTA M10 Specification
e0bf0021-7a74-51b3-b8d9-93e6667591fe | note | TEST/TASK REQUIRED: As per NZTA M10 Specification
e56a7889-a825-5e49-8143-22f33b47a914 | note | INSPECTION BY: UCCL
0cb0849a-8554-592f-85b4-6c518bc32d90 | note | TASK TIMING OR TASK FREQUENCY : On completion of the pavement surface.
25765812-775a-52c1-9d34-3045870d68bb | note | ACCEPTANCE CRITERIA: Test results submitted to Engineer.
0cc452c4-7e40-5f3b-8a36-e7e8a97840e2 | note | ○ Photographs.
a753b28c-100f-4114-a17a-e8ff6d45b641 | section | Post Construction
0e6a036d-3190-4368-8940-cb51166bd55d | checkpoint | As-Built Drawings
e1b9af54-7983-559a-b25c-16fc57a861c5 | note | SPECIFICATION REFERENCE: Wastewater Specification B.2.18.1
37c186ab-1dec-5186-bc0e-203f61f5fbd3 | note | TEST/TASK REQUIRED: As-built records and coordinate data
08440565-fcf9-51f5-a00a-3eb3a038f364 | note | INSPECTION BY: UCCL
c65659af-49a0-5a0f-b910-fdcb6b4f6cab | note | TASK TIMING OR TASK FREQUENCY : Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion.
fb5865aa-16f8-541a-b77d-6dd450e0cac3 | note | ○ Final as-builts issued prior to Final Completion.
89a51099-025c-5e67-a8c0-8d281cef24b8 | note | ACCEPTANCE CRITERIA: As-builts submitted to the Engineer for approval.
d02b0afc-712e-4ddc-9bbd-2b43bb42dae2 | checkpoint | CCTV
1caea204-bee6-52f6-abdc-1d8326ec4f49 | note | SPECIFICATION REFERENCE: Wastewater Specification B.2.18.2
d72523d9-b0ab-5f89-818d-7b26fd5d1c4d | note | TEST/TASK REQUIRED: CCTV video survey to the National Standards
f32162ef-3801-56da-8bff-e34fd6f66be2 | note | INSPECTION BY: UCCL
8e746ac0-363e-5995-84da-efa82d7e3f07 | note | TASK TIMING OR TASK FREQUENCY : On completion of the installation of each pipeline with backfill to the top of the pipe.
942eab34-e40b-5faf-aff2-4ba2134119fe | note | ACCEPTANCE CRITERIA: CCTV results submitted to Engineer for approval.
a2f1d806-93c8-4c51-8b1c-68b3bf42e925 | checkpoint | RAMM Information
7a0ec8b6-c11d-55d9-b549-a8ceb636c46c | note | SPECIFICATION REFERENCE: Wastewater Specifcation B.2.18.3
fe731bd0-d052-5b7c-92bc-35f1ffaa5e4a | note | TEST/TASK REQUIRED: RAMM information
51cee11a-e294-5613-80a5-2c8d4cef4c97 | note | INSPECTION BY: UCCL
373be550-9e5f-5eb7-959c-587a940906d4 | note | TASK TIMING OR TASK FREQUENCY : RAMM information submitted to the Engineer on completion of works.
c241db5b-10b3-56b3-85c1-6577e95a65ca | note | ACCEPTANCE CRITERIA: RAMM information submitted to the Engineer.
ed6cc460-ac9e-4eff-93ee-ec2affcdc29b | checklist | ITP - Water Reticuation | itp | ITP - Water Reticuation
c99ae8fd-074c-43b9-bf73-fc0fabd4c9f5 | section | Preconstruction
1fb82105-91e6-41a6-b8bf-972ca3a2061c | checkpoint | Precondition Survey
845fac82-7fea-5366-8599-9bffcbb1b3ff | note | SPECIFICATION REFERENCE: Water Specification B.2.11.2.2
5b231f43-a8ba-55c8-8ff5-d032ee20e393 | note | TEST/TASK REQUIRED: Visual inspection
b8d89ab6-f4cd-529b-a581-9dae213db4a0 | note | INSPECTION BY: UCCL
75036255-26c5-5d06-92cf-fbb09694b4b2 | note | TASK TIMING OR TASK FREQUENCY : Prior to starting on site.
95d97d7e-aaf2-5fae-aafd-dac6e0702775 | note | ○ Survey conducted of all surfaces and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works.
007ae91e-c560-5cef-9fb8-d366c485fccb | note | ACCEPTANCE CRITERIA: Survey documents submitted to Engineer.
686b7475-7366-41d9-87cd-984bcbe9b1d0 | checkpoint | Materials Quality
ad7fec6b-5240-5956-a854-8baf0de219b9 | note | SPECIFICATION REFERENCE: FNDC Approved Materials List - Water Services
dcf853e2-ed9c-508a-86e5-440caf41b7ef | note | TEST/TASK REQUIRED: Visual check for approved materials, quality and condition.
5a5825f1-c7a1-5aea-aa20-69f8d0499a49 | note | INSPECTION BY: UCCL
8c089a9b-a39c-5bf1-b529-f1ff7f2d80f4 | note | TASK TIMING OR TASK FREQUENCY : On arrival to site, prior to using materials.
bb8d2e08-d396-5444-b420-6d28fa75f44d | note | ACCEPTANCE CRITERIA: Materials meet specifications or otherwise approved by Engineer.
17fd7059-05fb-517d-87e6-5b86f760dee3 | note | ○ Delivery dockets.
1c37c735-4658-5389-b26b-831e73d75c4b | note | ○ Photos.
2221bce0-50ff-43a7-9ded-bd650c2907b2 | checkpoint | Survey Setout
1da70ff8-a83b-526c-bde1-b5d63c558480 | note | SPECIFICATION REFERENCE: Water Specification B.2.11.2.4
9d02915b-5a93-5e32-b51e-90f5b94d292e | note | TEST/TASK REQUIRED: Survey set out.
c3479be1-bc74-56ed-a47b-362dc1098678 | note | INSPECTION BY: UCCL
759025ce-8b5e-5d1c-b713-b238d6260bd8 | note | TASK TIMING OR TASK FREQUENCY : Prior to commencing each stage of work.
135aa476-ef8c-5935-af2a-daffa9169462 | note | ○ Engineer to be notified if any concerns
5844cd2a-58ba-5804-b30d-40ac9d445ce5 | note | ACCEPTANCE CRITERIA: Survey set out as per IFC drawings.
20480e7f-a136-4664-a9df-a40ab467352b | checkpoint | Service Location
01ba9c58-6cf4-50e9-95d0-a18b14fa7e08 | note | SPECIFICATION REFERENCE: Water Specification B.2.11.4.2
c150305c-0deb-574f-8fba-d72786acef4a | note | TEST/TASK REQUIRED: Locate underground services within work area.
b4aafe7b-a78d-51de-ae06-cb5f4ec7c349 | note | INSPECTION BY: UCCL
bb26e057-af88-5673-b83d-e3a5a2c91c6f | note | TASK TIMING OR TASK FREQUENCY : Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services.
4b506942-8585-5ccd-8453-a18727788aa0 | note | ACCEPTANCE CRITERIA:
3bafc20e-fc38-4102-9a8d-67b4de0461ad | section | Installation
5aa0b962-8fc3-4c8b-b7de-5a08d2324274 | checkpoint | Material Properties (Bedding) (1)
2e46aa5f-5399-53c6-8ea7-f1e2439750fc | note | SPECIFICATION REFERENCE: Water Specification B.5.5.1.13
a50b9401-5ff4-595b-9252-d47de78dc2fc | note | TEST/TASK REQUIRED: GAP20 grading curve to be submitted to Engineer for approval
adaec7a2-de12-56cd-b48f-16610f561aaf | note | INSPECTION BY: UCCL
3f58d0ad-6fc6-5ea0-8e3d-1d7fe63b925c | note | ○ Haigh Workman
b4459f87-1776-5531-8cdf-0ca8cf744be7 | note | TASK TIMING OR TASK FREQUENCY : Prior to using bedding material on site.
8cff7680-6601-59b9-8149-d2bf77b4235d | note | ○ PE bedding, pipe surround and haunching shall be GAP20 in accordance with AS/NZS 2566.
3710be17-f406-5f05-946b-7262fbdd58c0 | note | ACCEPTANCE CRITERIA: Bedding grading curve accepted by Engineer.
| checkpoint | Material Properties (Bedding) (2)
| note | SPECIFICATION REFERENCE: NTC020
| note | TEST/TASK REQUIRED: Aggregate Testing Frequency
| note | INSPECTION BY: UCCL, Haigh Workman
| note | TASK TIMING OR TASK FREQUENCY : PSD (Grading): 1 test per 500m3
| note | ○ Estimated requirement: 2 tests for ~1080m3
| note | ACCEPTANCE CRITERIA: Bedding material test certificates accepted by Engineer.
36fea487-4001-4231-9c02-d50f7731c287 | checkpoint | Material Properties (Subbase) (1)
452c8aec-ae02-5136-b09b-95cf8146d271 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
114def64-700b-5088-b3d8-9a2c52da53eb | note | TEST/TASK REQUIRED: Subbase material meets FNDC Engineering Standards
215bd4b8-df09-5777-a28a-2cdd19cfb0c9 | note | INSPECTION BY: UCCL
586ae9e2-1696-5ee9-8c02-87ea0bfe4f51 | note | ○ Haigh Workman
3e0175f6-fa74-5c96-b723-1971d840c087 | note | TASK TIMING OR TASK FREQUENCY : Prior to using subbase material on site.
d0610e90-7675-57b1-9148-652b8d9b0ec1 | note | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
| checkpoint | Material Properties (Subbase) (2)
| note | SPECIFICATION REFERENCE: NTC020
| note | TEST/TASK REQUIRED: Aggregate Testing Frequency
| note | INSPECTION BY: UCCL, Haigh Workman
| note | TASK TIMING OR TASK FREQUENCY : PSD (Grading): 1 test per 2000m3
| note | ○ Estimated requirement: 8 tests for ~15,853m3
| note | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
1756e81c-c7a0-4933-a7bb-848241d41ffd | checkpoint | Material Properties (Basecourse) (1)
60863e98-16ae-51be-bd0e-ca8d5fe6c2da | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
33817821-ae38-5b67-9672-657745d656cb | note | TEST/TASK REQUIRED: Basecourse material meets FNDC Engineering Standards
d759e3e4-42c1-527a-9bd0-dd68fed17eb8 | note | INSPECTION BY: UCCL
abc577b8-d353-5998-8b7e-78efb912a089 | note | ○ Haigh Workman
5fbd3687-f4b2-5268-bf2c-8b553c179fcc | note | TASK TIMING OR TASK FREQUENCY : Prior to using basecourse material on site.
df4d7fd0-8e18-5a34-9fa3-77bc6d6f0c71 | note | ACCEPTANCE CRITERIA: Basecourse material test certificates accepted by Engineer.
| checkpoint | Material Properties (Basecourse) (2)
| note | SPECIFICATION REFERENCE: NTC020
| note | TEST/TASK REQUIRED: Aggregate Testing Frequency
| note | INSPECTION BY: UCCL, Haigh Workman
| note | TASK TIMING OR TASK FREQUENCY : PSD (Grading): 1 test per 1000m3
| note | ○ Estimated requirement: 4 tests of each type for ~3240m3
| note | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
6694e172-3d1c-46d2-945d-2d03d00cb6bd | checkpoint | Pipe
06a32790-7a1b-54f8-b374-3cf534a1def0 | note | SPECIFICATION REFERENCE: Water Specification B.5.8.3
07c3fe25-47b3-53f7-a4f5-fbe82ada175b | note | TEST/TASK REQUIRED: Visual inspection
15ed7b3e-a2a0-536f-88d5-b895da8dd60c | note | INSPECTION BY: UCCL
0840673d-a901-54b3-a47a-10c640145f33 | note | TASK TIMING OR TASK FREQUENCY : Visual inspection prior to use (clean and free from defects).
7d579e27-5c7e-5ac7-8254-38e0fe91401a | note | ACCEPTANCE CRITERIA: Photographs.
24ee523b-375b-431e-80b8-13b9a2894ac6 | checkpoint | Test Welds (Butt Welding)
978ed83a-fe46-5fd4-9ad5-fd57dab2fcfd | note | SPECIFICATION REFERENCE: Water Specification B.5.10.2.2
0a60a3e1-4844-59b0-9379-309e6c771c27 | note | TEST/TASK REQUIRED: Laboratory testing
244940d2-4c51-5341-94d6-ca586f30d386 | note | INSPECTION BY: UCCL
8f089677-da87-576b-9177-912478b31965 | note | ○ Haigh Workman
25de6d57-89e6-593b-a97c-992b8ec5aa42 | note | TASK TIMING OR TASK FREQUENCY : Three butt welded joints and one section of virgin pipe shall be tested in accordance with ISO 13953.
85a516fa-4006-5b98-b86e-1d894368e848 | note | ○ One test weld for every 10 lengths of pipe laid.
35c481fe-b142-5245-89b4-544f19d62032 | note | ACCEPTANCE CRITERIA: Weld test results submitted to Engineer.
689c61ca-4c0f-4532-91c9-8f8ddcc92b6e | checkpoint | Welded Joints (Butt Welding)
13751480-ae35-5fb2-b516-d35ba16fc767 | note | SPECIFICATION REFERENCE: Water Specification B.5.10.2.1
ce36c2f4-6d45-5f87-b46b-61d771dc89aa | note | TEST/TASK REQUIRED: Visual inspection
4ff61144-edde-5222-b605-53cdb6a594df | note | INSPECTION BY: UCCL
476a4616-54c9-597f-9ea5-143ddb4e2e4f | note | TASK TIMING OR TASK FREQUENCY : On completion of each butt weld.
01021c8d-2336-52d9-a2af-abe290a3a361 | note | ○ Weld inspection checklist.
145f4130-f4af-5c8c-9819-c107e8ee41b3 | note | ○ Weld data log.
1319dd5c-456e-5791-bb46-17dfe3136f19 | note | ACCEPTANCE CRITERIA: Weld inspection checklist submitted for each butt weld.
0b9291b7-28be-592d-873d-199579e7a7a1 | note | ○ Weld data log submitted for each weld.
ffb37357-5ab4-4c45-a537-8f4229d4be28 | checkpoint | Welded Joints (EF Welding)
06447b36-b181-5d6e-9321-53c1ef44d5cd | note | SPECIFICATION REFERENCE: Water Specification B.5.10.2.1
74eec366-d184-50ff-ac22-bed7f317695d | note | TEST/TASK REQUIRED: Visual inspection
2285d7b8-d9b3-5b05-87fb-6c0b53582cd3 | note | INSPECTION BY: UCCL
dfce0c0f-0034-5b0d-ae1e-11e9658c4676 | note | TASK TIMING OR TASK FREQUENCY : On completion of each EF weld.
bcee6051-5dc3-5cb6-92f0-02a3d0483dbd | note | ○ Weld inspection checklist.
c4cef3ee-a6fc-5ea6-865c-abe63e5d8e21 | note | ACCEPTANCE CRITERIA: Weld inspection checklist submitted for each EF weld.
61fd87fb-60cc-4f61-9b3d-7e889b4bd36a | checkpoint | Pipeline Installation (PE)
06d77b32-dc0d-54f0-8d7b-b2e4277a9303 | note | SPECIFICATION REFERENCE: Water Specification B.6.4.5 and B.6.4.6
f920959e-ec78-59e0-98c8-ef3813d97ac7 | note | TEST/TASK REQUIRED: Visual inspection
c7f9c317-fd95-52cd-b1b4-0bb7020b5628 | note | ○ Pipeline installed to correct alignment, grade and level
bef2f3da-65bd-5370-8448-1ba9d5d2732d | note | INSPECTION BY: UCCL
673925d7-a66a-5d90-b7ad-cc57c4ff25b1 | note | TASK TIMING OR TASK FREQUENCY : On completion of installation of each length of pipe, prior to backfilling.
e02f6f26-46c6-5a1e-b424-beaa511c29b1 | note | ○ Horizontal alignment tolerance + 100mm.
29160c39-4b8f-55b2-b7eb-07320ef1eccd | note | ○ Vertical alignment tolerance + 100mm.
ae70c0da-e02c-5e8f-b70f-f3b48b492707 | note | ○ Valves on centreline of pipe permissible vertical deviation of +50mm.
4c142f3a-61f6-5c71-9941-47be9385032d | note | ACCEPTANCE CRITERIA: As-built drawings.
8422a77e-a249-5c1c-bc2c-327b57bdf49f | note | ○ Photographs.
a51bc7ea-39d2-5540-845b-997bd6f9315b | note | ○ Changes to horizontal or vertical alignment to be agreed with Engineer pror
1f6c404c-b682-4648-b561-aba47aba65ab | checkpoint | Valve Installation (including Chambers if required)
c5a0d313-124b-549b-9748-1445512a127f | note | SPECIFICATION REFERENCE: Water Specification B.5.8.4 and B.5.9
a65476ca-7f85-5c08-bded-23ed81d46def | note | ○ FNDC Engineering Standards 6.2.8
db602973-9b5c-5c76-8d93-5039f9d1ff4f | note | TEST/TASK REQUIRED: Visual inspection
a8a71081-fb1c-51c2-8ed7-d4e5c77e8afc | note | INSPECTION BY: UCCL
79454c71-4cf5-5441-af66-08a658be74b0 | note | TASK TIMING OR TASK FREQUENCY : Installed as per specifications.
e47d476e-ebb5-5ab9-9f79-3cd44af35aeb | note | ACCEPTANCE CRITERIA: Photographs.
31a06a15-f1ea-547c-8bb9-bfca0a50733f | note | ○ As-built drawings.
6923020b-778d-4f36-9d73-fd57ab0d168b | checkpoint | Valve Boxes and Markings
102bd963-2b13-5e6b-9f58-a9d49f8c1a92 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.2.8.5, and Sheet 48
9db768b7-de69-530b-a11b-f6daeaa6852e | note | TEST/TASK REQUIRED: Visual inspection
32790ba7-07d7-5325-8d94-c225aed468eb | note | INSPECTION BY: UCCL
5d39fd5f-b3cc-5639-8c29-30402c21d266 | note | TASK TIMING OR TASK FREQUENCY : On completion of installation.
958b6913-6e56-5f2b-bf54-47d52d7a3e1a | note | ○ Valve marker posts and kerb markings as per FNDC standard.
dc9a8da5-75df-528a-938a-f7d4e294c31a | note | ACCEPTANCE CRITERIA: Photographs.
f1e87706-b5dc-42a1-8334-e08aa36c2a51 | checkpoint | Hydrants
36ba94e3-1513-5541-9af1-6abda7b69d4e | note | SPECIFICATION REFERENCE: Water Specifcation B.5.8.4
ffc563ed-a314-5385-8c72-99e2dff43b80 | note | ○ FNDC Engineering Standards 6.2.9.1
43be9a44-15a4-5919-8f2e-eb5f0e173bd5 | note | TEST/TASK REQUIRED: Visual inspection
854f125b-1dc5-5f5e-a4f3-476844820555 | note | INSPECTION BY: UCCL
3caeabba-3229-5681-b36f-2ea69c9309eb | note | TASK TIMING OR TASK FREQUENCY : Installed as per specificationsand IFC drawings.
e90fa78e-4b34-57fe-9ea1-254c3a0ce742 | note | ACCEPTANCE CRITERIA: Photographs.
9e91129e-8d18-541f-80b9-7b623a43c4da | note | ○ As-built drawings.
6904223d-9fbb-4929-9e99-1305ef3bc4b3 | checkpoint | Hydrant Boxes and Markings
6ad88165-8584-588f-956f-62f97d0d1b8f | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.2.9.3, and Sheet 48
7d6c7dde-7ec5-538c-b226-83be4c7370fa | note | TEST/TASK REQUIRED: Visual inspection
5de38c6f-44c2-5274-919f-e9ee194ed450 | note | INSPECTION BY: UCCL
bfd6888e-ff17-51b6-b811-7ec11c8053eb | note | TASK TIMING OR TASK FREQUENCY : On completion of installation.
8cb28e5c-48ba-57f8-8109-ff15c0fccdfe | note | ○ Hydrant marker posts and kerb markings as per FNDC standard.
b6c06a88-c741-564a-bc4c-6a0381436d3a | note | ACCEPTANCE CRITERIA: Photographs.
d534b51c-af03-4ebf-b06b-ed31e3022214 | checkpoint | Air Release Valves
8fd4e6bf-b5f8-51f7-8ff0-865e3b695519 | note | SPECIFICATION REFERENCE: Water Specifcation B.5.5.1.11
3476974b-9b4f-56bc-888e-67a6f2778e94 | note | ○ FNDC Engineering Standards Sheet 51
7bda0259-5671-585d-9dcd-0cc87abaf8cf | note | TEST/TASK REQUIRED: Visual inspection
634a1ec2-4724-5a24-9676-357a2978267e | note | INSPECTION BY: UCCL
770bb539-e4ed-5b51-b8aa-3263f83d5819 | note | TASK TIMING OR TASK FREQUENCY : On completion of installation.
cd45e37a-3687-589c-9c12-dbcbafb21698 | note | ○ Air valves installed to specification
623c5c39-af5e-5e11-b8d8-0edac3eb91aa | note | ACCEPTANCE CRITERIA: Photographs.
e8483ca2-3ce6-5ec2-8941-9889e005b601 | note | ○ As-built drawings.
dbde0589-fc0e-4483-817a-a89889a1699c | checkpoint | Thrust Blocks
ee0362a8-63dd-5f2d-83bf-77e6c0b24783 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.2.3.8, and Sheet 50
54b59261-15b4-5948-9c18-9cfc92570c55 | note | TEST/TASK REQUIRED: Visual inspection
9dc16f4d-bad9-5a54-9e40-b5e0bbdb1589 | note | INSPECTION BY: UCCL
a08fd3af-d7cb-5dd2-b28f-9248730a51c8 | note | TASK TIMING OR TASK FREQUENCY : On completion of the thrust block installation, prior to backfilling.
6269d21d-67f8-5f83-8f00-0851bf7ecf43 | note | ACCEPTANCE CRITERIA: Photographs.
2f58fccf-6c17-4b29-892c-f549b3a1c6fc | checkpoint | Pipe Bedding
802ac9cf-e234-560d-a69e-ea8d59967df4 | note | SPECIFICATION REFERENCE: Water Specification B.3.4.1
960576ed-7924-51f5-bc18-048f69cff3a4 | note | ○ FNDC Engineering Standards Sheet 31
b02995e5-639b-5a2e-9083-2dbdb3c04c56 | note | TEST/TASK REQUIRED: Visual inspection
63c21588-6d8d-555c-8f42-c8d98fd644e7 | note | INSPECTION BY: UCCL
e223787c-490f-5451-b9f4-ef704d39f1e7 | note | TASK TIMING OR TASK FREQUENCY : Bedding installed as per specifications.
fc50cc7b-58ee-5169-97df-d097aabee4d9 | note | ACCEPTANCE CRITERIA: Photographs.
ed2f5e6f-f8f9-455c-bac4-d5c2ef066c3a | checkpoint | Pipe Backfill (Outside of Carriageway)
9f9a3ec7-9e90-5dc1-9c11-575ce76a5040 | note | SPECIFICATION REFERENCE: Water Specification B.3.3.2
f2478267-3230-526c-a5ff-39a529185f1d | note | TEST/TASK REQUIRED: Visual inspection
4d53c71f-15e2-5e78-8e2b-bc19a9d5f3e4 | note | INSPECTION BY: UCCL
5b03035a-d8e1-5158-9cec-4896d7593354 | note | TASK TIMING OR TASK FREQUENCY : On completion of backfill.
977a08d1-6a9e-5987-9af4-b73300472281 | note | ○ Trench backfilled with original sound material from the trench.
1d5c9ef3-d6d0-5e7e-8f01-72c48b6c0375 | note | ACCEPTANCE CRITERIA: Photographs.
f5dd5307-6312-4eb7-acac-874ff555a6e9 | checkpoint | Subbase
8abcb380-b7f9-5b05-8bd8-b2aec4c61b92 | note | SPECIFICATION REFERENCE: Water Specification B.3.5.2
93c4b7d8-a8b4-51e8-8ec5-bde33459a346 | note | ○ FNDC Engineering Standards 3.3.3.3 and Sheet 31
cb414140-bfdb-5f8c-8f0b-1a4afaf84225 | note | TEST/TASK REQUIRED: Visual inspection
b33a9f2f-8008-5446-a989-d6a2cb45c881 | note | ○ NDM testing
da42b502-ff75-57fb-a99a-0b78be089bd3 | note | INSPECTION BY: UCCL
b0a8aff6-c48c-5333-b6b4-39e11fdcd0a7 | note | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of subbase layer, prior to installing basecourse.
d1c47ff5-03a5-5e07-9a72-a69a0b3af09a | note | ○ Backfill and compaction completed as per specifications.
86377d3f-4eb0-58ee-8a16-9b2f501f15eb | note | ACCEPTANCE CRITERIA: Compaction records.
fe0eea5d-680d-528d-ab9c-7cfae20196c7 | note | ○ Photographs.
f2ae13db-12aa-4a38-8a4f-39070d63ba10 | checkpoint | Basecourse
8185ce8a-4353-51e9-867b-e7e20fc56797 | note | SPECIFICATION REFERENCE: Water Specification B.3.5.2
49abcf0c-3f5f-52ea-bc6d-b135fa3d04b5 | note | ○ FNDC Engineering Standards 3.3.3.4 and Sheet 31
03924241-d6b4-5c0d-827e-ffd42f0ac60d | note | TEST/TASK REQUIRED: Visual inspection
1868ce27-300b-5a13-a124-6ce015268fca | note | ○ NDM testing
014914e6-e910-5d52-8621-cf10cfa45329 | note | INSPECTION BY: UCCL
aac49ef3-33de-51a3-afff-b03ecee91c5c | note | ○ Haigh Workman
9c7c0c06-8f09-50e6-8527-f4349b0394b7 | note | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of basecourse layer, prior to sealing.
cccb9f23-334b-5dc3-90d5-2c7d2208a386 | note | ○ Basecourse installed as per FNDC Engineering Standards, and NZTA B/02.
8e09a4d7-6e5a-5ab7-b89d-0df2dc6d2995 | note | ACCEPTANCE CRITERIA: Compaction records.
3bf80ad2-a35e-59ec-922a-117e4b1079c7 | note | ○ Photographs.
ed564e93-f175-471e-85d6-7b7b0762ad36 | signoff | HOLD POINT
de061462-ff7a-484d-9999-3b91c664b611 | checkpoint | Detection Tape and Tracer Wire
26ac2289-a457-57d3-b135-777ef6ad3c53 | note | SPECIFICATION REFERENCE: Water Specification B.5.5.1.6
ce62eed9-8e1c-5e70-84b2-4c9f769d7f3e | note | ○ FNDC Engineering Standards 6.3.2.4 and Sheet 31
d891a075-69ab-5980-9926-a4845f1a19ff | note | TEST/TASK REQUIRED: Visual inspection and electrical continuity testing
62f15166-b889-50e5-aaf6-38207b7154a3 | note | INSPECTION BY:
8aa568a8-f9a8-58b0-8e62-316901b49dea | note | TASK TIMING OR TASK FREQUENCY : On completion of installation.
d77073a5-72e1-5ae3-aa2e-22156766e15f | note | ○ A blue metallic detection tape labelled 'Water' shall be laid directly above all new non-metallic watermains.
ebcce3f0-d5b5-5a67-9791-e246a5150f50 | note | ○ Tracer cable (2.5mm²) shall be attached to pipe wall at maximum 3.0m intervals.
1499d515-c6ce-5f7a-a3e5-6a17a6496b55 | note | ACCEPTANCE CRITERIA: Electrical continuity test results provided to Engineer.
68811db4-41c2-4296-8d50-5915fb050f0d | checkpoint | Pressure Testing of Pipes
dd76ca5c-0198-5255-a3c8-39217bda84b2 | note | SPECIFICATION REFERENCE: Water Specification B.5.10.1
99584116-12ab-5d86-9cf7-f109f3ad76c1 | note | ○ FNDC Engineering Standards 6.3.3.2
ca694dc3-7f4e-5e81-8b40-5cf1ff560349 | note | TEST/TASK REQUIRED: Pressure test of PE pipeline
9c408a52-3a3e-57a2-82d3-b90925cf05a7 | note | INSPECTION BY: UCCL, FNDC,
19f2ea27-d2c2-5859-b4c0-68b1b3dc4749 | note | ○ Haigh Workman
68a7cd7f-7d19-5290-ab7d-ce3c4504918b | note | TASK TIMING OR TASK FREQUENCY : On completion of installation of PE pipeline, after sufficent backfill has been placed to prevent movement.
bd642279-8b76-5665-bce4-03d95fbeec25 | note | ○ Pressure test as per FNDC Engineering Standard.
138dea5d-d6e2-5fc8-9e50-ddc1b5b22eae | note | ACCEPTANCE CRITERIA: Test results submitted to Engineer.
f129dc70-7993-4960-899b-a0c44e8fa33e | signoff | HOLD POINT
d48641b8-9066-417d-97f1-17b7bed85712 | checkpoint | Flushing and Disinfection
2ea617cf-6004-558c-9664-27df17ca135e | note | SPECIFICATION REFERENCE: Water Specifcation B.5.12.3
36139394-ffbe-504a-b7ea-c063278ffddb | note | ○ FNDC Engineering Standards 6.3.4
6548b2b4-ea8b-5dbc-9370-61af6da5884d | note | TEST/TASK REQUIRED: Visual inspection (flushing)
da174ed0-ff35-5d7e-8229-a7b393fbaeb9 | note | ○ Chlorination and testing
738aef9c-9857-580f-aacb-812385455494 | note | INSPECTION BY: UCCL, FNDC,
009e3f97-c85a-5643-a8ef-9ff025b094a8 | note | ○ Haigh Workman
a6bb065d-dbae-5535-a1aa-f6548da646ca | note | TASK TIMING OR TASK FREQUENCY : On completion of pressure test, prior to connection.
36e8bbd5-3a2d-58f6-a63e-f73f9763eaec | note | ○ Flushing and chlorination/testing completed as per specifications. Results meet FNDC specification.
3bd88fbc-7a5d-5052-9eef-92ebb7ec3573 | note | ACCEPTANCE CRITERIA: Test results provided to Engineer for approval prior to connection.
adedacd8-7eec-486c-b90a-75d0749c7d94 | signoff | HOLD POINT
779004bb-461e-41db-8fcd-ad6640cb87a6 | checkpoint | Connection to Existing Watermains
c2a92230-3c1a-5138-88dc-2ac09f7ce06e | note | SPECIFICATION REFERENCE: Water Specification B.5.12.4
6bdce408-d04b-5848-980c-6ca4fdf4ad74 | note | ○ FNDC Engineering Standards 6.3.5
ae801d85-6615-5080-9627-73c47ae465fc | note | TEST/TASK REQUIRED: Watermain connection
7cfdd2df-6d46-52e8-b425-f3eb9d50e888 | note | INSPECTION BY: UCCL, FNDC,
54964bb3-35f6-59e9-9e91-c7609dcdb7f0 | note | ○ Haigh Workman
f57c2058-ba21-52b4-a306-87caba61c729 | note | TASK TIMING OR TASK FREQUENCY : Connection to be completed after instruction from Engineer.
d9720c3c-305e-5610-9256-b1d54bf04d00 | note | ○ Note from FNDC Engineering Standard - "Only the FNDC's Reticulation Maintenance Contractor may undertake the connection".
d4e0f585-e658-5d29-a4e4-8f0640600812 | note | ACCEPTANCE CRITERIA: Photographs.
e5a45a67-945f-4ed6-a99e-ad25c6fa155b | signoff | HOLD POINT
50863d16-c217-40b5-a101-c7d241c1a609 | checkpoint | Service Connections
8bbca392-2cd7-5b97-8389-0e7ceeb16cb6 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.3.2.2 and Sheet 46
ae89c28d-bc01-593a-b8c7-12f3d3faac4a | note | TEST/TASK REQUIRED: Water connection
59ad669e-ef93-5b26-ad84-acad5e54a01e | note | INSPECTION BY: UCCL
c7712371-44e3-5f5b-b9cb-8893657f08c1 | note | TASK TIMING OR TASK FREQUENCY : Connection to be completed after instruction from Engineer.
d6272425-5603-5daa-878d-ab0efcd759ba | note | ACCEPTANCE CRITERIA: Photographs.
13307cc2-771d-57af-a969-1d655c38632d | note | ○ As-built drawings.
9eb75241-14df-4beb-bd05-efb6f5bdb72c | checkpoint | Reinstate Driveways
2eb98d06-eba6-5c7d-8ca5-77a1594f0b0f | note | SPECIFICATION REFERENCE: Water Specification B.3.7.6
ba86964c-ccbd-5820-a612-1c3361f217ef | note | TEST/TASK REQUIRED: Visual inspection
60802251-784a-56b2-a068-d95fe2efe5e3 | note | INSPECTION BY: UCCL
b619a545-41be-5891-a0cc-240ff966a7af | note | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
a75ce16a-ffd3-55cd-a7e2-d269c701f090 | note | ○ Driveways reinstated in the same material and to the same standard as existing prior to works.
8fc235de-8cdf-538a-b16b-cfc1890c01c4 | note | ACCEPTANCE CRITERIA: Photographs.
e83bade3-48b5-496d-a865-e259c1a22a43 | checkpoint | Reinstate Footpaths
c3a36a8e-025b-508c-b5d9-c30b33eb7623 | note | SPECIFICATION REFERENCE: Water Specification B.3.7.6
4c7b8922-280e-50d3-be00-0a72366aca82 | note | TEST/TASK REQUIRED: Visual inspection
a140a0aa-3a42-51c9-b92a-2597728a82e9 | note | INSPECTION BY: UCCL
0b0167a3-ad7e-5d15-bf5b-d9d63e16564b | note | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
63d0bf9d-e548-5451-b924-320fa5029854 | note | ○ Footpaths reinstated in the same material and dimensions but constructed to FNDC Footpath Standards.
715eb443-5888-5277-933a-bda3bab9c9d7 | note | ACCEPTANCE CRITERIA: Concrete dockets.
a12d29a1-61c5-5f13-83f6-96fed9678349 | note | ○ Photographs.
ca41cbe4-7a19-4251-ac32-5ae3b92bf45f | checkpoint | Reinstate Kerb and Channel
ebecc12b-5291-527b-8c94-31978026bb2e | note | SPECIFICATION REFERENCE: Water Specification B.3.7.6
a4fb346d-14ec-5b65-9567-3e7fe565b7ad | note | TEST/TASK REQUIRED: Visual inspection
12a1dbde-50c3-5390-b091-e64085580eeb | note | INSPECTION BY: UCCL
eac07fc6-dcd0-5fb0-adf2-0ed5b755401d | note | TASK TIMING OR TASK FREQUENCY : Replacement kerb and channel profiles match line and level of existing kerb and channel.
79b97941-59ff-5a7f-9c90-08087fe4aee9 | note | ○ Concrete has minimum 28-day strength of 25MPa.
fd655c7b-c128-53e1-a248-3789889ea8b7 | note | ACCEPTANCE CRITERIA: Photographs.
f63750b4-54d6-40f6-9ac5-5d07d43172da | checkpoint | Concrete Pour (Stuctural - Pipe Bridge Footings, Commercial Driveways)
f18db20e-21c4-513d-8a1c-afafe7cc18f8 | note | SPECIFICATION REFERENCE: Water Specification B.4.4.2
93d887fa-4a3a-508e-84e9-11a404b0779f | note | TEST/TASK REQUIRED: Prepour inspection
3287ac22-f0c7-5e44-a2ab-b36ba7614904 | note | INSPECTION BY: UCCL
83c5b3ae-95a3-5884-a2cb-d623c3f56aad | note | ○ Haigh Workman
af847fd1-40fe-5e4c-91b2-a2cf58c0a8ad | note | TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete.
3b64facf-2d2c-5b45-8011-4941773d3c13 | note | ACCEPTANCE CRITERIA: Pre-pour inspection checklist.
d210cab6-9c76-5ae3-8307-d0b081461ddc | note | ○ Concrete dockets.
c03637d8-036e-511c-bfc4-55e9f1f5a61a | note | ○ Photographs.
8817445f-10bb-491e-a53a-89f18c92f147 | checkpoint | Concrete Pour (Non-Structural - Footpaths, Residential Driveways)
8e3a9bdc-eb6f-515f-9540-986701d83927 | note | SPECIFICATION REFERENCE: FNDC Engineering Standards Sheets 12, 17 and 18
405de9c4-366d-5714-94c1-442582a60146 | note | TEST/TASK REQUIRED: Visual inspection
6d8dff0a-23e0-58d4-bd85-ad0c6870b47e | note | INSPECTION BY: UCCL
d4179f97-cc78-5f40-b373-7d4e8f471434 | note | TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete.
338d2a99-5347-5689-9af2-4df316704197 | note | ACCEPTANCE CRITERIA: Pre-pour inspection checklist.
9b811699-2405-5dfa-856b-5d82aa06fda5 | note | ○ Concrete dockets.
f5cd028c-1e17-5e6f-a4d7-4a90c4398df7 | note | ○ Photographs.
4e9fa573-228d-42db-8b9d-d759e73c2b13 | checkpoint | Asphaltic Concrete Layer (DG10)
fb9d1ad7-1993-5b0e-9221-347447816d42 | note | SPECIFICATION REFERENCE: NZTA M10 Specification
d7e93982-b1b0-5771-9ca3-84e94a1f4e5e | note | TEST/TASK REQUIRED: As per NZTA M10 Specification
353772aa-2a62-5721-84a8-bb86b7f78f99 | note | INSPECTION BY: UCCL
defeb214-9816-5155-a328-1f7b398fd444 | note | TASK TIMING OR TASK FREQUENCY : On completion of the pavement surface.
7a9c2614-e702-5573-a3d7-55d29d9831b4 | note | ACCEPTANCE CRITERIA: Test results submitted to Engineer.
3baccfa2-5f9d-5479-8132-0632857adb91 | note | ○ Photographs.
5d99da3f-2f78-4271-b1e4-875148fd36df | checkpoint | Grout Filling of Redundant Watermains
389138d6-3707-59b5-b744-ea85c196481a | note | SPECIFICATION REFERENCE: Water Supply Drawings Notes, No. 20.1 and 20.2
efd9264f-1a37-5c61-971a-d5d10ac3b435 | note | TEST/TASK REQUIRED: Redundant watermains to be grout filled and remain in place.
72021d4d-1a1c-534d-9408-f5a37427fb07 | note | ○ Remove redundant valve boxes, signs etc.
c49bde83-ecd5-5573-b769-2856eba8d96e | note | INSPECTION BY: UCCL
b3def3d2-9720-556b-bf94-2c57308c83a5 | note | TASK TIMING OR TASK FREQUENCY : Grout filling on completion of new pipelines.
185414d8-7484-5fe6-8e78-f22a07822ff9 | note | ACCEPTANCE CRITERIA: Grouting record.
8224f903-3705-5337-bbb8-59cef3890764 | note | ○ Photographs.
48732eed-cc2e-4489-8aca-16a35d93a5ff | section | Post Construction
5652c1fd-ff87-44f5-b361-6c77b27e80e6 | checkpoint | As-Built Drawings
f59e955d-0140-54ca-b7bd-7b22801dc660 | note | SPECIFICATION REFERENCE: Water Specifcation B.2.18.1
263c2ccb-6106-5d26-a3ba-19d31ca449c4 | note | TEST/TASK REQUIRED: As-built drawings meet FNDC specification
c9b35a5f-8f89-5980-b71b-ec195496b4f3 | note | INSPECTION BY: UCCL
7e761dcf-ceff-5e92-a236-9064a927c3ef | note | TASK TIMING OR TASK FREQUENCY : Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion.
e89ae773-3b4a-5139-926d-ea6b61f09351 | note | ○ Final as-builts issued prior to Final Completion.
71d34136-d67d-5fa5-80f3-fb5184911df8 | note | ACCEPTANCE CRITERIA: As-buiilts submitted to the Engineer for approval.
5aef8011-56fb-4015-b3ed-8157614dbad8 | checkpoint | RAMM Information
e65256d5-b43c-547f-b73e-9df7674e4ede | note | SPECIFICATION REFERENCE: Water Specification B.2.18.2
45483781-794d-519c-af86-16ee76a8c8b0 | note | TEST/TASK REQUIRED: RAMM information
1a23885e-6f60-5a93-9fd9-743e2d38adbb | note | INSPECTION BY: UCCL
0a3e252e-17ea-5e1d-821a-3da2696040b4 | note | TASK TIMING OR TASK FREQUENCY : RAMM information submitted to the Engineer on completion of works.
604e6982-56de-5e32-a770-ec87296af34d | note | ACCEPTANCE CRITERIA: RAMM information submitted to the Engineer.