## Table 1
ITP Inspection and Test Plan
Project Title: WDC Fluoridation | [6 empty] | Project No: CON23011 (internal #J2028) | [7 empty] | Procedure No:
Description of Activity: Ruddell’s WTP Chemical storage bund (Civil Works) | [13 empty] | ITP No.: 001
Location of Inspection / Testing: Ruddells WTP | [9 empty] | ITP Approved by (BCL) Name: Stephen Abercrombie Date: 11/01//24
ITP Prepared by: Stephen Abercrombie Date: 11/01/2024 | [9 empty] | ITP Approved by (Client) Name: WDC Date:
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  | Inspection Responsibility | [9 empty] | Verification Records of Inspection(s) / Test(s)
[13 empty] | BCL | [5 empty] | Client |  | Date
1 | Documentation
1.1 | Construction Drawings |  |  | All drawings are for construction and latest revision. | [5 empty] | Latest IFC Drawings |  |  | I | [5 empty] | S |  |  |  | Drawing Register
1.2 | Concrete mix design |  |  | Submitted to Beca for approval | [5 empty] | Approved RFI |  |  | H | [5 empty] | A |  |  |  | RFI
2 | Fence Relocation/Swale works
2.1 | Set Out, as per latest “For Construction” revision |  |  | Survey and mark the correct locations Check Boundary location | [5 empty] | IFC Drawings Survey data check by PM and Beca Engineer |  |  | D | [5 empty] | A |  |  |  | Survey Record, Redline Drawings Approved RFI
2.2 | Install new relocated fence to match existing |  |  | New fence matches existing | [5 empty] | Witness by engineer |  |  | I | [5 empty] | R |  |  |  | Photos
2.3 | Place rock riprap |  |  | 75-200mm size rock, 1m wide at top side to 1.5m wide at bottom end | [5 empty] | Witness by Engineer |  |  | I | [5 empty] | R |  |  |  | Photos
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  | Inspection Responsibility | [9 empty] | Verification Records of Inspection(s) / Test(s)
[13 empty] | BCL | [5 empty] | Client |  | Date
(inspected once at end of works)
3 | Excavation
3.1 | Set Out, as per latest “For Construction” revision |  |  | Survey and mark the bund location | [5 empty] | IFC Drawings Survey data check by PM |  |  | T | [5 empty] | I |  |  |  | Survey Record, Redline Drawings
3.2 | Subgrade inspection |  |  | Scala testing to confirm subgrade is of sufficient strength Witness by engineer Minimum of 2 tests per bund pour | [5 empty] | Minimum of 5 blows per 150mm |  |  | H | [5 empty] | A |  |  |  | Scala Test Results
3.3 | Ground Contaminants |  |  | Soil testing to confirm no contaminants | [5 empty] | Test results clear for clean fill |  |  | T | [5 empty] | R |  |  |  | Lab test report
5 | Post Excavation
5.1 | >150mm compacted hard fill under bund (GAP20) |  |  | Clegg hammer testing, 5x5 grid, minimum of 4no per bund pour | [5 empty] | Clegg CIV>10 |  |  | T | [5 empty] | R |  |  |  | Clegg results
6 | Concrete works
6.1 | Site concrete |  |  | Visual inspection and record of site concrete install, completed for each slab pour | [5 empty] | 50mm site concrete poured to base level of foundation +0mm - 10mm tolerance |  |  | D | [5 empty] | W |  |  |  | Photos Concrete pour record
6.2 | DPM |  |  | Visual inspection and record of DPM installed, completed prior to each pour | [5 empty] | Polythene laid on site concrete prior to reinforcing |  |  | D | [5 empty] | W |  |  |  | Photos Concrete pour record
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  | Inspection Responsibility | [9 empty] | Verification Records of Inspection(s) / Test(s)
[13 empty] | BCL | [5 empty] | Client |  | Date
6.3 | Reinforcing (material) |  |  | Review documentation for each pour | [5 empty] | Reinforcing to be Grade 500E to ASS/NZS4671 |  |  | D | [5 empty] | W |  |  |  | Mill certificates Detail sheet
6.4 | Sump Construction |  |  | Reinforcing check, dimension check, Formwork check | [5 empty] | As per IFC drawings |  |  | D | [5 empty] | W |  |  |  | Concrete pour record
6.5 | Reinforcing install |  |  | Measure to check cover, bar size and arrangement, lap length and type. Complete prior to pouring concrete | [5 empty] | Reinforcing matches IFC drawings, any deviations recorded and acceptance agreed with engineer prior to pour |  |  | D | [5 empty] | W |  |  |  | Concrete pour record Photos
6.6 | Reinforcing install |  |  | Starter bars for tank plinth Starter bars for blockwork | [5 empty] | Matches IFC drawing |  |  | D | [5 empty] | W |  |  |  | Concrete pour record Photos
6.7 | Tank plinth |  |  | Size of plinth, height of plinth Reinforcing checked, Formwork checked | [5 empty] | Matches IFC drawing and response of RFI017 |  |  | D | [5 empty] | W |  |  |  | Concrete pour record Photos
6.8 | Concrete pour |  |  | Embedded items located in slab - Ducting - Pits | [5 empty] | Matches IFC drawings |  |  | D | [5 empty] | W |  |  |  | Concrete pour record photos
6.9 | Concrete pour |  |  | Level check, formwork check, cover check. Inspections prior to every pour | [5 empty] | Matches IFC drawing dimensions and notes |  |  | D | [5 empty] | W |  |  |  | Concrete pour record
6.1 | Pour inspection/Approval to pour |  |  | Pre pour inspection by Beca Engineer (hold Point) | [5 empty] | Approval from Engineer to pour |  |  | H | [5 empty] | A
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  | Inspection Responsibility | [9 empty] | Verification Records of Inspection(s) / Test(s)
[13 empty] | BCL | [5 empty] | Client |  | Date
6.1 | Concrete strength |  |  | Test certificate 7 and 2no 28day tests required for each pour day or per 70m3 | [5 empty] | 28 day compressive strength >40mPa |  |  | D | [5 empty] | R |  |  |  | Test certificate
7 | Blockwork
7.1 | Blockwork (material) |  |  | Manufacturer documentation. Required once prior to commencement of works | [5 empty] | Masonry units meet AS/NZS4455 |  |  | D | [5 empty] | R |  |  |  | Supplier documentation
7.2 | Blockwork (reinforcing) |  |  | Inspect bar size, placement, lap length and number (once per pour) | [5 empty] | Install matches IFC drawings and notes. Deviations agreed with engineer via approved RFI |  |  | D | [5 empty] | R |  |  |  | Concrete pour record
7.3 | Blockwork (pour) |  |  | Inspection prior to pour, check washout location, dimensions, line and level (once per pour) | [5 empty] | Install matches IFC drawings and notes. Deviations agreed with engineer via approved RFI |  |  | W | [5 empty] | A |  |  |  | Concrete pour record
7.4 | Concrete strength |  |  | Test certificate 7 and 2no 28day tests required for each pour day | [5 empty] | 28 day compressive strength >17.5mPa |  |  | R | [5 empty] | R |  |  |  | Test certificate
8 | Bund Liner
8.1 | Pre lining check (post pour) |  |  | Square edges on all corners | [5 empty] | Placon check |  |  | W | [9 empty] | Photos
ID No | Sequence of Activity |  |  | Type of inspect / Test and Frequency | [5 empty] | Acceptance Criteria |  |  | Inspection Responsibility | [9 empty] | Verification Records of Inspection(s) / Test(s)
[13 empty] | BCL | [5 empty] | Client | Date
Concrete surface cleaned – all excess grout/splatters removed
8.2 | Watertightness of bund |  |  | Flood test of bund | [5 empty] | No leak, Water stable over 3 days (taking into account for evaporation, wind) |  |  | I |  |  |  | I |  | W |  |  |  | Photos, drop in water height measurement
9 | As-builts
9.1 | Redline Drawings |  |  | Redline Civil Drawings Sets post construction | [5 empty] | N/A |  |  | D | [5 empty] | R |  |  |  | As built drawings
Revision Status of ITP | [7 empty] | Inspection Responsibility Legend | [11 empty] | Records Legend
Rev. No: Rev. (ID No’s) Date: Approved by: |  | Revision 1: | Revision 2: |  |  | Revision 3: |  | A: D: I: S.Con: |  | Approve Document Inspection Subcontractor | H: R: S: | Hold Point Review Submit |  |  |  | T: V: W: Cons: |  | Test Visual Witness Consultant |  | ITR: Inspection and Test Report HPR: Hold Point Release form
Signature Verification Record
Sign |  |  |  |  | Name |  |  |  | Position / Title | [12 empty] | Company