## ITP02 - Service Duct
INSPECTION & TEST PLAN
|  | Contract Name: | [6 empty] | Rev: | Originator | Date | Approved | Date
[5 empty] | Hold Point (H) | Verify (V) |  |  | 1 | Michael Polglase | 2023-11-13
ITP02 - Service Ducting |  | 7020 Meridian Ruakaka Civil Works - Duct Installation |  |  | Submit (S) | Review (R) |  |  | 2 | J Welch | 2024-02-29
[5 empty] | Approve(A) | Witness (W)
Surveillance (SU)
TASK | SPECIFICATION REFERENCE | TEST/TASK REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL Signature | Client Signature | UCCL | Client | DATE | COMMENTS
Preconstruction
Review of proposed work |  | Drawings to be reviewed and permission to proceed given. | UCCL, MEL | Prior to Ordering Materials | Drawings to be IFC |  |  | R | A
Survey Setout |  | Initial Setout by Surveyor | UCCL | Prior to Installation | Surveyor to set out prior to construction |  |  | V | A
Service Ducts | 14.4 Specification for laying Cable Ducts | PVC Heavy Duty Electrical Ducts 50mm, 100mm and 150mm diameter. Colours as specified on drawings | UCCL | Prior to Installation | Supplier Documentation |  |  | S | A
Installation
Installation of 100mm Ducts Between PCS Slab and Containers |  | Visual Inspection | Meridian | On completion of the installation of each set of 100mm ducts. | Orange 100mm ducts from PCS slab to container installed to correct line and depth. |  |  | V | A
Installation of 50mm Ducts Between PCS Slab and Containers |  | Visual Inspection | Meridian | On completion of the installation of each set of 50mm coloured ducts. | Coloured 50mm ducts from PCS slab to containers installed to correct line and depth. |  |  | H | V
Thermal Backfill (as directed by principal) | Civil Works Specification 6.4 Amended to pleatu test for accepted MDD Refer MAIL NUMBER WSP-CONSC-000319 REFERENCE NUMBER MELNZ-RFI-000265 | Visual Inspection | UCCL | Following instalaltion of ducts, where specified | 10 passes with plate compactor, per MELNZ-RFI-000310 |  |  | V | A
Sand Backfill | Civil Works Specification 6.4 Amended to pleatu test for accepted MDD Refer MAIL NUMBER WSP-CONSC-000319 REFERENCE NUMBER MELNZ-RFI-000265 | Visual Inspection | UCCL | Following installation of ducts, where specified. | Self compaction of sand, as per MELNZ-RFI-000310 |  |  | V | A
Flowable Fill | Refer MAIL NUMBER MELNZ-RFI-000393 (Ducting at 101A, 201A, 301A, 401A and 501A requires flowable fill as per drawings supplied) | Visual Inspection | Meridian | Prior to pouring flowable fill over 100mm orande ducts at 101A, 201A, 301A, 401A and 501A. | Orange 100mm ducts from PCS slab to container installed to correct line and depth. Ducts braced and height pegs set for correct cover. |  |  | H | V
AP40 Hardfill Layer | Construction Drawing Set RUK-UMC-DS-01. Also refer MAIL NUMBER MELNZ-CA-000290. | Visual inspection. Cleeg test with minimum CIV value of 25. | UCCL | On completion of AP40 hardfill layer, prior to site concrete. | Minimum CIV of 25. |  |  | V | A
Cable Pits | 14.4 3 Specification for laying Cable Ducts | Supplier Documentation | UCCL |  | Cable pull pits to the dimensions shown on drawings |  |  | V | A
Post Construction
As Built & Final Design Documentation | 14.4 2.3 Specification for laying Cable Ducts | Surveying | UCCL | As constructed | The contractor shall undertake site survey of all duct ends so that they are installed within +/- 15mm of their design location |  |  | S | A
Ducting QA | 14.4 Specification for laying Cable Ducts | Duct Inspection Record | UCCL | Per trench | Duct Inspection Checklist completed per trench |  |  | S | A
Completion of Ducts for Handover |  | Handover Record - Handover of Ducts to Electrical | UCCL | On the completion of duct installation at handover for electrical installation. | Handover record sign by UCCL, Meridian, and Electrical Department. Ducts installation completed, and ducts cleaned ready for electrical installation. |  |  | H | V