## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | PCS Foundations |  |  |  |  | Yes | ITP 01 - PCS Foundations | dc37db2b-ed8d-4af2-ad41-deab064829df
checkpoint-group |  |  | section | Pre Construction
checkpoint-status |  |  | checkpoint | Review of proposed work
label | a015857a-71d5-5832-af51-7d6ef368be0c |  | note | SPECIFICATION REFERENCE - 1235 SHOP DRAWINGS - ITEM 1.10
label | ef6c6de1-ee59-5ee5-a429-24e7eaf63309 |  | note | TEST REQUIRED - Shop drawings to be reviewed and permission to proceed given.
label | 154e7045-facf-5dff-bbd6-adaf0b7b27c7 |  | note | INSPECTION BY - Named reviewer or contract administrator
label | b80015e9-965f-5c56-97ba-c9f5bbfbe1af |  | note | TASK TIMING OR TASK FREQUENCY - Start of task
label | 01b7eda7-c416-5a85-9668-3f87820e9018 |  | note | ACCEPTANCE CRITERIA - Shop drawings to be accepted by the reviewer. Building Information Model (BIM) is being used for the construction works.
label | a14759cf-37fa-5c62-a4ee-085b9c2d8059 |  | note | UCCL - H
label | 102e5c1a-6d9f-5324-9fbd-1e30888e6301 |  | note | Client - A
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Materials
checkpoint-status |  |  | checkpoint | Concrete Mix Design
label | 1ff17b05-ad05-519b-8bb0-633ac33753bc |  | note | SPECIFICATION REFERENCE - Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03
label | a97a66fb-6048-505d-9577-044ae72fa206 |  | note | TEST REQUIRED - Supplier Documentation
label | 19053180-29e3-5142-bb96-ec69b2746d52 |  | note | INSPECTION BY - UCCL, MEL
label | 6e1d0e1e-e0a6-548b-8a20-77e919d36dbb |  | note | TASK TIMING OR TASK FREQUENCY - Each Mix Design used prior to use
label | 7cf45f41-f19b-567b-adf7-c19477e09adc |  | note | ACCEPTANCE CRITERIA -
label | 784760dc-6471-5854-9bb7-169773a952c7 |  | note | Foundations (including retaining wall footing) -
label | f41ee08c-ccd7-537d-835f-dbf98dd3b45e |  | note | ○ Aggregate: 19mm
label | a96be871-a299-5bba-b467-7a3fa0f91799 |  | note | ○ 28 day strength: 35MPa
label | 218d7da3-68d8-552d-b337-0ef392350e92 |  | note | Precast retaining wall -
label | 81f3773d-63ee-5d7a-86d0-a28f1edd7909 |  | note | ○ Aggregate size: 19mm
label | d84c6630-bdb4-552f-b2f0-82858c4c4f0f |  | note | ○ 28 day strength: 35MPa
label | b1bbf60d-f1fa-5abe-85df-986361ab9375 |  | note | UCCL - S
label | 742f6370-e41b-5bc0-b3a7-04d65bff03cb |  | note | Client - R
checkpoint-status |  |  | checkpoint | Certificates
label | 7b0ebe92-d0e8-56d9-96e0-7714567f4052 |  | note | SPECIFICATION REFERENCE - 1.12 Certificates
label | acbe2368-d88f-53b7-8c03-c375576d52bb |  | note | TEST REQUIRED - Portland cement to NZS3121,
label | f838c7b4-d67c-53d3-912e-e1aef33f670e |  | note | INSPECTION BY - UCCL
label | 5c21c7de-3680-5303-80a5-55fa6b07158a |  | note | TASK TIMING OR TASK FREQUENCY - Each Batch
label | 165ace66-0be6-5fa8-ace6-90b106e520c6 |  | note | ACCEPTANCE CRITERIA - NZS 3122
label | 5ee59556-dd41-57ea-81c9-d5eb6b6e3890 |  | note | UCCL - S
label | 2b3f94ef-9938-5352-899d-da864a02cb24 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Reinforcement
label | c3148d81-749a-514d-b3fd-f91ef51bb6f9 |  | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-12
label | 4dbe8d17-c8d0-519c-95f9-628dae26e814 |  | note | TEST REQUIRED - Supplier Documentation, photos of spacings
label | 3ae3e378-ab26-5b93-8fcc-9f130e8a96e0 |  | note | INSPECTION BY - UCCL, MEL
label | f7d3a9c9-b6fd-57bb-8811-82a222db6718 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to pouring
label | bfa44109-6c4b-588b-9946-3bf5018d47c5 |  | note | ACCEPTANCE CRITERIA - Reinforcement of precast retaining wall to be YD12-200 vertical and horizontal with D12-200 starters. Reinforcement of in-situ strip footing to be 2/YD12 with R6-300 stirrups
label | 761c31ac-d8be-5118-a49b-466366c5a7d0 |  | note | UCCL - V
label | 546aed7c-8fae-578d-bef2-b75478898024 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Strip Footing
label | 60946fb8-9c9a-5fe2-84ed-d69c874b85f1 |  | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-12
label | 4d5da26e-cae4-5f25-ad5a-a35df12e4627 |  | note | TEST REQUIRED - Photos
label | 692164fc-48cb-5fd5-a003-c35658400a2a |  | note | INSPECTION BY - UCCL, MEL
label | e98962aa-a219-51df-a1a9-29c4ba1af75d |  | note | TASK TIMING OR TASK FREQUENCY - Prior to pouring
label | 4a636711-f2a7-5553-b860-961af734b14b |  | note | ACCEPTANCE CRITERIA - Reinforcement to have maximum 75mm clearance and minimum 50mm clearance.
checkpoint-status |  |  | checkpoint | Cast in Items - Nuts, Bolts and Studs
label | 28090b9a-138a-5fc3-acb1-d6daf3d28896 |  | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-10
label | 2c5cfa97-9d67-5203-99ec-6ba421522912 |  | note | TEST REQUIRED - Supplier Documentation
label | 55e1de77-fe1a-561a-886c-fc48c5a88179 |  | note | INSPECTION BY - UCCL
label | 05f3ed75-f9ba-5f52-bdef-cece9de0734a |  | note | TASK TIMING OR TASK FREQUENCY - Prior to Ordering
label | 58eb0dab-8ad9-54ac-8e28-96ff93fe5390 |  | note | ACCEPTANCE CRITERIA - EA bolts to be M16 Hilti RE-500
label | d0abf167-119c-5412-ab02-cda277d6b166 |  | note | UCCL - V
label | c9e7c594-bc0a-5d0c-b107-83e30f8d1613 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Air content test
label | e71e4264-4ee2-59ee-9e65-703476b4ee69 |  | note | SPECIFICATION REFERENCE - 1.13
label | 265ca5d3-6375-5dd6-aee1-302c2bf0456a |  | note | TEST REQUIRED - Supplier Documentation/IANZ Laboratory
label | b1c29214-691d-5f5b-bdc4-4438afc6cafa |  | note | INSPECTION BY - UCCL
label | 49e6fff7-e796-5652-9518-2256feed20e6 |  | note | TASK TIMING OR TASK FREQUENCY - Each Batch
label | acb68691-b603-5081-9d26-de7e519de028 |  | note | ACCEPTANCE CRITERIA - NZS3109
label | a73214a9-af49-552b-af6a-9a0be30cd862 |  | note | UCCL - V
label | de677fbb-78ef-502f-9833-600a89ea6d48 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Slump Test
label | cd3ad7ef-006d-54bf-bd65-44906a2c20dd |  | note | SPECIFICATION REFERENCE - 1,13
label | 3982c0cf-80d2-58b7-b2ee-83b2a089daac |  | note | TEST REQUIRED - Supplier Documentation/IANZ Laboratory
label | e148d26b-6899-5609-ab80-e89f551ebee1 |  | note | INSPECTION BY - UCCL
label | f32983b1-aaf3-55d0-a5ae-0a705e7d993e |  | note | TASK TIMING OR TASK FREQUENCY - Each Batch
label | 80471948-7ff8-57fa-8ee6-aed5e29b82b8 |  | note | ACCEPTANCE CRITERIA - NZS3109
label | 443e0c3e-59df-5c2d-bcf6-0e772d536854 |  | note | UCCL - V
label | 1f69e207-fa85-5f4e-8e6f-be93e62ea5a5 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Conduct 7 day strength test
label | 8fe6f766-0692-5a23-a8ea-b0e94b7b5bca |  | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.11
label | a98406e3-7bcc-59cd-a45d-baec1b973dc1 |  | note | TEST REQUIRED - 7 day strength test
label | 7c48a5af-d2f5-5498-b7f5-ae3772e2d5c4 |  | note | INSPECTION BY - UCCL
label | c2462735-2ebc-5691-ae75-97f9f7f74cb3 |  | note | TASK TIMING OR TASK FREQUENCY - 7 day after casting
label | 4896c328-d859-56ac-beda-7da38e6bb1c8 |  | note | ACCEPTANCE CRITERIA - 60 % of the specified strength
label | af51b19a-a39d-5c0a-9c50-a06f6a6abb76 |  | note | UCCL - V
label | 27a86699-6395-507f-bc02-2135478b07f7 |  | note | Client - SU
checkpoint-group |  |  | section | Pre Construction - Site works
checkpoint-status |  |  | checkpoint | Strip Footing
label | 97fd9e45-7600-5239-98d8-5e0b6ea92c04 |  | note | TEST REQUIRED - Photos
label | ee5e2a21-cbc9-54b9-bf45-b0a043b487b2 |  | note | INSPECTION BY - UCCL
label | 624d746a-0910-5325-9fc7-1f8ed8c4239a |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
label | fd4ac82a-f2b7-530e-b3b5-b74e445a5e24 |  | note | ACCEPTANCE CRITERIA - Strip footing to be 400mm wide and 200mm deep
label | 6ff6d2d6-995e-597f-a405-270160a74f7e |  | note | UCCL - V
label | edca2f0f-5dd5-509f-ab79-b566aa189426 |  | note | Client - Su
checkpoint-status |  |  | checkpoint | Subgrade Strength
label | 832ef7cb-d385-536c-a083-7de4b2426be7 |  | note | TEST REQUIRED - Scala Penetrometer Records
label | c3547d4a-b953-54ec-bd05-67653c21325d |  | note | INSPECTION BY - UCCL
label | 84bcf3ae-d67f-5c4c-b558-76e01f290e59 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
label | 4fb1def6-7272-586a-9a8e-4b8c06fbf852 |  | note | ACCEPTANCE CRITERIA - Subgrade to meet 3 blows/ 100mm with scala testing
label | 897f8fd4-14d8-5a85-bfec-4dd7082debb5 |  | note | UCCL - V
label | 27610774-8d12-54dc-9b76-e2c5ee633443 |  | note | Client - W
checkpoint-status |  |  | checkpoint | Formwork
label | 33d9f5e3-95a1-5db3-a693-dec849aeb1f3 |  | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.14
label | 2de8e55a-cc7e-5d3e-927c-abfca5f48583 |  | note | TEST REQUIRED - Quality shape and size of formwork
label | 5d661063-20e9-5f63-9017-f9108587ffab |  | note | INSPECTION BY - UCCL
label | 4bef5f18-7c3e-5f4d-9f5a-416954a6f7b5 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | f9fd92d0-d97c-5f61-b5be-8a69c989f294 |  | note | ACCEPTANCE CRITERIA - All formwork to meet the specification required for the unit being constructed
label | 206a427d-85f9-5261-b621-72b5a8fe4abd |  | note | UCCL - V
label | e106806e-b7f2-5384-b2e6-75bec8e00baa |  | note | Client - W
checkpoint-status |  |  | checkpoint | Site Concrete
label | 4ccaa8d5-1b08-5404-9fed-fd9c7499fe90 |  | note | TEST REQUIRED - Visual inspection
label | c09a95a8-e2aa-55e9-9123-44aefdc3b3c1 |  | note | INSPECTION BY - UCCL
label | 94e43f08-d88c-5c9b-ac72-666deb9d9d93 |  | note | TASK TIMING OR TASK FREQUENCY - Each Foundation
label | 66852368-6cf6-5f78-ba39-90b0b5d15e10 |  | note | ACCEPTANCE CRITERIA - Site concrete to be placed at the thicknesses shown on the drawings and finished to a height of +/- 10mm
label | e58d6350-7e61-53cc-a1e1-26824ede22dd |  | note | UCCL - V
label | 9ec2bcef-e924-5179-af65-778129058ea4 |  | note | Client - Su
checkpoint-status |  |  | checkpoint | Setout
label | 5e3d1f35-246f-5fc3-ac99-738eb9881095 |  | note | TEST REQUIRED - Survey
label | 9fedaf09-cf79-5507-a19d-93f597687ed1 |  | note | INSPECTION BY - UCCL
label | 32b144b7-7e58-5dbe-ab69-7fce691032cd |  | note | TASK TIMING OR TASK FREQUENCY - Each string
label | 59db3571-2a56-5a11-b072-6c0d16bf7a86 |  | note | ACCEPTANCE CRITERIA - Foundations and embedded items shall be set out following the tolerances, heights and positions shown in each foundations respective drawing.
label | 8a63898a-42c2-5474-8721-1562ee265996 |  | note | UCCL - V
label | 59681a56-b250-52e4-8772-954460f58c86 |  | note | Client - Su
checkpoint-group |  |  | section | Prepour Inspection
checkpoint-status |  |  | checkpoint | Pre pour inspection
label | 28ff528a-118b-52b0-9c82-dbff6abeb4da |  | note | TEST REQUIRED - Visual Inspection
label | 388a1272-492f-5fb0-8522-babd6d6bbde7 |  | note | INSPECTION BY - UCCL, MEL, WSP
label | de4d308d-a320-50cd-921d-9fe141f9f5e3 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing structural concrete
label | 8ebe09fb-dce3-5cd5-87c7-c21286472733 |  | note | ACCEPTANCE CRITERIA - Pre pour inspection sheet to be completed prior to placing concrete. WCL to be notified of pours for inspection at least 24 hours prior to placing concrete.
label | b156ec4c-540d-5d9a-9792-5ded84a1c158 |  | note | UCCL - H
label | 6f19ea62-2ee8-5326-adff-18ddb2752a51 |  | note | Client - W
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Postpour Inspection
checkpoint-status |  |  | checkpoint | Post pour inspection
label | 0f87c4f1-6f31-5187-b128-3651ec9b10bc |  | note | TEST REQUIRED - Visual Inspection
label | 724a37e9-0b05-5b6a-ab3f-52a2985055c0 |  | note | INSPECTION BY - UCCL
label | fb67f8f9-33f9-5c7c-82f0-e3f3c01fc721 |  | note | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
label | 05a7a0de-8265-5c98-913b-55bb0bfbd896 |  | note | ACCEPTANCE CRITERIA - Post pour inspection sheet to be completed following each pour.
label | 272c629c-97d2-544c-83ac-1fddf7c3e8ed |  | note | UCCL - A
label | f0ece2bc-9bef-57eb-85fe-1e8d39476118 |  | note | Client - Su
checkpoint-group |  |  | section | Post Construction
checkpoint-status |  |  | checkpoint | As Built & Final Design Documentation
label | 4ab69cb8-fa7b-53ed-8cd3-aa736b9a79d8 |  | note | TEST REQUIRED - Surveying
label | b389ca5f-475a-5bd4-9ac9-ac2c941eedd1 |  | note | INSPECTION BY - UCCL
label | d79d0632-032e-5cd2-b6af-a04a969cf066 |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 894f8aab-fe5c-59b3-8156-3544dfd17eb3 |  | note | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline mark ups
label | 2d8a961c-1c34-5b5e-8541-9b10c1397198 |  | note | UCCL - S
label | 0b50ff9b-4728-50a0-be0e-edbdb22bf649 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Records of:
label | 3403217d-75a8-59fb-814b-67e91f5056e0 |  | note | SPECIFICATION REFERENCE - Products and materials selected for alternatives specified, Approved substitutions and accepted alternatives, Other approved changes and deviations to items specified.
label | 245d164e-ad45-5a68-bdd3-901dda2aeeeb |  | note | INSPECTION BY - UCC
label | e3734712-a2ab-5ba1-88b3-c2f5077f25b2 |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | ac78d5f2-2a70-5ddf-bba3-9ab7f8df5622 |  | note | ACCEPTANCE CRITERIA - Confirmation From Engineer of all records
label | c50373ec-dc7f-51d8-9428-812cd6c26d7e |  | note | UCCL - S
label | 3ef35ab5-da76-563c-a0a2-9925eb196534 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Producer statement
label | 96ec4d67-a708-55b9-b649-4c89a4b06ca6 |  | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.14
label | 9842e11c-b4ff-5a51-a9dd-c4a425983eea |  | note | TEST REQUIRED - Submit a producer statement for precast units
label | 723d0dcc-a778-5d98-9706-0656b2481cff |  | note | INSPECTION BY - UCCL
label | 0f5ca29d-62c5-5978-8c93-f4c91cdc9c7f |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 1ee6a460-bf9f-54a4-a3fd-8cac62b5145f |  | note | ACCEPTANCE CRITERIA - Producer statement to verify the products meet the requirements specified.
label | c205097f-5f10-5794-9bbe-79d786037b76 |  | note | UCCL - S
label | 77398384-eb10-5406-a15c-c765197f5298 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Completion Inspection inc. Construction Defects Report
label | f7ee1f7f-2893-5b43-b468-650af138b8ba |  | note | TEST REQUIRED - Completion inspection on each foundation by CEL
label | c67cbaa4-c23b-57e8-920e-335e6b37812e |  | note | INSPECTION BY - UCCL
label | fda6f7db-8920-5b25-b095-593b9c941b7f |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | d5732374-7b88-509d-a5ba-b0bb927b8e91 |  | note | ACCEPTANCE CRITERIA - Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out
label | f8626187-16fa-57df-9f13-dd764053e012 |  | note | UCCL - S
label | 28927bce-1a14-58e2-9cc9-5dd4a3318a30 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Identification of panels
label | b0b21fd9-849e-52d9-86ea-1616d263df96 |  | note | TEST REQUIRED - Panel identification location
label | d048a50e-758c-51af-bdf5-abdb933f6b4a |  | note | INSPECTION BY - UCCL
label | 9eb1c352-0b21-5155-861c-baa51c1999d1 |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 0f8830a4-8d47-53e0-a009-0dccd2b7137b |  | note | ACCEPTANCE CRITERIA - Panels to be marked and identified as to which pour they're from and final location.
label | d7b97580-fb04-5f19-965b-0dfa0f7344bf |  | note | UCCL - V
label | 832cb9ea-a5d9-52de-8e1c-d52b5f412223 |  | note | Client - R