## res_ITP_1_Inspection_and_Test_P
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP 02 - Duct Installation | itp |  |  |  |  | ITP 02 - Duct Installation
section | Preconstruction
checkpoint | Review of proposed work
label | TEST/TASK REQUIRED - Drawings to be reviewed and permission to proceed given.
label | INSPECTION BY - UCCL, MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to Ordering Materials
label | ACCEPTANCE CRITERIA - Drawings to be IFC
label | UCCL - R
label | Client - A
checkpoint | Survey Setout
label | TEST/TASK REQUIRED - Initial Setout by Surveyor
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to Installation
label | ACCEPTANCE CRITERIA - Surveyor to set out prior to construction
label | UCCL - V
label | Client - A
checkpoint | Service Ducts
label | SPECIFICATION REFERENCE - 14.4 Specification for laying Cable Ducts
label | TEST/TASK REQUIRED - PVC Heavy Duty Electrical Ducts 50mm, 100mm and 150mm diameter. Colours as specified on drawings
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to Installation
label | ACCEPTANCE CRITERIA - Supplier Documentation
label | UCCL - S
label | Client - A
section | Installation
checkpoint | Installation of 100mm Ducts Between PCS Slab and Containers
label | SPECIFICATION REFERENCE -
label | TEST/TASK REQUIRED - Visual Inspection
label | INSPECTION BY - Meridian
label | TASK TIMING OR TASK FREQUENCY - On completion of the installation of each set of 100mm ducts.
label | ACCEPTANCE CRITERIA - Orange 100mm ducts from PCS slab to container installed to correct line and depth.
label | UCCL - V
label | Client - A
checkpoint | Installation of 50mm Ducts Between PCS Slab and Containers
label | SPECIFICATION REFERENCE -
label | TEST/TASK REQUIRED - Visual Inspection
label | INSPECTION BY - Meridian
label | TASK TIMING OR TASK FREQUENCY - On completion of the installation of each set of 50mm coloured ducts.
label | ACCEPTANCE CRITERIA - Coloured 50mm ducts from PCS slab to containers installed to correct line and depth.
label | UCCL - H
label | Client - V
holdpoint | HOLD POINT
checkpoint | Thermal Backfill (as directed by principal)
label | SPECIFICATION REFERENCE - Civil Works Specification 6.4 Amended to pleatu test for accepted MDD Refer MAIL NUMBER WSP-CONSC-000319 REFERENCE NUMBER MELNZ-RFI-000265
label | TEST/TASK REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following instalaltion of ducts, where specified
label | ACCEPTANCE CRITERIA - 10 passes with plate compactor, per MELNZ-RFI-000310
label | UCCL - V
label | Client - A
checkpoint | Sand Backfill
label | SPECIFICATION REFERENCE - Civil Works Specification 6.4 Amended to pleatu test for accepted MDD Refer MAIL NUMBER WSP-CONSC-000319 REFERENCE NUMBER MELNZ-RFI-000265
label | TEST/TASK REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following installation of ducts, where specified.
label | ACCEPTANCE CRITERIA - Self compaction of sand, as per MELNZ-RFI-000310
label | UCCL - V
label | Client - A
checkpoint | Flowable Fill
label | SPECIFICATION REFERENCE - Refer MAIL NUMBER MELNZ-RFI-000393 (Ducting at 101A, 201A, 301A, 401A and 501A requires flowable fill as per drawings supplied)
label | TEST/TASK REQUIRED - Visual Inspection
label | INSPECTION BY - Meridian
label | TASK TIMING OR TASK FREQUENCY - Prior to pouring flowable fill over 100mm orande ducts at 101A, 201A, 301A, 401A and 501A.
label | ACCEPTANCE CRITERIA - Orange 100mm ducts from PCS slab to container installed to correct line and depth. Ducts braced and height pegs set for correct cover.
label | UCCL - H
label | Client - V
holdpoint | HOLD POINT
checkpoint | AP40 Hardfill Layer
label | SPECIFICATION REFERENCE - Construction Drawing Set RUK-UMC-DS-01. Also refer MAIL NUMBER MELNZ-CA-000290.
label | TEST/TASK REQUIRED - Visual inspection. Cleeg test with minimum CIV value of 25.
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of AP40 hardfill layer, prior to site concrete.
label | ACCEPTANCE CRITERIA - Minimum CIV of 25.
label | UCCL - V
label | Client - A
checkpoint | Cable Pits
label | SPECIFICATION REFERENCE - 14.4 3 Specification for laying Cable Ducts
label | TEST/TASK REQUIRED - Supplier Documentation
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY -
label | ACCEPTANCE CRITERIA - Cable pull pits to the dimensions shown on drawings
label | UCCL - V
label | Client - A
section | Post Construction
checkpoint | As Built & Final Design Documentation
label | SPECIFICATION REFERENCE - 14.4 2.3 Specification for laying Cable Ducts
label | TEST/TASK REQUIRED - Surveying
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - As constructed
label | ACCEPTANCE CRITERIA - The contractor shall undertake site survey of all duct ends so that they are installed within +/- 15mm of their design location
label | UCCL - S
label | Client - A
checkpoint | Ducting QA
label | SPECIFICATION REFERENCE - 14.4 Specification for laying Cable Ducts
label | TEST/TASK REQUIRED - Duct Inspection Record
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Per trench
label | ACCEPTANCE CRITERIA - Duct Inspection Checklist completed per trench
label | UCCL - S
label | Client - A
checkpoint | Completion of Ducts for Handover
label | SPECIFICATION REFERENCE -
label | TEST/TASK REQUIRED - Handover Record - Handover of Ducts to Electrical
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On the completion of duct installation at handover for electrical installation.
label | ACCEPTANCE CRITERIA - Handover record sign by UCCL, Meridian, and Electrical Department. Ducts installation completed, and ducts cleaned ready for electrical installation.
label | UCCL - H
label | Client - V
holdpoint | HOLD POINT