## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
313231b6-3c49-4d40-ad87-e4c5cb0d6ced | checklist | *1 - Pre-Commencement Activities |  | *1 - Pre-Commencement Activities
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
b39c1a7b-3758-4d39-a0b8-60767b3a2b7d | checkpoint | Project Self-Assessment Tool- BU Project Audits -
6fc5e744-5ea4-4ab0-9b4a-1d2f4b5f8224 | checkpoint | 1.1 - Submission of Waterproofing System products
4d5b11e3-22f8-5ceb-b9af-4cf24c85ca5c | note | Specification Reference - GBA-SPE-AR-AS-0001
1a9ebd2f-9b4c-5fdc-8670-e2d1b699804f | note | Acceptance Criteria - Approval of Waterproofing System - confirmation of compatibility with substrate and follow-on trade requirements
8191262e-d7ce-5c5b-9a9c-e919987fc437 | note | Test/ Inspection - Review & Verify
5f987db2-9e71-52e6-8652-0e95b1b5a050 | note | Test/Inspection Frequency - One-off prior to commencement
498e1527-cdbb-5c59-bb80-1969f40ccfaf | note | Inspection: Subcontractor - WS (I)
dcdfe134-02e4-55b3-ae6f-7c167c828379 | note | Inspection: John Holland - PE (R)
3234914e-bd97-5f8d-8653-769ec5acff1b | note | Inspection: Nominated Authority - WC (R)
28551705-fcd8-4d21-8bca-dea4580ade3b | checkpoint | 1.2 - Submission of Waterproofing System Warranties
f238b294-8371-5ae1-a207-19871934aef6 | note | Specification Reference - GBA-SPE-AR-AS-0001
6285a28b-fb1c-5b1d-a7b3-cf5741ecd39b | note | Acceptance Criteria - Warranty is for required duration and relevant party
40c6458a-3152-5582-b791-0aa21649494b | note | Test/ Inspection - Review & Verify
f4448a0e-6334-50c4-af36-160d993363d3 | note | Test/Inspection Frequency - One-off prior to commencement
a1f9789a-629f-543f-97c9-a8e2ce42f8c6 | note | Inspection: Subcontractor - WS (I)
98dd2b62-33ca-5fe3-87c4-86085f36740e | note | Inspection: John Holland - PE (R)
f25ca8e5-dc92-5826-b87a-bc4eb1581e67 | note | Inspection: Nominated Authority - WC (R)
d577808f-a9bf-4571-bec7-0dcb6b3e5c23 | checkpoint | 1.3 - Submission of Manufacturer's Application Method Statement (MAMS)
b4279821-9929-5c31-8acf-dbd9179bbb14 | note | Specification Reference - GBA-SPE-AR-AS-0001
a7701cb0-498f-5fbf-9fd5-6865adb673e2 | note | Acceptance Criteria - Approval of MAMS by Waterproofing Consultant
73774f42-7173-5157-9d80-59bfa59e3d25 | note | Test/ Inspection - Review & Verify
95493b5b-e6e3-514f-b9c6-532702dcdc84 | note | Test/Inspection Frequency - One-off prior to commencement
a2785c3e-4e76-53f6-8788-e1aeceeb365f | note | Inspection: Subcontractor - WS (I)
5337e7ea-4efa-5255-a0d5-5fdc3b194747 | note | Inspection: John Holland - PE (R)
01d7bff9-09e0-5995-b9c7-6e8dcc973c7a | note | Inspection: Nominated Authority - WC (R)
f5fe2e76-557d-4585-85f0-a1b5ca005d25 | checkpoint | 1.4 - Submission of AMS and WRA Content - including Safety Data Sheets for chemicals
d66ffb3f-3a90-596d-be84-677fc880b090 | note | Specification Reference - GBA-SPE-AR-AS-0001
3c027519-bec1-5ac2-8623-d22461178aeb | note | Acceptance Criteria - Approval of AMSs and WRAs
3c0ab299-70ca-5493-8257-ae3a3f3b00a8 | note | Test/ Inspection - Review & Verify
5a9f9228-0525-50c1-965c-47f7ac9d3397 | note | Test/Inspection Frequency - One-off prior to commencement
41f21fe3-0334-5373-870a-5de2c9425f5d | note | Inspection: Subcontractor - WS (I)
d8c190dc-03c3-5b49-8efe-8d5974f06199 | note | Inspection: John Holland - PE (R)
500dbdf6-8cdb-54a0-ac17-d953b01f6e91 | note | Inspection: Nominated Authority - WC (R)
4570fb49-c0b7-4e7f-a9a4-4c1f7a64bcb5 | checkpoint | 1.5 - Waterproofing company to demonstrate Competency of Applicators
85c22bc8-2fc4-56c5-93fc-24203d7e8f7b | note | Specification Reference - GBA-SPE-AR-AS-0001
ed8166d0-8abf-5e85-9133-fd92997d76ea | note | Acceptance Criteria - Competency scheme document, register of applicators
84d51585-8326-556a-b793-d6f6fa4359cc | note | Test/ Inspection - Review & Verify
9b301039-39c3-52dc-870e-eacf98433b78 | note | Test/Inspection Frequency - One-off prior to commencement
c8267a49-d826-5066-a5e2-de9d48cab538 | note | Inspection: Subcontractor - WS (I)
bc1c5109-2386-5b23-974c-a49c4d62f7ba | note | Inspection: John Holland - PE (R)
df2dee3a-31ed-548d-883b-4cddc95bb025 | note | Inspection: Nominated Authority - WC (R)
42388873-44cc-447e-85a5-007ce2cb62ff | checkpoint | 1.6 - Detailed design complete - including shop details
b6302a2b-71e0-5b82-96b2-0811aaf641a7 | note | Specification Reference - GBA-SPE-AR-AS-0001
8493eff7-7070-54ee-87c8-1cb88043c0f5 | note | Acceptance Criteria - Approval of shop drawings
9e2f9ca5-7eb3-5cbf-ae48-bb792cbed0cc | note | Test/ Inspection - Review & Verify
216c01d6-c913-5d14-87d7-2a7d54343b49 | note | Test/Inspection Frequency - One-off prior to commencement
e8735c34-0d1d-513e-b1de-e4c7682ce924 | note | Inspection: Subcontractor - WS (I)
6d8b55d9-8ae5-5056-b2bc-98a9755dcb5a | note | Inspection: John Holland - PE (R)
ebc55445-2b70-54f3-99c6-aa9af925caf8 | note | Inspection: Nominated Authority - WC (R)
31cc7d2c-b748-46d2-90b7-9d9e60368727 | checkpoint | 1.7 - Testing equipment details - and calibration records (if electronic leak detection specified)
ef03fc0e-128a-5005-b818-f7b976cd39e7 | note | Specification Reference - AS3740 App C3 / GBA-SPE-AR-AS-0001
0adce048-e946-50ea-b5a8-909c02cca418 | note | Acceptance Criteria - In calibration
fada0d60-90c4-50d6-b85b-385796efa78e | note | Test/ Inspection - Review & Verify
2745af1f-9e78-541f-a164-fb341cd24a19 | note | Test/Inspection Frequency - One-off prior to commencement
5cdd1f43-d617-5c06-b762-5877f5ce14d0 | note | Inspection: Subcontractor - WS (I)
432d5611-d3bc-5bb5-8a66-fdecc1b2803c | note | Inspection: John Holland - PE (R)
ad8bcadd-8aa6-5bfa-aa80-3970a3dfe0da | note | Inspection: Nominated Authority - WC (R)
72ba1789-4d77-463f-96db-730e5ce56fe6 | checkpoint | 1.8 - First of Type Inspection -joint witness and sign-off on Prototype or First Install with membrane system representative (as below)
bdfb3d4b-9f50-5cad-9dc7-b77a543f7f80 | note | Specification Reference - GBA-SPE-AR-AS-0001
f5847aa1-a29e-577d-be3d-2a049e51cb3e | note | Acceptance Criteria - Joint acceptance of the First of Type and close-out of any agreed issues
381b18e4-2d5e-5882-951d-81435414c8f9 | note | Test/ Inspection - Review & Verify
d48574b6-94b1-50e2-823a-e5acd31c9800 | note | Test/Inspection Frequency - One-off prior to commencement
85fb92a5-bd3d-5a1b-b845-64c920241966 | note | Inspection: Subcontractor - WS (H)
db2d3b85-071e-5260-92b2-a1c8d814ed32 | note | Inspection: John Holland - PE (H)
d819ce59-3ee8-5a14-b32f-98e5ffd7c447 | note | Inspection: Nominated Authority - WC (H)
1b8ab6fd-df45-4fce-b589-a36dc35d524a | signoff | AUTHORITY HOLDPOINT
59740568-c7a3-450f-8aea-be2af74d63d5 | checklist | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 - 01 - Waterproof Ensuite Base |  | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 - 01 - Waterproof Ensuite Base
933d8624-d86f-438b-a664-4b7d8a51e313 | section | 2 - Construction Inspections
86840d61-1425-40c6-8981-478123887092 | checkpoint | Inspection Details
cab155b4-74d4-5342-ae84-c217811c4561 | textbox | Level:
d278206d-34b9-5c5b-af74-7bcce90290cb | textbox | Zone:
b37b6a11-d6db-4494-bffd-7d7d5039d854 | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
7dae2d54-b4c3-5662-b25f-58440329b49b | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
9a44f26b-9c94-591a-a0df-0ae149ba1df5 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter
a02612c5-d492-5064-8ec9-131dbdb74f0f | textbox | Test/ Inspection - Measurement
5a0ebc78-8e58-5712-a893-4d8b125b2d4d | note | Test/Inspection Frequency - Each wet area, every 20m2
bbd5f677-061e-505a-9bac-7dcc1dae9a0c | note | Inspection: Subcontractor - WS (I)
98053fc2-c300-5985-bc3c-02b3564a5c9f | note | Inspection: John Holland - PE (S)
9f7fe22a-d79a-4077-b495-080430b4cc39 | checkpoint | 2.2 - Drainage installation - puddle flange installation
69ce85fd-c696-5026-aade-b1033defe3b4 | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
93278d6a-b2d4-52b3-a12b-67f0d71ab7b9 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
55817f8e-9d79-5428-b997-11ff375e6842 | note | Test/ Inspection - Installation and Inspection
ce639751-bbf8-5257-9377-888466c52b2c | note | Test/Inspection Frequency - Each wet area
2c71b00b-4ada-5ec6-979c-885132fae44b | note | Inspection: Subcontractor - HS (I)
da96cfab-912c-5f1b-86d2-738b2ca57b99 | note | Inspection: John Holland - PE (S)
84c29cbe-b312-42d4-a52d-7685891b4eb8 | checkpoint | 2.3 - Substrate condition Inspection
ec3ed5f6-f743-5233-8375-3ada45fc3f2d | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
ae5ab77f-512d-5734-a601-6f14b3ab51aa | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
0bf076fd-0d42-5659-a561-e4362fb7d767 | note | Test/ Inspection - Inspection
92cc4c40-15e7-55d2-a78b-d18290925495 | note | Test/Inspection Frequency - Each wet area
d024a955-68a0-552f-b99e-33bbd31b3dde | note | Inspection: Subcontractor - WS (I)
c86b420d-986b-5c90-a645-20cf2ba319c0 | note | Inspection: John Holland - PE (S)
61d41109-867d-4b1a-bd58-cb82845611ca | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
40520f26-64f6-5c0f-b638-6cd1a4dff83f | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
d4b1eef4-f45d-5b24-9ede-c2c07349738e | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
069d8f0a-5124-51e1-8fc0-66115823cb52 | note | Test/ Inspection - Measurement
519ef3a0-bb52-5229-a7ad-c8ad588713bf | note | Test/Inspection Frequency - Each wet area
ca1c2cc5-27d8-5966-b8d4-2c40dbc7b5d4 | note | Inspection: Subcontractor - WS (I)
3598ad4b-457a-5843-ab58-69c152123627 | note | Inspection: John Holland - PE (S)
315be017-08d2-4b83-a1cd-c4ce1ca24d05 | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
cc3d2b9a-dc72-552a-a9a3-31187f762a47 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
4e2c9c9d-5e67-5e32-a66f-1d857a53105e | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
8f156b79-6ffc-5f9f-b88a-1a0b823e971f | note | Test/ Inspection - Installation and Inspection
aa933a73-4d8a-5d2a-9010-05ae22a86a2c | note | Test/Inspection Frequency - Each wet area
64f944de-f209-5e06-9394-28170400a53a | note | Inspection: Subcontractor - WS (I)
5ef0827b-10f4-58ff-93c9-233ce397cdb8 | note | Inspection: John Holland - PE (S)
5cc33188-24ed-5c84-9e3e-94ca1516c445 | textbox | Records & Comments - Measured fall:
4a67ed99-4dfa-49eb-a21c-ebc073cb4938 | signoff | AUTHORITY HOLDPOINT
1cf907ad-1c5b-4fea-8240-04de37f5db22 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
2c2f6391-634d-5384-8f8b-382fe93d889c | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
c66f6a54-921f-56c3-8558-8400af563f9b | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
83d9f20d-a91d-5ed4-8ad8-2d993e6abd22 | note | Test/ Inspection - Measurement
9ab5178f-8456-50d7-836c-c2210d891c1a | note | Test/Inspection Frequency - Each wet area
e90e5de1-2b86-5c9c-8e7b-da0588df70d2 | note | Inspection: Subcontractor - WS (I)
031ac72d-1011-5efb-9649-ef2a0215609c | note | Inspection: John Holland - PE (S)
acf0c027-0885-4552-9b81-ae034c48c4d8 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
8164abc1-7d15-5f07-b869-24343c4fd591 | note | Specification Reference - GBA-SPE-AR-AS-0001
5f063bc9-3d58-5cc0-bd48-a344161e4fbc | note | Acceptance Criteria - Everything ready to install
e06bedfc-1f3f-5fda-bfd2-ee6daef9162c | note | Test/ Inspection - Review & Verify
92e58d5a-0c80-558d-9cb0-76962823167a | note | Test/Inspection Frequency - Each wet area
6c695e7f-14cc-5b4c-b262-570eb3030e1e | note | Inspection: Subcontractor - WS (I)
ebaed9a2-34cd-568d-b823-c6d00a2b8ade | note | Inspection: John Holland - PE (S)
addf77d8-c97c-548c-8f85-e5194480ded3 | textbox | Records & Comments - Temperature Reading:
29883a80-0d27-4461-96cb-1283130a2d61 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
86e29860-093d-52e0-b0a1-9b85a00de41d | note | Specification Reference - GBA-SPE-AR-AS-0001
144337bf-1bd8-52fb-b6ac-70e76f22dde2 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
1b3eaf21-cdfd-5f05-837c-ffb4f2e02486 | note | Test/ Inspection - Visual Inspection
5452aa3c-e6f5-5d8f-ba9e-7540ac37c165 | note | Test/Inspection Frequency - Each wet area
8051adf3-226d-546c-88fc-37d3855dbd86 | note | Inspection: Subcontractor - WS (W)
d228a58d-0761-565d-a3aa-3f5ec9aeeef1 | note | Inspection: John Holland - PE (I)
a61f299c-a0dd-585c-8c28-05de4b690e41 | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
63e78437-84e0-5638-90db-3c81b3fd8502 | textbox | Applicator Names:
bf5e7ce3-1425-56b9-b743-1693c59b1b72 | textbox | Temperature at placement:
4c6c8efb-59b8-49de-a203-5668c6ddfc68 | signoff | AUTHORITY HOLDPOINT
deb324ad-1b8e-439a-95f6-e6348a4c775c | checkpoint | 2.9 - Apply TREMCO Primer - take a photograph of the primer container with technical details and a photo/video of the application
89d85569-b2b6-554d-96fa-89b914617217 | note | Specification Reference - GBA-SPE-AR-AS-0001
db9b0b4b-e1e4-5ed6-9206-3c11f8a38233 | note | Acceptance Criteria - TREMCO Primer Applied
d67219d5-dd27-52d9-8d97-b5c14e003d93 | note | Test/ Inspection - Installation and Inspection
c5d53ba2-748c-5f75-91ad-ce71da825180 | note | Test/Inspection Frequency - Each wet area
c2fcd4eb-ba40-56b6-bff4-20bdb845bbec | note | Inspection: Subcontractor - WS (I)
616f6811-f317-5ae3-af59-e65536d65342 | note | Inspection: John Holland - PE (W)
9bf79cc2-93bd-442f-825b-f30b0b6170aa | checkpoint | 2.10 - Apply membrane layers in line with data sheet and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
3d92a60c-051a-500c-b867-ff84ecc08df4 | note | Specification Reference - GBA-SPE-AR-AS-0001
509630be-6971-5a3d-a59b-49ccb31db15b | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
3aa5329a-ba93-5d34-bdb0-045179e3b6cf | note | Test/ Inspection - Installation and Inspection
4aa6c2df-a697-5da1-bf84-80477b9db942 | note | Test/Inspection Frequency - Each wet area
e6b6615a-0e5b-5c42-8964-8b1c64311cd2 | note | Inspection: Subcontractor - WS (I)
3f6ade71-e247-5d34-898b-66dee0f1a723 | note | Inspection: John Holland - PE (W)
38dd4a97-35e6-476a-9fb8-4084502ee9c8 | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
317e1b92-8802-5e5a-956a-d9ce8d661085 | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
9b9f7dd3-f09a-56ad-90c5-331a0051e721 | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
184cfd7f-d7d6-58ce-bcb7-cf1575a47f40 | note | TREMCO Primer curing times
6bc9df63-e8bd-52ef-a81a-670d33e68365 | note | Full Cure time: 2-3hrs
4dff7a03-420d-5241-a3fa-1b23d2e0633b | note | Test/ Inspection - Installation and Inspection
75db2579-c861-5010-ab88-1eeb4f569e2e | note | Test/Inspection Frequency - Each wet area
08e554fd-308b-5243-80de-7972b93aa0ed | note | Inspection: Subcontractor - WS (H)
9a888972-1ce4-5333-8d2a-d8e0122ff390 | note | Inspection: John Holland - PE (H)
d9a515da-6af7-5334-8463-3f981137ffe0 | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
9c990c1f-10d9-538a-b699-cf977d97472a | textbox | Layer 1 time:
a087d945-1063-587b-91a8-c52ed373a756 | textbox | Layer 2 time:
4a93cbe7-a467-45dd-8d67-fafca36f39a7 | signoff | AUTHORITY HOLDPOINT
127d0941-9ea9-48c7-b069-b349045924f6 | checkpoint | 2.12 - Membrane test - Flood / Electronic Leak Detection / Seam Probe test the area in line with the AMS instruction
12278258-7b9e-5b7d-9f79-a0e8c0285e16 | note | Specification Reference - AS3740 cl 4.5.4 / GBA-SPE-AR-AS-0001
6f48394e-75d8-5105-a295-74b0ea9a666e | note | Acceptance Criteria - Flood test - no leakage observed / measured over 24 hours Electronic Leak Detection Test - no points of electrical conduction identified Seam probe test - no seam failures reported
f64e8c31-c670-59f9-ad79-9ec36200ce91 | note | Test/ Inspection - Test
ca0e3a3a-9f82-5fba-850a-61249c1e9cdc | note | Test/Inspection Frequency - Each wet area
c621ddc7-eeb0-5318-a3f1-f1e41a67f2c9 | note | Inspection: Subcontractor - WS (I)
d60e6895-d165-56a0-8236-b443b78fcb1f | note | Inspection: John Holland - PE (W)
d70b92f0-7305-527f-a4f6-c4d42052d5ae | note | Inspection: Site Manager - DC (W)
5af2c79b-2f16-50e8-85f4-1a9fe5b08cf2 | note | Records & Comments - Pass or Fail
da57220a-066e-58d1-b860-2a355a1c98c1 | textbox | Observed setting time:
6687c715-89b4-49f5-8e4c-6203c47e6cd5 | section | 3 - Close-Out
2a28bbc2-add1-4467-87a2-6887e8217d36 | checkpoint | 3.1 - ITP close-out.
fd341994-e22a-548a-8351-5e7f77dd4f2c | note | Specification Reference - GBA-SPE-AR-AS-0001
0ea06e54-47aa-5586-944e-38b41eb4e685 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
8abf0876-4966-5a61-856b-756f056a4944 | note | Test/Inspection Frequency - Each Lot
e29a7d93-3be7-51a2-a99e-8944387123eb | note | Inspection: John Holland - QR (R)
39e1033b-341c-5f4c-9596-88d345b5cc88 | note | Records & Comments - Check all measurements are recorded and photos attached.
7a6ef1be-8cc7-5622-8735-7c840d8b8c09 | note | All records loaded into the Work Lot System and Verified.
3d59889c-90d6-4351-80a9-a8f3117402fe | checklist | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 - 02 - Ensuite Walls |  | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 - 02 - Ensuite Walls
5a206b5a-cfb5-43ff-b04f-f5fcc0d8f607 | section | 2 - Construction Inspections
2c72760a-de85-480f-9eff-db95225ccb14 | checkpoint | Inspection Details
d5a893e2-756e-5b05-b6d8-850c0d851736 | textbox | Level:
78f1b474-80c9-5ea0-b9ca-6d1158ede27f | textbox | Zone:
c7b37808-15db-4077-8c68-98c3688c9727 | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
dcfc4ab2-0141-58be-8341-2ad8cd2172e4 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
f48acc87-b81e-5cd0-a1da-27a2faad3947 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter
65aa2b04-fa30-5261-b2bd-6353a26ba649 | textbox | Test/ Inspection - Measurement
9a0a50bb-122a-5294-a9ab-106a32a6d209 | note | Test/Inspection Frequency - Each wet area, every 20m2
cb3f16cf-3fef-5492-851e-dbe768ed6f5b | note | Inspection: Subcontractor - WS (I)
3b9c8fd6-7251-5ee4-9eff-2d0165e023d1 | note | Inspection: John Holland - PE (S)
fa1ca17a-122e-4695-ba67-dae093ad981d | checkpoint | 2.2 - Drainage installation - puddle flange installation
17945d7d-611d-5dab-822a-99503a46c85d | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
fdc359ff-483f-5373-af97-d2c2a65be180 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
c2c5e8f0-3416-5e9b-a9da-cff14cfbb407 | note | Test/ Inspection - Installation and Inspection
c2045ceb-7430-5042-9898-a723010d80a9 | note | Test/Inspection Frequency - Each wet area
94d7aecf-329a-580e-b295-e8ac69b3ad6a | note | Inspection: Subcontractor - HS (I)
fcf9e7be-cf33-5049-a459-922906beac95 | note | Inspection: John Holland - PE (S)
ab76f0a4-ad98-450e-bbe4-ca7f0e4a9a9a | checkpoint | 2.3 - Substrate condition Inspection
029c5636-a991-5e03-a5dc-e760fbb6d9ac | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
63ed0fb1-4ded-5e05-9d74-9212621491b8 | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
675e6fbb-997d-59db-8ba8-15c9ebb9e3e5 | note | Test/ Inspection - Inspection
349bcb63-2565-5a4f-8dc4-598b8ea15b69 | note | Test/Inspection Frequency - Each wet area
8837866b-b07a-558a-b5f8-018c37ee48b9 | note | Inspection: Subcontractor - WS (I)
dc81ab9c-bdfd-5097-8115-59cfd875a75c | note | Inspection: John Holland - PE (S)
07ad4d8e-5a3c-40b3-829c-573b06f6502d | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
e7057d94-6c08-506f-9c05-23dbf67492cb | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
de994652-e931-57de-a174-a15083a73033 | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
cc87db96-e190-57fb-a3f7-3782a2a20a14 | note | Test/ Inspection - Measurement
b3f8b1e0-9cb7-54f3-af75-b428ad1c10b0 | note | Test/Inspection Frequency - Each wet area
8ce37cca-9922-5679-9c74-6dff1dc6a9e8 | note | Inspection: Subcontractor - WS (I)
435de046-592f-56c4-8e7d-f636bad777b6 | note | Inspection: John Holland - PE (S)
7ba4acc4-4cd9-40d5-be79-4f43acacca07 | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
c442c5aa-39a1-5496-8631-e96f325d4435 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
ff72ef8a-7443-51c6-909f-f128eedb8dd9 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
fefd9e90-43b0-5614-aaa9-1b71c1f9487c | note | Test/ Inspection - Installation and Inspection
4eb36428-9164-5464-aa81-f1d4ba53b9ba | note | Test/Inspection Frequency - Each wet area
d908a647-9385-567d-bff6-cbcc7c80f9bb | note | Inspection: Subcontractor - WS (I)
898bdb03-4a54-579c-898f-c1803a09b6d5 | note | Inspection: John Holland - PE (S)
cf0b03a4-7bba-515f-897f-33dabcb3e76f | textbox | Records & Comments - Measured fall:
d416cf3c-b8bc-4356-a890-c2b9961b3d83 | signoff | AUTHORITY HOLDPOINT
6c679cf1-1f51-4b93-9bc1-c501bae78e20 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
8df887b7-209f-5c85-b1f8-8556a7af2d80 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
47ec431f-e73f-5d61-9bbd-81edd7d72981 | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
0271d2af-5f07-5284-8eec-57f4a323bfed | note | Test/ Inspection - Measurement
5b9ff0be-e66c-5293-a72a-bf163972c864 | note | Test/Inspection Frequency - Each wet area
649db6bf-f0d8-5cac-9695-3ff6e85c5001 | note | Inspection: Subcontractor - WS (I)
51bc4acf-1161-567e-8fd8-9a5f5679d323 | note | Inspection: John Holland - PE (S)
56da30d2-a9eb-417d-a5de-2bc3dee36a87 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
eaef3382-f38e-5d5c-8357-ed9be43d28eb | note | Specification Reference - GBA-SPE-AR-AS-0001
a57ead02-b089-5f44-bfef-808e4fac9aa2 | note | Acceptance Criteria - Everything ready to install
81f17761-b13e-556e-99c2-7c99b52867fa | note | Test/ Inspection - Review & Verify
c651d150-deaf-5594-ac51-6a5d136e6d62 | note | Test/Inspection Frequency - Each wet area
e8908db2-d5de-58ce-9b1a-d12439e68c79 | note | Inspection: Subcontractor - WS (I)
a4afe489-f9d4-5f1a-8b90-a9ca3d3e4034 | note | Inspection: John Holland - PE (S)
a3773df3-c6c8-5fa2-97c9-0acb6a025943 | textbox | Records & Comments - Temperature Reading:
5937bada-b84d-4510-9ba1-6af544b2d367 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
e60f22a7-6798-5a6b-b074-2804bb0583c9 | note | Specification Reference - GBA-SPE-AR-AS-0001
8690761e-cb94-527c-ad09-b1641b9f30a8 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
56b2281b-9f09-5c59-b0e5-991be688f112 | note | Test/ Inspection - Visual Inspection
1a998eb5-5a60-5de6-a487-8b07e10cdd78 | note | Test/Inspection Frequency - Each wet area
8b1dbb9f-fc38-54bb-b4ea-4f287fac7c55 | note | Inspection: Subcontractor - WS (W)
1f075d97-5e14-5ce4-ad1c-30a8779cecbc | note | Inspection: John Holland - PE (I)
c470ae38-97ca-5a46-b8f9-879b7c96ce5c | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
f9092c52-c06a-5d64-9017-72ec9815bd42 | textbox | Applicator Names:
62d54ade-1af5-5745-915e-6dbedcc6cd97 | textbox | Temperature at placement:
ba5c76a6-e3ad-4aa0-b89b-9f120f1fc9a6 | signoff | AUTHORITY HOLDPOINT
62857767-933e-4121-ba5b-8700a23e7dad | checkpoint | 2.9 - Apply Flowcoat Resin Primer - take a photograph of the primer container with technical details and a photo/video of the application
f6d84c84-b7a0-51ad-be7f-9b67dd3fe1f4 | note | Specification Reference - GBA-SPE-AR-AS-0001
ec312762-d27b-5f17-aa29-335e1f95d7eb | note | Acceptance Criteria - Flowcoat Resin Primer Applied
56da23af-a43b-5e1c-ae53-142c90284fde | note | Test/ Inspection - Installation and Inspection
d256e993-fa89-556d-9644-2e363121e821 | note | Test/Inspection Frequency - Each wet area
202da845-cdbe-5e00-a2c0-5e3b08837093 | note | Inspection: Subcontractor - WS (I)
a64246d8-0139-5819-b89f-1f24ac66c2b4 | note | Inspection: John Holland - PE (W)
a15199f8-b957-497d-9afd-a53e3e8a1311 | checkpoint | 2.10 - Apply membrane layers in line with data sheet and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
0aa0d4cc-3ec1-5322-a094-dfe6a17718a5 | note | Specification Reference - GBA-SPE-AR-AS-0001
c5d64284-8f7e-5a32-b7fc-75dc1ba7c7ce | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
cfca4522-a270-564f-953e-ce43998736ea | note | Test/ Inspection - Installation and Inspection
68582e8a-3c2d-5d38-a297-14218e86c97b | note | Test/Inspection Frequency - Each wet area
53e539d1-cbfb-5cf7-8955-81c448fc826e | note | Inspection: Subcontractor - WS (I)
cc0c860a-7ec8-5fe9-8f3b-34d2b1d98daa | note | Inspection: John Holland - PE (W)
69cba897-88a6-49c5-af4a-9b733ac9d93a | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
edd2ff68-0464-5d34-ae4a-bb666ab488be | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
cb0ac0e6-1ba1-59e4-8afb-6b855b3e8c38 | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
f8ff120f-cc26-5cf8-9f05-6ef457f54168 | note | Flowcoat Resin Primer curing times
e5f72658-0639-598e-8091-da63c99d92f5 | note | Full Cure time: 24 hrs at 20°
73353fb2-263d-5576-bdd5-f54daac1f0e7 | note | Test/ Inspection - Installation and Inspection
0f2d1cbe-90ce-5a30-95ca-3ef767ff316c | note | Test/Inspection Frequency - Each wet area
038ee9f3-6da3-5e34-92fe-032d06a5cad9 | note | Inspection: Subcontractor - WS (H)
4d8e137c-44ab-5c4d-8f97-607ecf24d0bb | note | Inspection: John Holland - PE (H)
75696e82-8036-5740-8dd7-3bfd68804e4e | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
d93176e8-9b11-5483-b98e-8a04ad6e897e | textbox | Layer 1 time:
c7d582e7-c7ef-5d26-82a4-f632398fa3a9 | textbox | Layer 2 time:
3db3a08c-1336-4900-a409-851e4e8ac3b6 | signoff | AUTHORITY HOLDPOINT
c1c4c81b-d082-4d13-994d-861f9683f95e | section | 3 - Close-Out
8c71e652-4e79-4471-b4a9-3b4afbaea4b6 | checkpoint | 3.1 - ITP close-out.
fb5d5713-e9e6-5f69-b2bd-215c77e30b22 | note | Specification Reference - GBA-SPE-AR-AS-0001
344b85f7-238d-5d80-a670-71ebc1486f24 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
68a94464-f939-5fdd-a498-9c5e9d12533a | note | Test/Inspection Frequency - Each Lot
914c1f89-e8cb-5c63-81f7-593eaeed83be | note | Inspection: John Holland - QR (R)
5ea5607d-84d7-5f0d-bb24-0d8a8055760b | note | Records & Comments - Check all measurements are recorded and photos attached.
c079e027-5177-5422-aa51-51e93c2819bd | note | All records loaded into the Work Lot System and Verified.
d586850f-473f-46f1-9fc4-320956b798c9 | checklist | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 - 03 - Epoxy Screed to Falls (Entire Ensuite) |  | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 - 03 - Epoxy Screed to Falls (Entire Ensuite)
5705efe1-9534-47e4-8a37-b1cedb12c71f | section | 2 - Construction Inspections
3e00d6b6-9ccc-4889-bd5d-1433c672c1c3 | checkpoint | Inspection Details
fd552ec3-1842-5553-bea3-ab498b73f597 | textbox | Level:
dcee6dec-378f-5e05-a6cf-0e0f0196e2e4 | textbox | Zone:
ce49dddb-6ad7-4311-a7d7-837ed8287532 | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
7b9efbea-5ab1-5753-8091-3261a1501df9 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
03695815-85f0-5f8c-9666-4d1bb6df11a4 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter
7ef569c0-15b1-5269-bad6-ab39eac05882 | textbox | Test/ Inspection - Measurement
d1b94ec5-74cb-54a4-a204-f58bf704d9cf | note | Test/Inspection Frequency - Each wet area, every 20m2
89bd12fa-7361-5d7d-8d22-593506c9ec39 | note | Inspection: Subcontractor - WS (I)
5c86ae6e-d2bf-53e6-bb8d-7c6367e1125d | note | Inspection: John Holland - PE (S)
28e9dc0f-8341-4bd1-90bf-5a471e189eaf | checkpoint | 2.2 - Drainage installation - puddle flange installation
3857ad5b-ddcf-53e8-99e2-76f4bb056741 | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
0a6b37ca-4b10-5aba-af2d-46b1a2084b35 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
c4473cc2-4df8-5ad7-9bf6-8cc163e51635 | note | Test/ Inspection - Installation and Inspection
631f02ba-bf9e-5d6a-8cf0-970d01567027 | note | Test/Inspection Frequency - Each wet area
6198d22b-97b3-548c-b092-c63e112ed799 | note | Inspection: Subcontractor - HS (I)
47c2420c-3346-50a5-8c61-113a91573405 | note | Inspection: John Holland - PE (S)
71e9b6cd-f366-41b2-b5de-3eaa920abec6 | checkpoint | 2.3 - Substrate condition Inspection
62231e37-16fa-5bce-84b5-57e2cfa3721a | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
877ed5a8-4b15-5a78-b05e-e3cabc662dc8 | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
a515e233-ff29-5648-8565-b96a7664cb82 | note | Test/ Inspection - Inspection
02e70da2-529b-5794-ab2b-fa570cb567ed | note | Test/Inspection Frequency - Each wet area
8775fd3c-0f1a-5d2f-a6bc-c90808dbdd77 | note | Inspection: Subcontractor - WS (I)
a18c0ec1-6e07-57cd-b08b-7cf3f380b730 | note | Inspection: John Holland - PE (S)
80aa8c34-8859-4009-aca6-09e938d986e6 | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
e35bfd4d-f10d-5c5f-8cc9-054ba74e397d | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
218da305-d568-5974-8f78-9795e2de5438 | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
06eae9b9-5fac-53c9-87e0-bdcc1b23e7d0 | note | Test/ Inspection - Measurement
3e917cc0-36e7-50e4-930d-3e05fded8646 | note | Test/Inspection Frequency - Each wet area
2faeeaa9-ef31-5ef6-be82-b6506c765961 | note | Inspection: Subcontractor - WS (I)
b5ff842b-b3fc-5ef1-9183-8d72bddb97f9 | note | Inspection: John Holland - PE (S)
276e7b20-aa2d-463a-9aeb-291abbc8b21b | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
900e2998-108a-5481-b62b-57118fab3af4 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
be9eda68-5733-526f-bbb3-a1b31f789ae6 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
cea1c192-7a3e-5c25-8111-e09f080b0f4d | note | Test/ Inspection - Installation and Inspection
087e3000-bfa2-5559-bd12-ced5e119dea6 | note | Test/Inspection Frequency - Each wet area
0fe8709f-571c-547b-9959-8b2b7944fd1c | note | Inspection: Subcontractor - WS (I)
0a4f1601-aead-5845-b397-df311a014d5e | note | Inspection: John Holland - PE (S)
72640518-008f-5120-82f1-3412d2ec8f17 | textbox | Records & Comments - Measured fall:
8d5bede5-6eae-42ff-98aa-9f2c67be3ca8 | signoff | AUTHORITY HOLDPOINT
b986b216-f74e-42b5-b461-db73ceb913b9 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
9f45d381-88dc-5f5b-907c-6abf191af133 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
d3d54a0c-3495-5460-bd3c-38ece344985d | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
dfd14eaa-8ee7-50cf-b9a3-e2db78456272 | note | Test/ Inspection - Measurement
e2e932f8-9abd-5d79-b9c4-6455f9f3576a | note | Test/Inspection Frequency - Each wet area
90c07b86-18c4-51ab-bf6a-f80864feb86a | note | Inspection: Subcontractor - WS (I)
4ada9bb2-72d0-5c0c-b953-e488b6d29068 | note | Inspection: John Holland - PE (S)
d289fb5b-c5f2-4e3c-8b94-f1303b073d0c | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
0321b13b-4d14-5409-99bd-704bd8b02769 | note | Specification Reference - GBA-SPE-AR-AS-0001
c5fb671a-c6e9-5ae5-a4a0-4a8af4ac4e1d | note | Acceptance Criteria - Everything ready to install
443f70cb-881f-5948-a97b-51ca8516fd0c | note | Test/ Inspection - Review & Verify
6b66c611-50ce-56db-9fbb-81f8c19b3bfa | note | Test/Inspection Frequency - Each wet area
dae008d6-3868-537f-bc55-8afd61202590 | note | Inspection: Subcontractor - WS (I)
b26ab503-e3bd-55b3-ac11-2d426adc2bfc | note | Inspection: John Holland - PE (S)
7a736ebe-f853-5b31-a357-21fb1c79fd14 | textbox | Records & Comments - Temperature Reading:
9e5efdd3-7579-4364-a1df-a007cd034b24 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
66221cb0-b393-5d60-beae-9508da42bc23 | note | Specification Reference - GBA-SPE-AR-AS-0001
16a039e0-5e32-5614-b3d0-f73d5348c03d | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
90a831af-6c33-50b0-91ad-43149d8e4a71 | note | Test/ Inspection - Visual Inspection
25de734f-c23d-5011-b5c0-9788ceb36911 | note | Test/Inspection Frequency - Each wet area
5275132f-bdee-5204-a3d7-5388f8709968 | note | Inspection: Subcontractor - WS (W)
1d11dc3b-c9b3-543c-b501-0ab144eb3838 | note | Inspection: John Holland - PE (I)
6b6f3495-e960-50d2-84b2-8311b452a50d | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
b00ef212-0bb9-5c88-843a-debf0103c662 | textbox | Applicator Names:
cf2c30df-32bb-5436-8734-a2b8fd201bb2 | textbox | Temperature at placement:
67280f88-6115-4bba-8aac-8a1e11c2f9cd | signoff | AUTHORITY HOLDPOINT
9556d0f3-6019-491d-aaac-0d9339a96f9d | checkpoint | 2.9 - Apply Flowcrete Resin Primer - take a photograph of the primer container with technical details and a photo/video of the application
8f722539-d148-5f1f-9e5e-bd74947aaa87 | note | Specification Reference - GBA-SPE-AR-AS-0001
93fe95e8-2b10-5d97-be90-42452308bbfd | note | Acceptance Criteria - Flowcrete Resin Primer Applied
60bccef5-f8bf-5ed4-82aa-a312e4091b49 | note | Test/ Inspection - Installation and Inspection
eb2b7f48-534d-58d6-b923-f0970e58b955 | note | Test/Inspection Frequency - Each wet area
b010d277-173f-5022-8415-274a2453e0e4 | note | Inspection: Subcontractor - WS (I)
3cecdd0d-b596-53be-a3fd-ecef9c180636 | note | Inspection: John Holland - PE (W)
9f4bb5a0-e68e-4567-ae3d-b2efceacb0af | checkpoint | 2.10 - Apply Epoxy layers in line with data sheet and the figures in AS3740 - take photograph of epoxy container with technical details and photo/video of application - note details of timing on checklist
efd27738-7eb3-520b-bc81-34cef408565c | note | Specification Reference - GBA-SPE-AR-AS-0001
ceef762c-3d93-54fb-a778-3dc5273d6146 | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
87844ed8-bc0b-530d-9026-f3396b8051fb | note | Test/ Inspection - Installation and Inspection
5b877c2c-a894-57ac-92ad-74ba92dc6d04 | note | Test/Inspection Frequency - Each wet area
fc6c233b-aa68-5724-94a4-f0c6d8ab7de9 | note | Inspection: Subcontractor - WS (I)
07768d8d-7035-5ceb-bba4-cc9545104d60 | note | Inspection: John Holland - PE (W)
8ddf3922-48ff-447b-acf6-c5ee575194fa | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the epoxy and completion of installation.
c22955f6-5500-5132-b2d3-254bec71f553 | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
18bab788-fada-58d3-afef-0d07a59d3ca6 | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
f55af1a6-3213-50ac-b17d-961263ad5f5a | note | Flowcrete Resin Primer curing times
1b823270-4d1b-5ef4-b700-9e6a0ea57623 | note | Full Cure time: 24 hrs at 20°
9128f6a7-0c90-5918-b250-aa14b44bc226 | note | Test/ Inspection - Installation and Inspection
f169d399-c548-592e-a77d-38a51d17d9b2 | note | Test/Inspection Frequency - Each wet area
27a4595b-049d-50cb-a098-632c9de0292c | note | Inspection: Subcontractor - WS (H)
83f28a65-73e9-5da3-bc5a-ab11cc07ec87 | note | Inspection: John Holland - PE (H)
2fb7c3f6-16bb-55dd-a910-0fc4763fc501 | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
ed138a40-2292-5ab8-a2aa-6428c4e014a3 | textbox | Layer 1 time:
8df00dc5-849f-567c-90b6-b606a84583d3 | textbox | Layer 2 time:
1ff0e852-7b0d-4c4c-b1a8-4aa185ae0d6b | signoff | AUTHORITY HOLDPOINT
b2deee35-080f-46ef-b6a9-763de232908d | section | 3 - Close-Out
2b48e2b2-f1f6-41ff-bc07-be97c2046732 | checkpoint | 3.1 - ITP close-out.
d242caca-20f5-5547-89eb-6fd2e600bc18 | note | Specification Reference - GBA-SPE-AR-AS-0001
8a68025c-fcb5-5ff7-af32-5acadc45dab0 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
23f86fc0-8682-5fb1-9c8f-7200a7244661 | note | Test/Inspection Frequency - Each Lot
a7e0f542-6bb8-509d-88cb-fb1d036fcfbe | note | Inspection: John Holland - QR (R)
da85a9b2-250a-5bdd-a973-e73b03b3da55 | note | Records & Comments - Check all measurements are recorded and photos attached.
038ac2ca-e584-5bcc-a6da-5c90ceaa8171 | note | All records loaded into the Work Lot System and Verified.
de4d4179-ff62-4d57-bd82-92f025abb427 | checklist | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 - 04 - Epoxy Cove to Ensuites |  | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 - 04 - Epoxy Cove to Ensuites
c734ef3c-d082-43dd-b892-2eed0f383abd | section | 2 - Construction Inspections
bdbc18d0-7dd0-455f-8720-dfaff741ae33 | checkpoint | Inspection Details
8b44dd3a-1dd7-5e2b-b6c0-9e3dc9125b2d | textbox | Level:
ca25acb0-8685-5754-9fc6-f7eaff176cfc | textbox | Zone:
49941a0f-54e1-4085-a4fb-4c92224fac28 | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
e1ac63f6-b7ea-5323-accd-ee9a613c3b1e | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
ef11dab9-2ffd-5ed9-bb6d-de3ee537eb8c | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter
c2040d9c-e30d-5642-b636-0fafc03a1cca | textbox | Test/ Inspection - Measurement
bbea77f2-6bf9-54f5-bf52-65f4ca7f8702 | note | Test/Inspection Frequency - Each wet area, every 20m2
a705ab1d-a415-5a57-845f-b65714ca18fd | note | Inspection: Subcontractor - WS (I)
a60f884f-2c6f-52ff-8846-727e559f9662 | note | Inspection: John Holland - PE (S)
37a25879-a1ad-48e5-a6dd-8825841d1496 | checkpoint | 2.2 - Drainage installation - puddle flange installation
373f8b11-da38-5935-8f45-e1bf80021ca4 | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
a6d5c264-63bd-571d-bca7-55c87dfea678 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
306dabaf-7cf9-537f-8b1d-25a7f2e97ec2 | note | Test/ Inspection - Installation and Inspection
cc2afce6-cc82-5b18-b4f9-239c1775c09d | note | Test/Inspection Frequency - Each wet area
5a44069d-8a63-5167-aeb1-fe9c94ea88c8 | note | Inspection: Subcontractor - HS (I)
e755d374-d6cb-51f5-bcc0-77e9c5f51cc0 | note | Inspection: John Holland - PE (S)
39c8d950-5a76-4d03-aa1c-c05cfb5ecdbd | checkpoint | 2.3 - Substrate condition Inspection
b7fd1834-ea58-5cb9-a8c3-29ae50b3855c | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
ad61b424-cb6c-5074-834d-927bc8ac2117 | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
b8d1a0cf-f9fe-5e75-91ee-ea6f24cd7d25 | note | Test/ Inspection - Inspection
a07b0e8a-4cff-5376-b47a-13aa7efa09db | note | Test/Inspection Frequency - Each wet area
151641f0-4702-5d1a-bac8-be06b1c2745b | note | Inspection: Subcontractor - WS (I)
9b7e919c-e1b5-53a2-9e2f-56ee7d10f9cc | note | Inspection: John Holland - PE (S)
a601365f-6e77-4399-8d00-322843ae8bb7 | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
981ff686-6e70-5a67-b39f-5bb0fd9432f5 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
914c2cfc-597f-5508-8019-85e943023d41 | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
00c922dd-5533-537f-a362-9a756fec2745 | note | Test/ Inspection - Measurement
93e9d3a5-9e46-5322-b932-0953f984630d | note | Test/Inspection Frequency - Each wet area
b2b4e84b-5d87-523e-a3fa-fbfbe113be39 | note | Inspection: Subcontractor - WS (I)
96ee8337-de4c-5f5a-85e9-c091b536e549 | note | Inspection: John Holland - PE (S)
1f6c1b4b-fcc3-42f1-adc8-36e500f6f1b9 | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
406176f4-4554-5426-ad3d-da278b800fe3 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
9bb203ff-a316-5f66-ba5b-6934ed1a9ab1 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
4bd81646-8343-5bc3-8ff1-311547cf8684 | note | Test/ Inspection - Installation and Inspection
c1b61334-83b1-5534-943b-0e6de72119bb | note | Test/Inspection Frequency - Each wet area
80a5f57f-55e5-5656-83bb-f81dc78df407 | note | Inspection: Subcontractor - WS (I)
f5616b07-321b-5a43-8f4a-43f834cac152 | note | Inspection: John Holland - PE (S)
589b81e9-f340-5d8e-bfac-6f535c27afa1 | textbox | Records & Comments - Measured fall:
f3c0748d-b0cc-4fc1-8439-08f7bb8b714e | signoff | AUTHORITY HOLDPOINT
3c4f683b-91aa-4f67-b347-2e7c2145fbcc | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
b3f69db0-dba9-53fc-8ea5-4d4a378c7fd2 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
4d8245fe-ef0e-5aa1-92bf-88ce03b08077 | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
b6007af8-2102-526f-8985-ce32ef31c0aa | note | Test/ Inspection - Measurement
cc6cf3e3-b293-5fef-9e92-7494bac9a7a5 | note | Test/Inspection Frequency - Each wet area
b33fe59d-10d3-5b9c-bd8f-19a67a4ffcc6 | note | Inspection: Subcontractor - WS (I)
e17026dd-80d7-50f7-b184-93d88771ae16 | note | Inspection: John Holland - PE (S)
e19e33b6-1f33-4aca-9148-5c9abc494f49 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
64f5601a-719b-53e6-8389-76e77785bf78 | note | Specification Reference - GBA-SPE-AR-AS-0001
74e866dc-38b3-5aee-8ae3-1850bedafff6 | note | Acceptance Criteria - Everything ready to install
40d0420f-2b2b-5020-aa20-67555d8e74ed | note | Test/ Inspection - Review & Verify
b12fc576-01c3-5cbc-8963-e07348c70bcb | note | Test/Inspection Frequency - Each wet area
f621b8c4-00a3-50cc-9ae3-7c89a57525b4 | note | Inspection: Subcontractor - WS (I)
5e69ad1a-5cac-518f-8abd-6511b5940cca | note | Inspection: John Holland - PE (S)
2210d925-09b5-55f3-9a3b-fbcea6016da4 | textbox | Records & Comments - Temperature Reading:
ceff4968-9ca1-4991-88a5-1acf5614ab50 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
0d664132-112f-5ac9-b5b5-6590a2845cf5 | note | Specification Reference - GBA-SPE-AR-AS-0001
a1dd07ac-8da9-5ca7-a9e6-62035ff64326 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
076681d0-d3a6-5ccc-be7a-cb9f199a3e35 | note | Test/ Inspection - Visual Inspection
fdaee7ac-ee82-526b-9577-9a90eed74e0a | note | Test/Inspection Frequency - Each wet area
aa59c6af-6247-5e5c-a774-c6f341f152d3 | note | Inspection: Subcontractor - WS (W)
194a5620-5aab-58c1-a74c-8f81e852046c | note | Inspection: John Holland - PE (I)
debd0064-2fd1-597f-87b1-25d4568a824e | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
eb44bd52-f7e9-56ae-8395-a417e425e7d1 | textbox | Applicator Names:
b31696f2-7600-53f4-86d2-c908d13e3ab2 | textbox | Temperature at placement:
a0e3a80a-fbfd-4a25-96b1-d16679b1e628 | signoff | AUTHORITY HOLDPOINT
1e3963cb-016f-433a-a739-2550219fa2ee | checkpoint | 2.9 - Apply Flowcrete Resin Primer (with sand) - take a photograph of the primer container with technical details and a photo/video of the application
5ccedb61-96f9-5f5e-b805-a8e11ce40292 | note | Specification Reference - GBA-SPE-AR-AS-0001
c2386289-08e6-5c7e-891c-8f0dd3b7f439 | note | Acceptance Criteria - Flowcrete Resin Primer (with sand) Applied
47aebeca-aef8-5b76-ab1b-c532b818178a | note | Test/ Inspection - Installation and Inspection
1abcf3f7-f741-5a18-9a46-c91d29711479 | note | Test/Inspection Frequency - Each wet area
02595bde-4792-559a-9ee8-a6105717cc1d | note | Inspection: Subcontractor - WS (I)
6d9f2045-41fb-5399-8a27-f04f604deb31 | note | Inspection: John Holland - PE (W)
676ecb67-7415-4c43-8eff-c692cf16c19e | checkpoint | 2.10 - Apply Epoxy layers in line with data sheet and the figures in AS3740 - take photograph of epoxy container with technical details and photo/video of application - note details of timing on checklist
fb6352dd-f98e-5e13-a791-35f4f8335117 | note | Specification Reference - GBA-SPE-AR-AS-0001
ec49e960-bee5-560f-9e9d-60da86c58130 | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
d8c92336-8168-58e1-86c6-69272972ab72 | note | Test/ Inspection - Installation and Inspection
ee5fad69-30aa-537c-a98a-6cda3f7cfdaa | note | Test/Inspection Frequency - Each wet area
5abaa3f3-17ec-599b-b9ec-c68fb85ab1e6 | note | Inspection: Subcontractor - WS (I)
8c137040-9261-5bd0-b9ca-059719e99ae0 | note | Inspection: John Holland - PE (W)
1bc67400-3e08-4bf0-8f74-a9cbc8cb1fa3 | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the epoxy and completion of installation.
95fa2159-a2d9-50d2-bd38-23b9f88c11a0 | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
bd5d45a4-38f1-5fa5-b50a-0d81f28d04cf | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
d0e87f00-1bea-5f19-9d7b-6672934cca74 | note | Flowcrete Resin Primer (with sand) curing times
0aa49114-7063-51d1-a972-f66a16bec950 | note | Full Cure time: 24 hrs at 20°
a4999ec0-f4f3-5944-8247-010d5bd93d0e | note | Test/ Inspection - Installation and Inspection
e63cd52b-b3ed-58ef-85dd-1c50a0e9245f | note | Test/Inspection Frequency - Each wet area
5a91e466-c82e-566d-b3c0-7f3cdc08060a | note | Inspection: Subcontractor - WS (H)
d0c443cc-eaf5-5833-b24e-14da88829335 | note | Inspection: John Holland - PE (H)
5dc53f70-1462-5c8f-a5e6-1984b837f2be | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
5bf8efe4-a08a-54ca-a5a2-98619ddca488 | textbox | Layer 1 time:
02126d05-2608-5a32-b1ca-b9ec114d7b3c | textbox | Layer 2 time:
c0097244-56a0-43a4-aa0f-767ec349654d | signoff | AUTHORITY HOLDPOINT
d0f9ea95-1d5e-4b56-9060-71aa7792f624 | section | 3 - Close-Out
0ec7112c-9734-4e04-8531-ba042e63f529 | checkpoint | 3.1 - ITP close-out.
3ca1e8d2-507c-54bf-9aba-1093510275fe | note | Specification Reference - GBA-SPE-AR-AS-0001
9b118d20-303d-5b78-8331-69993bfaa41e | note | Acceptance Criteria - All prior items of this ITP have been complied with.
f5466cd7-7f88-5a93-a8b3-32f98ac2b8dc | note | Test/Inspection Frequency - Each Lot
c70cd5e9-550f-5cba-a373-676e2d6bc7b8 | note | Inspection: John Holland - QR (R)
74a0c27e-f4dd-5420-a0a2-d401064317e1 | note | Records & Comments - Check all measurements are recorded and photos attached.
b281b954-d1cd-5bfc-9aa8-1cf841d873b5 | note | All records loaded into the Work Lot System and Verified.
c4906f59-254c-4ca2-9822-357f5e713f8f | checklist | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 - 05 - Vinyl Flake to Ensuite Floors |  | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 - 05 - Vinyl Flake to Ensuite Floors
c28ba002-b3ac-4bbe-b0f4-9f7573ba6971 | section | 2 - Construction Inspections
0c7e8ec2-c349-4f33-8385-c7fc98cf53e2 | checkpoint | Inspection Details
415b1164-049e-5a92-a55b-0049e0b7dce6 | textbox | Level:
885ad02b-22d0-5543-b3e3-c96bf542113b | textbox | Zone:
5f96d6e5-bea7-4172-b43f-19118ee76f49 | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
cfb919b5-9e6e-5a6b-b66b-5f5bc6e939f4 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
e807ebf8-d893-5ee4-990f-272407cdf3a8 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter
63b50365-5111-5445-ac2e-144e52899119 | textbox | Test/ Inspection - Measurement
602464c3-46b6-5f67-9bfd-3ec69e3bca92 | note | Test/Inspection Frequency - Each wet area, every 20m2
4c75f12b-0107-5600-8719-0f996af69985 | note | Inspection: Subcontractor - WS (I)
902a4373-3ad8-5772-a0a5-e406a2f1e588 | note | Inspection: John Holland - PE (S)
ac7e3aa4-93b8-40cf-96ba-a8cb8bb94175 | checkpoint | 2.2 - Drainage installation - puddle flange installation
5c0e4391-1168-5b4b-9118-334d6036cf04 | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
921034ca-f2e6-548b-8a4f-d78e63654036 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
16f60a1f-20d5-5f84-a86e-962dba489934 | note | Test/ Inspection - Installation and Inspection
6d860e06-1e34-50f6-9a29-0922ee009992 | note | Test/Inspection Frequency - Each wet area
baf5ee5c-0e92-5bc5-9251-890b539af18d | note | Inspection: Subcontractor - HS (I)
bb08898c-1290-5256-9004-2c7195edaceb | note | Inspection: John Holland - PE (S)
451ce4f2-0eeb-4e9f-9d21-ffeb6481fa9f | checkpoint | 2.3 - Substrate condition Inspection
8b5e64bd-5ab5-5bcb-a20c-91e67826bb0d | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
a90fd467-dac2-52f8-a637-96816d673e37 | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
cbbdbb7a-b12b-538a-ba9e-9465599a1412 | note | Test/ Inspection - Inspection
488c4f06-b24c-5891-88bd-3de9eb0b0eb5 | note | Test/Inspection Frequency - Each wet area
46f25f13-8dcc-55d8-abf6-01caddae9bae | note | Inspection: Subcontractor - WS (I)
01918f5a-a62a-5543-8071-cb4d1baa551f | note | Inspection: John Holland - PE (S)
57516d56-0197-4206-b6f0-f704669cf29c | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
7e30bd7a-a394-5e52-8e2b-e90bf6ed2671 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
b0bee1ba-0704-56be-9986-7487fa5d3d9c | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
899768cf-d202-5af1-9bc4-558587574e57 | note | Test/ Inspection - Measurement
2db40c69-cc17-5ee8-a2b9-a429f0b522d2 | note | Test/Inspection Frequency - Each wet area
1204017b-eba1-5cbe-8ed3-1f37730e0a3a | note | Inspection: Subcontractor - WS (I)
7908f551-408e-5269-b162-b80c9d53fb4f | note | Inspection: John Holland - PE (S)
3899c94f-a97a-4864-8e25-b00e2059104b | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
dbf5d570-57e2-5f82-901f-af91d7a55e0c | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
2f5bb83d-4ef0-5c64-8812-dee843de4fc7 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
e706a161-e8dd-5ba4-82b9-2e8472a920f2 | note | Test/ Inspection - Installation and Inspection
486a12d3-83ad-52f4-b6a4-bbe667843fd9 | note | Test/Inspection Frequency - Each wet area
26d2c6c3-ce22-5399-a7b4-3f7bd0bd96aa | note | Inspection: Subcontractor - WS (I)
f7ef25b3-e25d-545d-bc90-e08a31e00b06 | note | Inspection: John Holland - PE (S)
e4fa2196-271b-5956-b295-7d0c7cc06663 | textbox | Records & Comments - Measured fall:
86a26802-4b33-4b92-aa4d-719184367bc1 | signoff | AUTHORITY HOLDPOINT
e72c1616-0944-4a67-bf3c-aa38d6045715 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
84fd2d7b-92d2-50c8-8b4c-33182e6e8e73 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
726237b3-c192-526e-9569-524b59b27dd9 | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
e72731aa-7c17-5f5c-977f-c0e1c9eb5bf2 | note | Test/ Inspection - Measurement
16543341-122f-5f4f-88db-23da69202627 | note | Test/Inspection Frequency - Each wet area
8d5a623d-bcd1-5909-8baf-7381beb83178 | note | Inspection: Subcontractor - WS (I)
f623f607-f4c1-5908-b5d8-21223bcd0614 | note | Inspection: John Holland - PE (S)
3f0b5d97-5ace-4af5-a078-6d8a30d62353 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
0cb74ebb-f341-5b13-8665-f2702de93725 | note | Specification Reference - GBA-SPE-AR-AS-0001
eeb6ed38-d8a6-50ff-9a5c-6d9b7a14c99b | note | Acceptance Criteria - Everything ready to install
64d8befb-344c-5b9e-8f7d-87c388f8bda3 | note | Test/ Inspection - Review & Verify
a7dbc55b-4480-53dd-a2ba-8d8279fe1deb | note | Test/Inspection Frequency - Each wet area
588d2595-081b-5b7c-a513-4668bc5abe99 | note | Inspection: Subcontractor - WS (I)
0f7f455d-e189-5e37-8332-304d95690bf4 | note | Inspection: John Holland - PE (S)
53ae6d5f-cd63-5a6a-bbee-e812c556e020 | textbox | Records & Comments - Temperature Reading:
f073275e-51a3-409b-bf04-fceb083ef85a | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
b0cc3902-a5d1-54e6-8070-6a221c59062a | note | Specification Reference - GBA-SPE-AR-AS-0001
1a70b786-cf2c-54c3-a3c6-7cfd796be88b | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
4af4785a-a7e7-5307-865a-86ad72aeb847 | note | Test/ Inspection - Visual Inspection
195cb60f-2403-5036-b62e-e29c9d854b06 | note | Test/Inspection Frequency - Each wet area
cd84f065-338a-52fb-b907-bd311c5bdd58 | note | Inspection: Subcontractor - WS (W)
f4bbeb9d-526a-5c7f-ae48-ad2c07890e90 | note | Inspection: John Holland - PE (I)
8d8ea405-90f7-5a76-9398-2a84d628630e | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
341e9dda-34c2-5e5e-8cbd-16359370d5fa | textbox | Applicator Names:
386db646-f48d-56ca-8364-f08d96700311 | textbox | Temperature at placement:
e34ee2bf-db4b-442e-8a74-f89fe63448fa | signoff | AUTHORITY HOLDPOINT
9c99cf2b-b1aa-44b4-94be-ae2114356106 | checkpoint | 2.9 - Apply Flowcoat OP Suck Coat Primer - take a photograph of the primer container with technical details and a photo/video of the application
e3122210-9ae9-56ef-a784-ee3a80388162 | note | Specification Reference - GBA-SPE-AR-AS-0001
ff4e932e-851c-5fcb-87b3-e8ae7b8dd496 | note | Acceptance Criteria - Flowcoat OP Suck Coat Primer Applied
d1f97a51-7c03-59a6-a531-e24e3a100f3e | note | Test/ Inspection - Installation and Inspection
d796dc43-ec64-5817-aa37-f8c88905d3cd | note | Test/Inspection Frequency - Each wet area
5dbc6b13-81f9-534d-8d10-d60e13b54058 | note | Inspection: Subcontractor - WS (I)
04adc975-d651-5b6b-bda2-54898b786fbf | note | Inspection: John Holland - PE (W)
c4e48dd3-9747-4c57-9517-7953ebb8bcdb | checkpoint | 2.10 - Apply membrane layers in line with data sheet and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
209b129e-f19f-57f3-af76-66faf117ab2d | note | Specification Reference - GBA-SPE-AR-AS-0001
31a01307-523f-5e58-94cd-959457fdf79c | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
9ac5ea0f-b91b-55f5-8b84-bd97a7e126b3 | note | Test/ Inspection - Installation and Inspection
98cd52ae-d375-58b7-a326-792ee62b7c37 | note | Test/Inspection Frequency - Each wet area
e7ff1a29-15d5-5de3-91c9-36d134b4f757 | note | Inspection: Subcontractor - WS (I)
e74bed99-df4b-5fe6-829c-9f2ad15dfc72 | note | Inspection: John Holland - PE (W)
40c90799-ba42-4665-886b-0791850c4c0f | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
c2bc5d1b-31df-519a-8025-c9cb4f124bf7 | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
2ecdab18-26d8-5b8d-bc33-4a09c80093e1 | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
cb3bf72d-2a9e-5f3b-83b4-6e29fdf6d8e5 | note | Flowcoat OP Suck Coat Primer curing times
5de24166-10b0-5eaa-b4c3-060c95738ce4 | note | Full Cure time: 24 hrs at 20°
d23cb288-9dd4-50ee-95fe-f8f8bb54964a | note | Test/ Inspection - Installation and Inspection
b88e01ab-5435-530d-b17e-6ac4f6960621 | note | Test/Inspection Frequency - Each wet area
4041bc98-e091-50e1-8751-bfe5bbe08e9c | note | Inspection: Subcontractor - WS (H)
b8b72147-7b88-5028-abab-ffd391c599fe | note | Inspection: John Holland - PE (H)
130b47f7-9251-5a38-8d03-3940f4c18cc8 | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
3bfaccd6-57ee-5516-bc52-892b1ba67172 | textbox | Layer 1 time:
09b3e165-98a6-582c-a793-8281b1b8be7d | textbox | Layer 2 time:
cb92591d-1409-47f3-95fc-887797a84204 | signoff | AUTHORITY HOLDPOINT
d5981e78-c4d1-4234-a15c-b1cde469bf6a | checkpoint | 2.13 - 100% Witness Point: Supervise the follow-on Subcontractor(s) to ensure protection has been applied to Vinyl Flake.
632da26a-cd51-5841-a1ad-135e1e74e25e | note | Specification Reference - GBA-SPE-AR-AS-0001
57819992-f3c5-515f-81fa-1f62807a0a2d | note | Acceptance Criteria - Each layer applied in line with MAMS requirements - dressed into puddle flange
35b11093-6ba7-5d66-ab06-d63c250fd448 | note | Test/ Inspection - Installation and Inspection
1b57491c-95d7-55b3-9be3-aa40343f4816 | note | Test/Inspection Frequency - Each wet area
9c6110b2-0d59-5d71-b7e7-0142062d9786 | note | Inspection: Subcontractor - WS (W)
d1f09f6a-0761-55c3-9e0c-2535b8fb39ec | note | Inspection: John Holland - PE (I)
495798c3-f99c-415b-965d-d123f2b463a1 | section | 3 - Close-Out
68541eb7-bed1-402b-aa98-c3e25999740c | checkpoint | 3.1 - ITP close-out.
2b3c1272-db5d-59d2-bfd6-8a3e01931947 | note | Specification Reference - GBA-SPE-AR-AS-0001
ccf39850-9ffa-56fb-b728-6273a8d5fbe9 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
9428baa5-81bf-5791-96f6-14f648143d78 | note | Test/Inspection Frequency - Each Lot
8495c185-5a72-5011-87eb-5b77d93f3e3d | note | Inspection: John Holland - QR (R)
0cad43d9-b45c-5f4f-869e-74c679be2d1e | note | Records & Comments - Check all measurements are recorded and photos attached.
604e9271-7ca1-52e1-ad4a-059dc66cbad9 | note | All records loaded into the Work Lot System and Verified.
93c6ec1d-8d30-4b91-a1b2-32c1cc2200b0 | checklist | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-05 TREMPROOF 90 UNDER WET AREA SCREEDS BUILDING C&F |  | Standard ITP - Aus Standards - Wet Area Waterproofing WP-08 TREMCO VULKEM 350R/951NF BUILDING F Under Plinths
9e5178fe-275d-4f66-a1d8-c2dfb2595b6e | section | 2 - Construction Inspections
9b42ef48-75ff-4fe0-b45f-d63fa7a00f94 | checkpoint | Inspection Details
99147e17-537f-5b03-9da6-e50edb4527ab | textbox | Level:
bd41c8d2-bfda-534c-808b-7f0e4dc584f0 | textbox | Zone:
2fcdccd6-ea1b-4aed-8a70-0e17ed1f631d | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
96201ade-dcca-5b3d-a6c5-a3ae93feee85 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
99c3f8df-eff4-5c8d-b2f4-6f1d29088d76 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter
ea421e94-008a-5c8d-8b8e-a7601f157c73 | textbox | Test/ Inspection - Measurement
f86ac474-28c1-5697-be6a-e58d9bc3daf5 | note | Test/Inspection Frequency - Each wet area, every 20m2
6cf3e71d-c2ee-5a5c-ba3b-674348252abf | note | Inspection: Subcontractor - WS (I)
4565c4c6-4d2d-5474-95ab-41343318208a | note | Inspection: John Holland - PE (S)
90e49087-aac7-40a7-9806-ef8e4a339d89 | checkpoint | 2.2 - Drainage installation - puddle flange installation
2f3646ab-f896-5188-8e2d-b9987d4aec3f | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
cc328293-f678-536a-a587-7d253099f364 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
bae9c3b4-910f-5f63-ab36-ad95261ee082 | note | Test/ Inspection - Installation and Inspection
fd6c5132-e6cc-555a-914b-f6b58b43ecaa | note | Test/Inspection Frequency - Each wet area
674d7feb-eba4-5a6d-b15f-ee634970b934 | note | Inspection: Subcontractor - HS (I)
b23f7f36-3ad2-559f-908a-4d2593e464cf | note | Inspection: John Holland - PE (S)
0ffe2ed6-0447-46cf-afed-d36722c5e0ad | checkpoint | 2.3 - Substrate condition Inspection
5d6d53e5-3aa6-551c-bf8f-18cdce1ad464 | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
afe4b9f4-3b64-5a38-830b-95b79c4d457a | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
a82dd030-d95a-5c07-b8db-bfc492829914 | note | Test/ Inspection - Inspection
ac9e23b1-27d4-5e1c-ad64-e3d2eca86ca5 | note | Test/Inspection Frequency - Each wet area
ee4390cb-133c-5109-9c57-606c7eefbaee | note | Inspection: Subcontractor - WS (I)
f35105ec-12af-5c69-be4b-b4cadbd65ca1 | note | Inspection: John Holland - PE (S)
1f992917-9d30-4dfa-a190-aeab456f663c | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
92c8c68d-6b09-5dab-a8fd-05b6d5d32c88 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
da5a0942-7821-5f26-95fa-208ff67a190b | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
98fefd0d-925e-5bac-bf98-551f884c2609 | note | Test/ Inspection - Measurement
faeff10b-75b3-56af-b2d7-c899a11a825a | note | Test/Inspection Frequency - Each wet area
6f9a24e5-1fdf-589a-a5e3-636478bf997b | note | Inspection: Subcontractor - WS (I)
2b56515e-cb5f-50af-9e8a-0cb87667a866 | note | Inspection: John Holland - PE (S)
b93e8744-eb60-43cc-b6f4-0ced895eba20 | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
9ff264ad-7b1a-5588-8be7-20ea17178676 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
6e64d360-6c59-544c-a28c-b65ff527bff4 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
27a16273-0284-5da2-824e-9d581be54185 | note | Test/ Inspection - Installation and Inspection
77554298-3ff6-5ad6-bb6a-e873adddcdec | note | Test/Inspection Frequency - Each wet area
e0d31f59-aadd-56f9-909f-ce37e131c572 | note | Inspection: Subcontractor - WS (I)
90b6b4f7-00c0-580c-ac34-731f05263758 | note | Inspection: John Holland - PE (S)
757c4c65-646f-502d-a7de-8f021f3fc7b2 | textbox | Records & Comments - Measured fall:
a780a240-67e7-4191-904f-7258db7dc85f | signoff | AUTHORITY HOLDPOINT
2666ef5e-cf95-460c-ac99-83ddac1acbb4 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
79bfe317-3b2f-546e-bc6b-f5dc7d568ad1 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
f12bc53a-6929-5f5d-84e0-5bab2f48354c | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
8e5b2e9b-f4b9-5abc-87e7-9d5e03dd8622 | note | Test/ Inspection - Measurement
f89588fc-de39-52e8-8a18-7360cded0ffd | note | Test/Inspection Frequency - Each wet area
c1eba538-3d18-5187-8321-0533f090efeb | note | Inspection: Subcontractor - WS (I)
5a9359f3-994b-5135-9d9e-797967732386 | note | Inspection: John Holland - PE (S)
2be213cf-2d02-4723-97b8-f1fc23d44fa6 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
f751970f-6540-57ba-b412-8d2b32672122 | note | Specification Reference - GBA-SPE-AR-AS-0001
ebb244f2-ead3-5244-a116-dc3ad39ceefc | note | Acceptance Criteria - Everything ready to install
7cb8199d-10a8-51f6-b690-5ef87bf733fc | note | Test/ Inspection - Review & Verify
6a20f454-0874-5024-9c2f-57d9a3f1245a | note | Test/Inspection Frequency - Each wet area
4e31e055-551a-58f9-bd57-e136d261e47a | note | Inspection: Subcontractor - WS (I)
14cd3ca7-96e7-5161-a412-6f72a6f22d46 | note | Inspection: John Holland - PE (S)
d85e862b-a381-5224-b140-93cbe102eb65 | textbox | Records & Comments - Temperature Reading:
87bd8b50-8a98-481b-b23c-4939fce47521 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
512f2459-4989-57fd-ad57-d2f7979cf269 | note | Specification Reference - GBA-SPE-AR-AS-0001
ea74eded-b5d6-567b-b59e-7c1908389fc6 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
8bd7ebce-35d3-52b4-ad24-7b42f2548933 | note | Test/ Inspection - Visual Inspection
774528bc-26dc-50f5-afdf-946a3f6af122 | note | Test/Inspection Frequency - Each wet area
8eea14f0-25c6-56af-bfcc-4fb7ee102f22 | note | Inspection: Subcontractor - WS (W)
740e9fd0-54a5-5b05-8024-575c846eb791 | note | Inspection: John Holland - PE (I)
3ac9bde7-c3a0-51bd-a189-f34c7eea56df | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
c33abc46-1121-5322-ab2c-9c844f12f708 | textbox | Applicator Names:
90be6c50-2004-5485-a669-bb1c01f39847 | textbox | Temperature at placement:
867b5da5-6264-4fe9-9a76-772e0570c9b9 | signoff | AUTHORITY HOLDPOINT
35aecec2-4bb0-4d64-abc9-b30cc23777fe | checkpoint | 2.9 - Apply TREMProof WB Primer - take a photograph of the primer container with technical details and a photo/video of the application
5813fcff-c3fa-515d-8c3b-a671b0b2aaba | note | Specification Reference - GBA-SPE-AR-AS-0001
da34dfa3-7cf3-5726-b03e-3539abb3b1f4 | note | Acceptance Criteria - TREMProof WB Primer applied
91fb654c-3331-5b92-bc67-2e75291e064b | note | Test/ Inspection - Installation and Inspection
ffbdfd99-9cb3-562b-9786-45557b0c82e4 | note | Test/Inspection Frequency - Each wet area
4d1763be-d098-52a7-b459-7feefd43f296 | note | Inspection: Subcontractor - WS (I)
d8f55d01-8993-5e8c-b7d1-c95c9dced01e | note | Inspection: John Holland - PE (W)
a97bf58e-a112-485f-bc71-1e7dcfd70208 | checkpoint | 2.10 - Apply membrane layers in line with data sheet and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
4727dca9-1b29-5144-9636-2e05a8c1bd9c | note | Specification Reference - GBA-SPE-AR-AS-0001
584bbd90-8cec-55f2-baa5-0778ecd41975 | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
d8f86bb1-b253-56bd-be67-05449cda4fab | note | Test/ Inspection - Installation and Inspection
d4a7e3d7-5260-5106-88e0-52374e408355 | note | Test/Inspection Frequency - Each wet area
39a1f77a-484d-532f-a8e1-420f334a61fa | note | Inspection: Subcontractor - WS (I)
3242926e-197d-572c-8ac5-c34263573b39 | note | Inspection: John Holland - PE (W)
5c3bce6d-2258-4ac0-bf9e-b2c25e9a7551 | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
409eb6fc-ba24-5b12-aef8-22282f640cae | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
6ba4f540-26b5-5a8b-b95e-7444a69dbafe | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
9915773e-d4c5-5390-8fd3-0994e83b7b6d | note | TREMproof 90 curing times
e65ec7d0-d239-5e05-9a2d-82581ea78e41 | note | Full Cure time @23°C, 50%RH = 48 hrs
a3662691-c8f7-5906-9555-6e1be417e81a | note | Test/ Inspection - Installation and Inspection
42aebd7c-83be-5abf-8099-f271c2603b2e | note | Test/Inspection Frequency - Each wet area
bbc0a9e4-d3fb-5ad2-b79f-060bef2cb33d | note | Inspection: Subcontractor - WS (H)
40bfb9b5-2cfd-5fef-b5ae-5065c62bcca2 | note | Inspection: John Holland - PE (H)
b05401c4-2370-5fb7-9a0c-20ac18d087d3 | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
3d6cbf6a-eea2-5f3a-8aff-b4874d9ef498 | textbox | Layer 1 time:
191d1bff-9ee8-5aec-bb86-59fe48e5125a | textbox | Layer 2 time:
736b99ac-2a26-42c6-b1bd-b4b70d698769 | signoff | AUTHORITY HOLDPOINT
92a7c8f9-fb03-42a7-9c0a-bf78b6ade0eb | checkpoint | 2.12 - Membrane test - Flood / Electronic Leak Detection / Seam Probe test the area in line with the AMS instruction
a70f3f04-456a-5d95-b94f-733e238a407a | note | Specification Reference - AS3740 cl 4.5.4 / GBA-SPE-AR-AS-0001
8d065204-2c24-5ff0-a5b0-c1deb9514b2f | note | Acceptance Criteria - Flood test - no leakage observed / measured over 24 hours Electronic Leak Detection Test - no points of electrical conduction identified Seam probe test - no seam failures reported
a7ecd370-c4dd-5b17-a9e8-59d1f0816617 | note | Test/ Inspection - Test
17de7e5c-8d1b-5ff3-8bde-ce9ee18d2101 | note | Test/Inspection Frequency - Each wet area
e6b70776-4c08-5d3d-9f41-60edfa017c71 | note | Inspection: Subcontractor - WS (I)
a1f6dff6-3a6d-56fc-a144-a92cea55a68a | note | Inspection: John Holland - PE (W)
48cece36-a294-5706-8e11-9458e20903a6 | note | Inspection: Site Manager - DC (W)
3a13f252-b449-54a9-8244-0b69df2b6bed | note | Records & Comments - Pass or Fail
71bc046e-5fa3-509c-9709-59b0f5a5b4c0 | textbox | Observed setting time:
a1fd0bd2-4591-40f4-9b62-d65fc189ca73 | checkpoint | 2.13 - 100% Witness Point: Supervise the follow-on Subcontractor(s) to ensure protection has been applied to membrane.
3b37c4b4-0303-5490-aca7-bfcf22a8b8f0 | note | Specification Reference - GBA-SPE-AR-AS-0001
be089706-55a9-535f-8844-99be51d8eec5 | note | Acceptance Criteria - Each layer applied in line with MAMS requirements - dressed into puddle flange
a9451b4f-d873-5258-a2b7-f767db6fd270 | note | Test/ Inspection - Installation and Inspection
666c3517-b86b-5788-94e5-13539fda90ec | note | Test/Inspection Frequency - Each wet area
8719a4bb-f238-5b31-8e97-b63ac11a8c55 | note | Inspection: Subcontractor - WS (W)
58b90d3b-ce92-5e50-9cfa-a40bd51e9268 | note | Inspection: John Holland - PE (I)
f0f3f7eb-1b9e-408f-8d21-07a6ae596c4e | section | 3 - Close-Out
3f7be114-21b5-4663-9804-7e96ec136e3c | checkpoint | 3.1 - ITP close-out.
39405c20-c8e1-5db9-9c97-9ec5a991f525 | note | Specification Reference - GBA-SPE-AR-AS-0001
64f109d6-c70d-5778-9e73-aa6ea73d3448 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
9cacd09a-dd10-533f-90e3-5d449a776bef | note | Test/Inspection Frequency - Each Lot
f8275ed9-c757-5104-866f-cbf5da065dd1 | note | Inspection: John Holland - QR (R)
522c366e-5e74-5b50-a198-895827cd4d13 | note | Records & Comments - Check all measurements are recorded and photos attached.
6dd754f2-e1cb-5317-932b-29ae8b5f331d | note | All records loaded into the Work Lot System and Verified.
47630c41-23fb-4306-852c-3d2e234cf82f | checklist | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-06 ROOF AREAS TORCH MEMBRANE BUILDING C Roof level |  | *Standard ITP - Aus Standards - Wet Area Waterproofing
9e5178fe-275d-4f66-a1d8-c2dfb2595b6e | section | 2 - Construction Inspections
9b42ef48-75ff-4fe0-b45f-d63fa7a00f94 | checkpoint | Inspection Details
99147e17-537f-5b03-9da6-e50edb4527ab | textbox | Level:
bd41c8d2-bfda-534c-808b-7f0e4dc584f0 | textbox | Zone:
2fcdccd6-ea1b-4aed-8a70-0e17ed1f631d | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
96201ade-dcca-5b3d-a6c5-a3ae93feee85 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
99c3f8df-eff4-5c8d-b2f4-6f1d29088d76 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter
ea421e94-008a-5c8d-8b8e-a7601f157c73 | textbox | Test/ Inspection - Measurement
f86ac474-28c1-5697-be6a-e58d9bc3daf5 | note | Test/Inspection Frequency - Each wet area, every 20m2
6cf3e71d-c2ee-5a5c-ba3b-674348252abf | note | Inspection: Subcontractor - WS (I)
4565c4c6-4d2d-5474-95ab-41343318208a | note | Inspection: John Holland - PE (S)
90e49087-aac7-40a7-9806-ef8e4a339d89 | checkpoint | 2.2 - Drainage installation - puddle flange installation
2f3646ab-f896-5188-8e2d-b9987d4aec3f | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
cc328293-f678-536a-a587-7d253099f364 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
bae9c3b4-910f-5f63-ab36-ad95261ee082 | note | Test/ Inspection - Installation and Inspection
fd6c5132-e6cc-555a-914b-f6b58b43ecaa | note | Test/Inspection Frequency - Each wet area
674d7feb-eba4-5a6d-b15f-ee634970b934 | note | Inspection: Subcontractor - HS (I)
b23f7f36-3ad2-559f-908a-4d2593e464cf | note | Inspection: John Holland - PE (S)
0ffe2ed6-0447-46cf-afed-d36722c5e0ad | checkpoint | 2.3 - Substrate condition Inspection
5d6d53e5-3aa6-551c-bf8f-18cdce1ad464 | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
afe4b9f4-3b64-5a38-830b-95b79c4d457a | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
a82dd030-d95a-5c07-b8db-bfc492829914 | note | Test/ Inspection - Inspection
ac9e23b1-27d4-5e1c-ad64-e3d2eca86ca5 | note | Test/Inspection Frequency - Each wet area
ee4390cb-133c-5109-9c57-606c7eefbaee | note | Inspection: Subcontractor - WS (I)
f35105ec-12af-5c69-be4b-b4cadbd65ca1 | note | Inspection: John Holland - PE (S)
1f992917-9d30-4dfa-a190-aeab456f663c | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
92c8c68d-6b09-5dab-a8fd-05b6d5d32c88 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
da5a0942-7821-5f26-95fa-208ff67a190b | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
98fefd0d-925e-5bac-bf98-551f884c2609 | note | Test/ Inspection - Measurement
faeff10b-75b3-56af-b2d7-c899a11a825a | note | Test/Inspection Frequency - Each wet area
6f9a24e5-1fdf-589a-a5e3-636478bf997b | note | Inspection: Subcontractor - WS (I)
2b56515e-cb5f-50af-9e8a-0cb87667a866 | note | Inspection: John Holland - PE (S)
b93e8744-eb60-43cc-b6f4-0ced895eba20 | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
9ff264ad-7b1a-5588-8be7-20ea17178676 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
6e64d360-6c59-544c-a28c-b65ff527bff4 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
27a16273-0284-5da2-824e-9d581be54185 | note | Test/ Inspection - Installation and Inspection
77554298-3ff6-5ad6-bb6a-e873adddcdec | note | Test/Inspection Frequency - Each wet area
e0d31f59-aadd-56f9-909f-ce37e131c572 | note | Inspection: Subcontractor - WS (I)
90b6b4f7-00c0-580c-ac34-731f05263758 | note | Inspection: John Holland - PE (S)
757c4c65-646f-502d-a7de-8f021f3fc7b2 | textbox | Records & Comments - Measured fall:
a780a240-67e7-4191-904f-7258db7dc85f | signoff | AUTHORITY HOLDPOINT
2666ef5e-cf95-460c-ac99-83ddac1acbb4 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
79bfe317-3b2f-546e-bc6b-f5dc7d568ad1 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
f12bc53a-6929-5f5d-84e0-5bab2f48354c | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
8e5b2e9b-f4b9-5abc-87e7-9d5e03dd8622 | note | Test/ Inspection - Measurement
f89588fc-de39-52e8-8a18-7360cded0ffd | note | Test/Inspection Frequency - Each wet area
c1eba538-3d18-5187-8321-0533f090efeb | note | Inspection: Subcontractor - WS (I)
5a9359f3-994b-5135-9d9e-797967732386 | note | Inspection: John Holland - PE (S)
2be213cf-2d02-4723-97b8-f1fc23d44fa6 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
f751970f-6540-57ba-b412-8d2b32672122 | note | Specification Reference - GBA-SPE-AR-AS-0001
ebb244f2-ead3-5244-a116-dc3ad39ceefc | note | Acceptance Criteria - Everything ready to install
7cb8199d-10a8-51f6-b690-5ef87bf733fc | note | Test/ Inspection - Review & Verify
6a20f454-0874-5024-9c2f-57d9a3f1245a | note | Test/Inspection Frequency - Each wet area
4e31e055-551a-58f9-bd57-e136d261e47a | note | Inspection: Subcontractor - WS (I)
14cd3ca7-96e7-5161-a412-6f72a6f22d46 | note | Inspection: John Holland - PE (S)
d85e862b-a381-5224-b140-93cbe102eb65 | textbox | Records & Comments - Temperature Reading:
87bd8b50-8a98-481b-b23c-4939fce47521 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
512f2459-4989-57fd-ad57-d2f7979cf269 | note | Specification Reference - GBA-SPE-AR-AS-0001
ea74eded-b5d6-567b-b59e-7c1908389fc6 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
8bd7ebce-35d3-52b4-ad24-7b42f2548933 | note | Test/ Inspection - Visual Inspection
774528bc-26dc-50f5-afdf-946a3f6af122 | note | Test/Inspection Frequency - Each wet area
8eea14f0-25c6-56af-bfcc-4fb7ee102f22 | note | Inspection: Subcontractor - WS (W)
740e9fd0-54a5-5b05-8024-575c846eb791 | note | Inspection: John Holland - PE (I)
3ac9bde7-c3a0-51bd-a189-f34c7eea56df | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
c33abc46-1121-5322-ab2c-9c844f12f708 | textbox | Applicator Names:
90be6c50-2004-5485-a669-bb1c01f39847 | textbox | Temperature at placement:
867b5da5-6264-4fe9-9a76-772e0570c9b9 | signoff | AUTHORITY HOLDPOINT
35aecec2-4bb0-4d64-abc9-b30cc23777fe | checkpoint | 2.9 - Apply Anti Rock Primer Primer in line with MAMS - take photograph of primer container with technical details and photo/video of application
5813fcff-c3fa-515d-8c3b-a671b0b2aaba | note | Specification Reference - GBA-SPE-AR-AS-0001
da34dfa3-7cf3-5726-b03e-3539abb3b1f4 | note | Acceptance Criteria - Anti Rock Primer applied
91fb654c-3331-5b92-bc67-2e75291e064b | note | Test/ Inspection - Installation and Inspection
ffbdfd99-9cb3-562b-9786-45557b0c82e4 | note | Test/Inspection Frequency - Each wet area
4d1763be-d098-52a7-b459-7feefd43f296 | note | Inspection: Subcontractor - WS (I)
d8f55d01-8993-5e8c-b7d1-c95c9dced01e | note | Inspection: John Holland - PE (W)
a97bf58e-a112-485f-bc71-1e7dcfd70208 | checkpoint | 2.10 - Apply membrane layers in line with data sheet and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
4727dca9-1b29-5144-9636-2e05a8c1bd9c | note | Specification Reference - GBA-SPE-AR-AS-0001
584bbd90-8cec-55f2-baa5-0778ecd41975 | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
d8f86bb1-b253-56bd-be67-05449cda4fab | note | Test/ Inspection - Installation and Inspection
d4a7e3d7-5260-5106-88e0-52374e408355 | note | Test/Inspection Frequency - Each wet area
39a1f77a-484d-532f-a8e1-420f334a61fa | note | Inspection: Subcontractor - WS (I)
3242926e-197d-572c-8ac5-c34263573b39 | note | Inspection: John Holland - PE (W)
5c3bce6d-2258-4ac0-bf9e-b2c25e9a7551 | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
409eb6fc-ba24-5b12-aef8-22282f640cae | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
6ba4f540-26b5-5a8b-b95e-7444a69dbafe | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
a3662691-c8f7-5906-9555-6e1be417e81a | note | Test/ Inspection - Installation and Inspection
42aebd7c-83be-5abf-8099-f271c2603b2e | note | Test/Inspection Frequency - Each wet area
bbc0a9e4-d3fb-5ad2-b79f-060bef2cb33d | note | Inspection: Subcontractor - WS (H)
40bfb9b5-2cfd-5fef-b5ae-5065c62bcca2 | note | Inspection: John Holland - PE (H)
b05401c4-2370-5fb7-9a0c-20ac18d087d3 | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
3d6cbf6a-eea2-5f3a-8aff-b4874d9ef498 | textbox | Layer 1 time:
191d1bff-9ee8-5aec-bb86-59fe48e5125a | textbox | Layer 2 time:
736b99ac-2a26-42c6-b1bd-b4b70d698769 | signoff | AUTHORITY HOLDPOINT
92a7c8f9-fb03-42a7-9c0a-bf78b6ade0eb | checkpoint | 2.12 - Membrane test - Flood / Electronic Leak Detection / Seam Probe test the area in line with the AMS instruction
a70f3f04-456a-5d95-b94f-733e238a407a | note | Specification Reference - AS3740 cl 4.5.4 / GBA-SPE-AR-AS-0001
8d065204-2c24-5ff0-a5b0-c1deb9514b2f | note | Acceptance Criteria - Flood test - no leakage observed / measured over 24 hours Electronic Leak Detection Test - no points of electrical conduction identified Seam probe test - no seam failures reported
a7ecd370-c4dd-5b17-a9e8-59d1f0816617 | note | Test/ Inspection - Test
17de7e5c-8d1b-5ff3-8bde-ce9ee18d2101 | note | Test/Inspection Frequency - Each wet area
e6b70776-4c08-5d3d-9f41-60edfa017c71 | note | Inspection: Subcontractor - WS (I)
a1f6dff6-3a6d-56fc-a144-a92cea55a68a | note | Inspection: John Holland - PE (W)
48cece36-a294-5706-8e11-9458e20903a6 | note | Inspection: Site Manager - DC (W)
3a13f252-b449-54a9-8244-0b69df2b6bed | note | Records & Comments - Pass or Fail
71bc046e-5fa3-509c-9709-59b0f5a5b4c0 | textbox | Observed setting time:
a1fd0bd2-4591-40f4-9b62-d65fc189ca73 | checkpoint | 2.13 - 100% Witness Point: Supervise the follow-on Subcontractor(s) to ensure protection has been applied to membrane.
3b37c4b4-0303-5490-aca7-bfcf22a8b8f0 | note | Specification Reference - GBA-SPE-AR-AS-0001
be089706-55a9-535f-8844-99be51d8eec5 | note | Acceptance Criteria - Each layer applied in line with MAMS requirements - dressed into puddle flange
a9451b4f-d873-5258-a2b7-f767db6fd270 | note | Test/ Inspection - Installation and Inspection
666c3517-b86b-5788-94e5-13539fda90ec | note | Test/Inspection Frequency - Each wet area
8719a4bb-f238-5b31-8e97-b63ac11a8c55 | note | Inspection: Subcontractor - WS (W)
58b90d3b-ce92-5e50-9cfa-a40bd51e9268 | note | Inspection: John Holland - PE (I)
f0f3f7eb-1b9e-408f-8d21-07a6ae596c4e | section | 3 - Close-Out
3f7be114-21b5-4663-9804-7e96ec136e3c | checkpoint | 3.1 - ITP close-out.
39405c20-c8e1-5db9-9c97-9ec5a991f525 | note | Specification Reference - GBA-SPE-AR-AS-0001
64f109d6-c70d-5778-9e73-aa6ea73d3448 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
9cacd09a-dd10-533f-90e3-5d449a776bef | note | Test/Inspection Frequency - Each Lot
f8275ed9-c757-5104-866f-cbf5da065dd1 | note | Inspection: John Holland - QR (R)
522c366e-5e74-5b50-a198-895827cd4d13 | note | Records & Comments - Check all measurements are recorded and photos attached.
6dd754f2-e1cb-5317-932b-29ae8b5f331d | note | All records loaded into the Work Lot System and Verified.
57d0067c-39ad-495f-86be-c4533504a332 | checklist | *Standard ITP - Aus Standards - Wet Area Waterproofing WP-09 TREMCO NEM COURTYARDS BUILDING F Level 3 |  | Standard ITP - Aus Standards - Wet Area Waterproofing WP-08 TREMCO VULKEM 350R/951NF BUILDING F Under Plinths
9e5178fe-275d-4f66-a1d8-c2dfb2595b6e | section | 2 - Construction Inspections
9b42ef48-75ff-4fe0-b45f-d63fa7a00f94 | checkpoint | Inspection Details
99147e17-537f-5b03-9da6-e50edb4527ab | textbox | Level:
bd41c8d2-bfda-534c-808b-7f0e4dc584f0 | textbox | Zone:
2fcdccd6-ea1b-4aed-8a70-0e17ed1f631d | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
96201ade-dcca-5b3d-a6c5-a3ae93feee85 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
99c3f8df-eff4-5c8d-b2f4-6f1d29088d76 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter
ea421e94-008a-5c8d-8b8e-a7601f157c73 | textbox | Test/ Inspection - Measurement
f86ac474-28c1-5697-be6a-e58d9bc3daf5 | note | Test/Inspection Frequency - Each wet area, every 20m2
6cf3e71d-c2ee-5a5c-ba3b-674348252abf | note | Inspection: Subcontractor - WS (I)
4565c4c6-4d2d-5474-95ab-41343318208a | note | Inspection: John Holland - PE (S)
90e49087-aac7-40a7-9806-ef8e4a339d89 | checkpoint | 2.2 - Drainage installation - puddle flange installation
2f3646ab-f896-5188-8e2d-b9987d4aec3f | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
cc328293-f678-536a-a587-7d253099f364 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
bae9c3b4-910f-5f63-ab36-ad95261ee082 | note | Test/ Inspection - Installation and Inspection
fd6c5132-e6cc-555a-914b-f6b58b43ecaa | note | Test/Inspection Frequency - Each wet area
674d7feb-eba4-5a6d-b15f-ee634970b934 | note | Inspection: Subcontractor - HS (I)
b23f7f36-3ad2-559f-908a-4d2593e464cf | note | Inspection: John Holland - PE (S)
0ffe2ed6-0447-46cf-afed-d36722c5e0ad | checkpoint | 2.3 - Substrate condition Inspection
5d6d53e5-3aa6-551c-bf8f-18cdce1ad464 | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
afe4b9f4-3b64-5a38-830b-95b79c4d457a | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
a82dd030-d95a-5c07-b8db-bfc492829914 | note | Test/ Inspection - Inspection
ac9e23b1-27d4-5e1c-ad64-e3d2eca86ca5 | note | Test/Inspection Frequency - Each wet area
ee4390cb-133c-5109-9c57-606c7eefbaee | note | Inspection: Subcontractor - WS (I)
f35105ec-12af-5c69-be4b-b4cadbd65ca1 | note | Inspection: John Holland - PE (S)
1f992917-9d30-4dfa-a190-aeab456f663c | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
92c8c68d-6b09-5dab-a8fd-05b6d5d32c88 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
da5a0942-7821-5f26-95fa-208ff67a190b | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
98fefd0d-925e-5bac-bf98-551f884c2609 | note | Test/ Inspection - Measurement
faeff10b-75b3-56af-b2d7-c899a11a825a | note | Test/Inspection Frequency - Each wet area
6f9a24e5-1fdf-589a-a5e3-636478bf997b | note | Inspection: Subcontractor - WS (I)
2b56515e-cb5f-50af-9e8a-0cb87667a866 | note | Inspection: John Holland - PE (S)
b93e8744-eb60-43cc-b6f4-0ced895eba20 | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
9ff264ad-7b1a-5588-8be7-20ea17178676 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
6e64d360-6c59-544c-a28c-b65ff527bff4 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
27a16273-0284-5da2-824e-9d581be54185 | note | Test/ Inspection - Installation and Inspection
77554298-3ff6-5ad6-bb6a-e873adddcdec | note | Test/Inspection Frequency - Each wet area
e0d31f59-aadd-56f9-909f-ce37e131c572 | note | Inspection: Subcontractor - WS (I)
90b6b4f7-00c0-580c-ac34-731f05263758 | note | Inspection: John Holland - PE (S)
757c4c65-646f-502d-a7de-8f021f3fc7b2 | textbox | Records & Comments - Measured fall:
a780a240-67e7-4191-904f-7258db7dc85f | signoff | AUTHORITY HOLDPOINT
2666ef5e-cf95-460c-ac99-83ddac1acbb4 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
79bfe317-3b2f-546e-bc6b-f5dc7d568ad1 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
f12bc53a-6929-5f5d-84e0-5bab2f48354c | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
8e5b2e9b-f4b9-5abc-87e7-9d5e03dd8622 | note | Test/ Inspection - Measurement
f89588fc-de39-52e8-8a18-7360cded0ffd | note | Test/Inspection Frequency - Each wet area
c1eba538-3d18-5187-8321-0533f090efeb | note | Inspection: Subcontractor - WS (I)
5a9359f3-994b-5135-9d9e-797967732386 | note | Inspection: John Holland - PE (S)
2be213cf-2d02-4723-97b8-f1fc23d44fa6 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
f751970f-6540-57ba-b412-8d2b32672122 | note | Specification Reference - GBA-SPE-AR-AS-0001
ebb244f2-ead3-5244-a116-dc3ad39ceefc | note | Acceptance Criteria - Everything ready to install
7cb8199d-10a8-51f6-b690-5ef87bf733fc | note | Test/ Inspection - Review & Verify
6a20f454-0874-5024-9c2f-57d9a3f1245a | note | Test/Inspection Frequency - Each wet area
4e31e055-551a-58f9-bd57-e136d261e47a | note | Inspection: Subcontractor - WS (I)
14cd3ca7-96e7-5161-a412-6f72a6f22d46 | note | Inspection: John Holland - PE (S)
d85e862b-a381-5224-b140-93cbe102eb65 | textbox | Records & Comments - Temperature Reading:
87bd8b50-8a98-481b-b23c-4939fce47521 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
512f2459-4989-57fd-ad57-d2f7979cf269 | note | Specification Reference - GBA-SPE-AR-AS-0001
ea74eded-b5d6-567b-b59e-7c1908389fc6 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
8bd7ebce-35d3-52b4-ad24-7b42f2548933 | note | Test/ Inspection - Visual Inspection
774528bc-26dc-50f5-afdf-946a3f6af122 | note | Test/Inspection Frequency - Each wet area
8eea14f0-25c6-56af-bfcc-4fb7ee102f22 | note | Inspection: Subcontractor - WS (W)
740e9fd0-54a5-5b05-8024-575c846eb791 | note | Inspection: John Holland - PE (I)
3ac9bde7-c3a0-51bd-a189-f34c7eea56df | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
c33abc46-1121-5322-ab2c-9c844f12f708 | textbox | Applicator Names:
90be6c50-2004-5485-a669-bb1c01f39847 | textbox | Temperature at placement:
867b5da5-6264-4fe9-9a76-772e0570c9b9 | signoff | AUTHORITY HOLDPOINT
35aecec2-4bb0-4d64-abc9-b30cc23777fe | checkpoint | 2.9 - Apply 171 PRIMER - take a photograph of the primer container with technical details and a photo/video of the application
5813fcff-c3fa-515d-8c3b-a671b0b2aaba | note | Specification Reference - GBA-SPE-AR-AS-0001
da34dfa3-7cf3-5726-b03e-3539abb3b1f4 | note | Acceptance Criteria - 171 Primer applied
91fb654c-3331-5b92-bc67-2e75291e064b | note | Test/ Inspection - Installation and Inspection
ffbdfd99-9cb3-562b-9786-45557b0c82e4 | note | Test/Inspection Frequency - Each wet area
4d1763be-d098-52a7-b459-7feefd43f296 | note | Inspection: Subcontractor - WS (I)
d8f55d01-8993-5e8c-b7d1-c95c9dced01e | note | Inspection: John Holland - PE (W)
a97bf58e-a112-485f-bc71-1e7dcfd70208 | checkpoint | 2.10 - Apply membrane layers in line with data sheet and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
4727dca9-1b29-5144-9636-2e05a8c1bd9c | note | Specification Reference - GBA-SPE-AR-AS-0001
584bbd90-8cec-55f2-baa5-0778ecd41975 | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
d8f86bb1-b253-56bd-be67-05449cda4fab | note | Test/ Inspection - Installation and Inspection
d4a7e3d7-5260-5106-88e0-52374e408355 | note | Test/Inspection Frequency - Each wet area
39a1f77a-484d-532f-a8e1-420f334a61fa | note | Inspection: Subcontractor - WS (I)
3242926e-197d-572c-8ac5-c34263573b39 | note | Inspection: John Holland - PE (W)
5c3bce6d-2258-4ac0-bf9e-b2c25e9a7551 | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
409eb6fc-ba24-5b12-aef8-22282f640cae | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
6ba4f540-26b5-5a8b-b95e-7444a69dbafe | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
cd0da64e-e738-5aa6-84fb-c4f108103c5d | note | Vulkem NEM Curing Times:
a6898c81-4514-598c-b5f6-14ec1a828ff1 | note | Full Cure time @23°C - 50%RH = 24hrs/coat
a3662691-c8f7-5906-9555-6e1be417e81a | note | Test/ Inspection - Installation and Inspection
42aebd7c-83be-5abf-8099-f271c2603b2e | note | Test/Inspection Frequency - Each wet area
bbc0a9e4-d3fb-5ad2-b79f-060bef2cb33d | note | Inspection: Subcontractor - WS (H)
40bfb9b5-2cfd-5fef-b5ae-5065c62bcca2 | note | Inspection: John Holland - PE (H)
b05401c4-2370-5fb7-9a0c-20ac18d087d3 | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
3d6cbf6a-eea2-5f3a-8aff-b4874d9ef498 | textbox | Layer 1 time:
191d1bff-9ee8-5aec-bb86-59fe48e5125a | textbox | Layer 2 time:
736b99ac-2a26-42c6-b1bd-b4b70d698769 | signoff | AUTHORITY HOLDPOINT
92a7c8f9-fb03-42a7-9c0a-bf78b6ade0eb | checkpoint | 2.12 - Membrane test - Flood / Electronic Leak Detection / Seam Probe test the area in line with the AMS instruction
a70f3f04-456a-5d95-b94f-733e238a407a | note | Specification Reference - AS3740 cl 4.5.4 / GBA-SPE-AR-AS-0001
8d065204-2c24-5ff0-a5b0-c1deb9514b2f | note | Acceptance Criteria - Flood test - no leakage observed / measured over 24 hours Electronic Leak Detection Test - no points of electrical conduction identified Seam probe test - no seam failures reported
a7ecd370-c4dd-5b17-a9e8-59d1f0816617 | note | Test/ Inspection - Test
17de7e5c-8d1b-5ff3-8bde-ce9ee18d2101 | note | Test/Inspection Frequency - Each wet area
e6b70776-4c08-5d3d-9f41-60edfa017c71 | note | Inspection: Subcontractor - WS (I)
a1f6dff6-3a6d-56fc-a144-a92cea55a68a | note | Inspection: John Holland - PE (W)
48cece36-a294-5706-8e11-9458e20903a6 | note | Inspection: Site Manager - DC (W)
3a13f252-b449-54a9-8244-0b69df2b6bed | note | Records & Comments - Pass or Fail
71bc046e-5fa3-509c-9709-59b0f5a5b4c0 | textbox | Observed setting time:
a1fd0bd2-4591-40f4-9b62-d65fc189ca73 | checkpoint | 2.13 - 100% Witness Point: Supervise the follow-on Subcontractor(s) to ensure protection has been applied to membrane.
3b37c4b4-0303-5490-aca7-bfcf22a8b8f0 | note | Specification Reference - GBA-SPE-AR-AS-0001
be089706-55a9-535f-8844-99be51d8eec5 | note | Acceptance Criteria - Each layer applied in line with MAMS requirements - dressed into puddle flange
a9451b4f-d873-5258-a2b7-f767db6fd270 | note | Test/ Inspection - Installation and Inspection
666c3517-b86b-5788-94e5-13539fda90ec | note | Test/Inspection Frequency - Each wet area
8719a4bb-f238-5b31-8e97-b63ac11a8c55 | note | Inspection: Subcontractor - WS (W)
58b90d3b-ce92-5e50-9cfa-a40bd51e9268 | note | Inspection: John Holland - PE (I)
f0f3f7eb-1b9e-408f-8d21-07a6ae596c4e | section | 3 - Close-Out
3f7be114-21b5-4663-9804-7e96ec136e3c | checkpoint | 3.1 - ITP close-out.
39405c20-c8e1-5db9-9c97-9ec5a991f525 | note | Specification Reference - GBA-SPE-AR-AS-0001
64f109d6-c70d-5778-9e73-aa6ea73d3448 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
9cacd09a-dd10-533f-90e3-5d449a776bef | note | Test/Inspection Frequency - Each Lot
f8275ed9-c757-5104-866f-cbf5da065dd1 | note | Inspection: John Holland - QR (R)
522c366e-5e74-5b50-a198-895827cd4d13 | note | Records & Comments - Check all measurements are recorded and photos attached.
6dd754f2-e1cb-5317-932b-29ae8b5f331d | note | All records loaded into the Work Lot System and Verified.
ce1f9535-7f88-597a-a26d-643c050ceb56 | checklist | Apply 2 coats Vulkem NEM 150mm upstands |  | Apply 2 coats Vulkem NEM 150mm upstands
98b56fea-114a-58f3-a001-2cc8e8022a53 | checkpoint | Apply 2 coats Vulkem NEM 150mm upstands
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
f61d2e52-4102-5004-b8d8-6e8dd1773d41 | checklist | Below ground tremco system |  | Below ground tremco system
554919a2-05ac-50f7-9e22-ad50b0c1c8f1 | checkpoint | Tremco Paraseal system installed.
f7b76478-5211-5b26-bfd4-da0aa675cb07 | checkpoint | Pressure strip install
e8ffd3ee-3116-5fb3-b659-42fd36f0a197 | checkpoint | Install Versidrain 8 geo
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
4d7dbcad-3628-4712-9968-30db9c9213eb | checklist | Car Park Sealer |  | Car Park Sealer
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
50040f5a-7b95-4685-893d-20ac4db7db8b | checkpoint | Check substrate – Ensure the surface is clean and free from all loose particles.
25df33ea-bcdd-490f-a4f5-8f430b96cc10 | checkpoint | Apply Deflecta Topel-O sealer to manufactures recommendations.
81375262-c4ad-5143-b1cc-08613835a9fe | checklist | Car Park Sealer - Old |  | Car Park Sealer
8da3452a-155b-529c-9971-f6cec6ac5c93 | checkpoint | Apply Carpark sealer P4 rating
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
3aaaa63c-4d39-5fd7-b11d-ad8912781f81 | checklist | Courtyards under paving |  | Courtyards under paving
9d0f23f8-2f36-5389-bec9-f4548b753c77 | checkpoint | Apply primer
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
72ad31aa-60d7-5ce5-a6b7-ae15032a21b3 | checklist | Coving |  | Coving
b8a7ed05-3c3a-551e-b5e9-4130eb1102ca | checkpoint | Install coving (40mm radius) vinyl flake 150mm high.
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
f3a21c64-2db4-5f12-9e78-b6873b121ea1 | checklist | Epoxy screeds to fall wet area setdowns |  | Epoxy screeds to fall wet area setdowns
ea16bccd-9816-514a-9bcc-231607084bf8 | checkpoint | Install screed to fall using Hychem GP epoxy/sand mortar.
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
a238c38b-1c2e-57e5-a486-6e0e825bdbf2 | checklist | Epoxy wall coating to ensuites 74 @ 23sqm per cell |  | Epoxy wall coating to ensuites 74 @ 23sqm per cell
fb4620cf-be78-53eb-81ed-4a5456a52a9b | checkpoint | Mechanical sand walls
c10ce5e2-8a5f-528a-97da-da999d5df847 | checkpoint | Prime with Hychem GP epoxy resin
aef9cdd0-fde3-54fe-a39f-02fa5754521e | checkpoint | Apply 2 coats Hychem SF 20v epoxy
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
5deb2211-0e6b-5abd-b1b5-9c3fa9ab60ba | checklist | FLGE 505.1 - Topel Sealer |  | FLGE 505.1 - Topel Sealer
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
3e70785c-fa0f-593e-9e0b-6c1ce3571e69 | checkpoint | Concrete moisture content check – measure moisture content of concrete substrate.
aa337151-3b03-5e81-b638-ddffd0269ebc | checkpoint | Substrate condition inspection.
6ecab2a7-f2b6-5180-8ead-3fef3eca28db | checkpoint | Apply clear sealer (Topel Sealer) in line with MAMS.
26d81c37-b444-5660-9362-73d06feff797 | checklist | FLGE 505.2 - Deckshield ID at 1.5mm |  | FLGE 505.2 - Deckshield ID at 1.5mm
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
3e70785c-fa0f-593e-9e0b-6c1ce3571e69 | checkpoint | Concrete moisture content check – measure moisture content of concrete substrate.
aa337151-3b03-5e81-b638-ddffd0269ebc | checkpoint | Substrate condition inspection.
8975616c-a239-5bd5-bf8b-fab41482d875 | checkpoint | Prime Flowprime in line with MAMS.
9c3dd750-00f4-58ec-bb25-3646ffcee637 | checkpoint | Apply seal coat (Flowcoat OP) in line with MAMS.
c08cb554-64bb-5a5c-b557-8c7afe7ec0ca | checkpoint | Apply topcoat (Deckshield UV) in line with MAMS.
a346e394-6d46-5147-a03f-8c9448d28a06 | checklist | FLGE 505.2 Deckshield ID 1.5mm |  | FLGE 505.2 Deckshield ID 1.5mm
8b7a5ccf-51f6-5945-a1e6-5ce36406c700 | checkpoint | Apply flowcrete flowprime and broadcast aggregate
56418b78-934e-56f2-9903-596ca87050a0 | checkpoint | Apply seal coat of Flowcoat OP
dafab438-7fcb-5b83-b651-34975db23a62 | checkpoint | Apply top coat of Deckshield UV
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
8d60f92a-742f-5298-ae28-ef163b222ac9 | checklist | FLGE 505.3 Dark grey Deckshield ID 2mm |  | FLGE 505.3 Dark grey Deckshield ID 2mm
0c8fed49-b534-50de-a9e1-9708fee3d22e | checkpoint | Apply 2 coats Flowprime and broadcast with aggregate
23db0ca5-bce9-5df9-b548-aabda063bc0d | checkpoint | Apply 1 coat Flowcoat OP
2a2cdef0-14e4-5e78-bd3d-ed8b256132d5 | checkpoint | Apply1 coat Deckshield UV
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
25c57f68-64c3-429b-90e5-e4c02aa34cc1 | checklist | FLGE.3 - Deckshield ID at 2mm |  | FLGE.3 - Deckshield ID at 2mm
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
3e70785c-fa0f-593e-9e0b-6c1ce3571e69 | checkpoint | Concrete moisture content check – measure moisture content of concrete substrate.
aa337151-3b03-5e81-b638-ddffd0269ebc | checkpoint | Substrate condition inspection.
8975616c-a239-5bd5-bf8b-fab41482d875 | checkpoint | Prime Flowprime in line with MAMS.
9c3dd750-00f4-58ec-bb25-3646ffcee637 | checkpoint | Apply seal coat (Flowcoat OP) in line with MAMS.
c08cb554-64bb-5a5c-b557-8c7afe7ec0ca | checkpoint | Apply topcoat (Deckshield UV) in line with MAMS.
56162ac6-aced-594c-a10e-eafe9325cb1f | checklist | ILD |  | ILD
cb704cbc-8ede-5d1e-be25-5c121808a75e | checkpoint | ILD testing
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
60b3bb54-507a-5e2d-9720-8220e169faf7 | checkpoint-no-value | International Leak Detection (ILD Australia) Sign Off Required
c3e1e1b4-7ff3-549a-bbd9-c18376a18563 | signoff | HOLDPOINT - Request Sign Off / Add Signature
58dd724d-7d9a-540b-b6f9-e41835e50f8e | checklist | L.L Roof plant |  | L.L Roof plant
fd37de27-0c85-51a5-a9c3-4ffaa9a28897 | checkpoint | Apply Tremproof 200EC primer
8d94564a-8c96-56a9-91ec-2641184ffc94 | checkpoint | Apply Vulkem 360 base coat
40c73498-ad52-5b8f-852b-cc77b838d2b4 | checkpoint | Apply 951 top coat 150mm upstands
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
627b9ddf-5518-5aa2-955b-e067fed3ea19 | checklist | Level 1 plant room/L.L roof plant room |  | Level 1 plant room/L.L roof plant room
63eccd4f-f2f7-509c-a425-80eaa142944b | checkpoint | Apply tremproof 200EC primer
8d94564a-8c96-56a9-91ec-2641184ffc94 | checkpoint | Apply Vulkem 360 base coat
3dcdf7e7-646d-5130-b6d7-3ab60d6aa3fb | checkpoint | Apply Vulkem 951 top coat
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
fcf7d473-a01c-58e8-b41e-ce1634e5d9d0 | checklist | Protection |  | Protection
64b59fd5-ec6a-55d8-b937-d3312cd4467a | checkpoint | Install protection to horizontal surfaces
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
3056e015-fe22-5612-86e8-02dc5299e8bd | checklist | Protection to BOH |  | Protection to BOH
64b59fd5-ec6a-55d8-b937-d3312cd4467a | checkpoint | Install protection to horizontal surfaces
1e0f3527-b90d-5fc9-b46d-92c148755e75 | checkpoint | Remove Protection
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
aeb287fc-a2d7-58e7-aed5-02fb20974a4c | checklist | Remove protection |  | Remove protection
bf318480-6ea6-5ae0-b0fd-50d6148598e7 | checkpoint | Remove protection
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
d057f40c-1733-5379-a921-adc28f0f407b | checklist | Roof Areas |  | Roof Areas
e304b3d7-29c5-5af3-ac45-f1cbc0548167 | checkpoint | Apply Primer
d64f5f92-3931-5445-b834-2f08909ffb96 | checkpoint | Apply base layer 3mm
5a527c44-7cbf-544c-9605-5392e37f033c | checkpoint | Apply top layer 4mm mineral finish
158138d7-4614-5951-bc9f-cedc37c31aa0 | checkpoint | Pressure strip termination at 150mm
cb704cbc-8ede-5d1e-be25-5c121808a75e | checkpoint | ILD testing
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
763a5323-f5d8-58a5-bd2a-5d10e54eb3dc | checklist | Sealing of Pour Joints |  | Sealing of Pour Joints
3a179d51-2ef1-5ea9-bb9c-67dda86f9c78 | checkpoint | Supply and install Enviro joint band
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
3283d164-cff2-5a99-8737-63d9eaa6fa90 | checklist | Stairs/BOH/Dryers |  | Stairs/BOH/Dryers
d00319d3-8d3f-560d-bfcf-3a755d9d5287 | checkpoint | Apply 2 coats Flowcoat OP light grey to 0.35 DFT
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
63c24bd7-e07b-5e5a-8a46-e1eeb3408d84 | checklist | Standard ITP - Aus Standards - Wet Area Waterproofing |  | Standard ITP - Aus Standards - Wet Area Waterproofing
9992b0db-f9e6-5134-b38b-5cadae36310b | section | 1 - Pre-Commencement Activities
849f6127-6124-55d8-8671-26929b00045f | checkpoint | Project Self-Assessment Tool- BU Project Audits -
ed40f965-2194-50ea-bc0c-bea35a52e0d3 | checkpoint | 1.1 - Submission of Waterproofing System products
6f093118-99a9-5bd3-af4e-b3b5a47e78d0 | note | Specification Reference - GBA-SPE-AR-AS-0001
4d9766db-1063-5d71-9ad0-6e4e154bd4f6 | note | Acceptance Criteria - Approval of Waterproofing System - confirmation of compatibility with substrate and follow-on trade requirements
c6a816de-92c9-5381-80c9-414e4c629cfb | note | Test/ Inspection - Review & Verify
8d7dea86-ecf1-5ed7-b916-d6fca59fb7ac | note | Test/Inspection Frequency - One-off prior to commencement
a3a27c52-bd38-5fd7-9dd6-d1000368ad92 | note | Inspection: Subcontractor - WS (I)
5735740d-7eb0-535b-9068-056260dd2d7e | note | Inspection: John Holland - PE (R)
5d76cd7a-c090-5799-8596-0c767316cde4 | note | Inspection: Nominated Authority - WC (R)
10ee727d-1d15-5c3e-b876-4f9c39a9bf00 | checkpoint | 1.2 - Submission of Waterproofing System Warranties
6ddf78af-9a17-5be2-8f1e-9b21ff299d4d | note | Specification Reference - GBA-SPE-AR-AS-0001
96f0c1ed-f9ae-534d-b719-8d5240becdc1 | note | Acceptance Criteria - Warranty is for required duration and relevant party
8220e93f-e774-5f04-b9dc-8f37f8dcbeaa | note | Test/ Inspection - Review & Verify
d16e5ea8-9c0c-5a64-ae7f-e4f4678983bf | note | Test/Inspection Frequency - One-off prior to commencement
12da7609-eb78-57e0-a616-a940926be7f4 | note | Inspection: Subcontractor - WS (I)
dc0f6f67-9242-525b-bcd9-ebe959c9e553 | note | Inspection: John Holland - PE (R)
a5015fd1-78b5-5a03-96ab-d88011d396c1 | note | Inspection: Nominated Authority - WC (R)
ec426ebd-b547-569d-b821-cddb253ab5cd | checkpoint | 1.3 - Submission of Manufacturer's Application Method Statement (MAMS)
60a74713-80a4-5fb4-ba5c-9faefdda0a99 | note | Specification Reference - GBA-SPE-AR-AS-0001
c0975b77-7816-57c8-84f4-a2a9d33b28b6 | note | Acceptance Criteria - Approval of MAMS by Waterproofing Consultant
d7a7b636-8b61-51a6-a72e-5f8f6bd38776 | note | Test/ Inspection - Review & Verify
9aea9d67-50b6-5e95-9cfd-8e185a1e809b | note | Test/Inspection Frequency - One-off prior to commencement
ea0c9c11-d0d5-53a8-a796-0cf2cdd1dee2 | note | Inspection: Subcontractor - WS (I)
8ffaa8d8-8205-5b64-8e5e-d58d663eaf14 | note | Inspection: John Holland - PE (R)
4be8152d-a93c-594e-9c27-9bed14ddf65e | note | Inspection: Nominated Authority - WC (R)
69988c17-4dd7-5ebd-8bc4-f23d3a90f59a | checkpoint | 1.4 - Submission of AMS and WRA Content - including Safety Data Sheets for chemicals
850fd7a0-7d3e-5168-ab85-76b1817b6808 | note | Specification Reference - GBA-SPE-AR-AS-0001
afcba0d4-95fd-5305-a1e3-c74b268a5b5d | note | Acceptance Criteria - Approval of AMSs and WRAs
0266f3a8-d8f8-5bb5-950d-e20cc625cf06 | note | Test/ Inspection - Review & Verify
c9768110-ff62-53f2-9b21-200ff9606f4d | note | Test/Inspection Frequency - One-off prior to commencement
0ce60546-80a5-5f4c-9ce2-17cd5efa62dd | note | Inspection: Subcontractor - WS (I)
eae0dddb-37a8-5377-8a1d-b1114220a070 | note | Inspection: John Holland - PE (R)
ad5fb686-1685-5c97-9394-341d36ff4e68 | note | Inspection: Nominated Authority - WC (R)
ece26ba9-1ea7-56a9-956b-ad62962f100d | checkpoint | 1.5 - Waterproofing company to demonstrate Competency of Applicators
a603c104-70d1-5b02-9445-2d404ad6d258 | note | Specification Reference - GBA-SPE-AR-AS-0001
fc3f48e3-38b1-5fd7-978f-c461fc7b446c | note | Acceptance Criteria - Competency scheme document, register of applicators
a52a7591-e7d2-5af6-aa36-8c25542339a8 | note | Test/ Inspection - Review & Verify
76e092bb-fc88-58d1-b5f6-b18361a5f879 | note | Test/Inspection Frequency - One-off prior to commencement
f1701295-a55d-53b4-8b0b-bdaa5451c582 | note | Inspection: Subcontractor - WS (I)
bec80d59-81bf-5f2b-92aa-fcd451acaaea | note | Inspection: John Holland - PE (R)
fb1a3c85-70ff-523c-81be-513f3e102853 | note | Inspection: Nominated Authority - WC (R)
699fa0a7-a281-5518-89b3-c0df28596e23 | checkpoint | 1.6 - Detailed design complete - including shop details
0971256f-83bc-595d-a60e-0e6d4bb3d4e7 | note | Specification Reference - GBA-SPE-AR-AS-0001
ae43b0bc-757f-56c3-8184-51702f6441d7 | note | Acceptance Criteria - Approval of shop drawings
80da7c98-4141-5ec1-8773-d8193592fe95 | note | Test/ Inspection - Review & Verify
78bfae7f-4a97-5b19-8fd5-0191f8e8570b | note | Test/Inspection Frequency - One-off prior to commencement
9f42db96-a1b7-5e32-bf7d-54d97a891771 | note | Inspection: Subcontractor - WS (I)
c105b2df-fcf3-5dff-8b48-26f717424701 | note | Inspection: John Holland - PE (R)
2f8041e9-da5b-58bc-b9c6-592026dd9e68 | note | Inspection: Nominated Authority - WC (R)
53a7bdb6-fb93-553b-94e1-8e396e00d47b | checkpoint | 1.7 - Testing equipment details - and calibration records (if electronic leak detection specified)
713dfe55-6176-585e-a799-48e6ec2b4e3e | note | Specification Reference - AS3740 App C3 / GBA-SPE-AR-AS-0001
40800fd4-39de-5d7e-9819-a475517f7e00 | note | Acceptance Criteria - In calibration
6053e470-3bfa-5988-b621-c96545245ca1 | note | Test/ Inspection - Review & Verify
d239e3db-f278-5666-bf84-7b6181e8b9ea | note | Test/Inspection Frequency - One-off prior to commencement
771052f6-4b2f-5a1a-ab20-d50d8b44bfc4 | note | Inspection: Subcontractor - WS (I)
80175da7-2490-5340-94b2-3d038f6df0e0 | note | Inspection: John Holland - PE (R)
3d2233e4-8ebd-5e1f-99d3-e9c83e424b0e | note | Inspection: Nominated Authority - WC (R)
9f6e9613-1231-505f-bc69-0e19bfd6be12 | checkpoint | 1.8 - First of Type Inspection -joint witness and sign-off on Prototype or First Install with membrane system representative (as below)
008998e3-6468-5ac5-9486-296b425efbaf | note | Specification Reference - GBA-SPE-AR-AS-0001
ffa05eab-2b3f-5dcc-84f8-3002df4bd2a6 | note | Acceptance Criteria - Joint acceptance of the First of Type and close-out of any agreed issues
5fcee83b-9e1d-5779-a2f6-3e957dbf4b18 | note | Test/ Inspection - Review & Verify
3802be7a-3ad1-55dc-aac7-57bfd39307cc | note | Test/Inspection Frequency - One-off prior to commencement
ebabfbc3-9716-5530-bbf8-1025bccdcf0a | note | Inspection: Subcontractor - WS (H)
99814c0b-4404-52b5-aaf0-9974aad71a8b | note | Inspection: John Holland - PE (H)
340f49f1-aaee-5c91-a08a-18ca6e63ab6c | note | Inspection: Nominated Authority - WC (H)
aca6a227-6ff1-57f3-83c6-a8957ecafa65 | signoff | AUTHORITY HOLDPOINT
97aa05c2-3251-5231-acfa-ce1ee219ad53 | section | 2 - Construction Inspections
7c23bd9c-feeb-5e31-aa53-dc9ce5e12145 | checkpoint | 2.1 - Install Concrete substrate and wall system
cfb3dd58-137e-5402-a270-5c7abc42941b | note | Specification Reference - AS3600 / GBA-SPE-AR-AS-0001
fd7b894b-d712-525b-bea6-d285454fe19e | note | Acceptance Criteria - Project specification criteria
0de9e403-5086-548b-af58-e028b864ab29 | note | Test/ Inspection - Installation and Inspection
0a0c8bc2-6c6f-5d4f-a59b-3eca7832ca97 | note | Test/Inspection Frequency - Each wet area
028c2920-b2a3-5f77-87aa-07ffcb4f42fe | note | Inspection: Subcontractor - SS (I)
1efa6ef6-ae85-5977-a0ac-0e779f14029b | note | Inspection: John Holland - PE (S)
2daf3233-41cc-557e-85cf-c045f6a968d0 | note | Records & Comments - Project Self-Assessment Tool- BU Project Audits
cffa65e0-383c-502c-a6d3-0708f33c8f9e | checkpoint | 2.2 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
85ca0317-6151-5315-9cec-cbae96ace255 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
55b825b7-085e-5127-ada0-edc57999f298 | note | Acceptance Criteria - Slabs require a relative humidity of less than 75%
acf9c02e-b2b6-5f9c-ae9e-83f21987c71d | note | Test/ Inspection - Measurement
77132e1e-89ff-5f68-8f38-937f4958fd24 | note | Test/Inspection Frequency - Each wet area
20e31e75-da79-59b3-be58-2b7cde5f3651 | note | Inspection: Subcontractor - WS (I)
181853b4-093e-5cca-95d7-8daa692db860 | note | Inspection: John Holland - PE (S)
e48f3e97-df76-531c-8771-59422ad1a493 | checkpoint | 2.3 - Drainage installation - puddle flange installation
3112353e-a6ca-5da5-b860-a4415a869725 | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
0ad56244-3e65-52b2-8ada-0bbb95cdc4b4 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
0f544c6d-9485-5786-a164-078f7e7a1782 | note | Test/ Inspection - Installation and Inspection
2b4aa9ba-7582-581a-a6e8-272dd336511c | note | Test/Inspection Frequency - Each wet area
6af08bfa-ec14-5532-84a1-ed0a2c8f7269 | note | Inspection: Subcontractor - HS (I)
31a579fe-3eee-5135-b3e2-e96f65f5eb42 | note | Inspection: John Holland - PE (S)
956a830d-4236-5c13-bdd4-f5ad8f72f115 | checkpoint | 2.4 - Substrate condition Inspection
e2fb6f54-07b0-5bd3-b2ab-5e4db4827b6f | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
a72912a7-015a-5792-bd91-09a47655deb1 | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
ec5102e3-ecbb-568f-8943-76be35c79e0e | note | Test/ Inspection - Inspection
f83fd6a1-2a6a-5bbd-a1e1-ae9cd956e8e4 | note | Test/Inspection Frequency - Each wet area
87084b74-70ff-5e80-92d8-0926a77605a4 | note | Inspection: Subcontractor - WS (I)
7547851b-1bc9-5027-be41-57e103c6c04f | note | Inspection: John Holland - PE (S)
b81b2628-297d-54a5-a234-ddecf667b6b3 | checkpoint | 2.5 - Substrate falls - measurement - note actual fall on checklist, take photos
481c01de-69da-54b8-9c70-696772ccd638 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
752de7b1-4dad-526b-a8a9-6f28f1bb5087 | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
3770c0e8-dbca-51c1-8b85-37000998c8a8 | note | Test/ Inspection - Measurement
68ad544f-5268-5e66-b1a7-de4f77e362d3 | note | Test/Inspection Frequency - Each wet area
14bb07ca-f0a2-5a6d-abef-67c3b94a38dd | note | Inspection: Subcontractor - WS (I)
afdca61b-f464-5b8f-9e0e-b73775a29f12 | note | Inspection: John Holland - PE (S)
372ecd93-b1d7-5275-bddd-f2495d6bf7fb | checkpoint | 2.6 - Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
d8d49e0c-d246-598c-80b3-01f0ab771509 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
0e67a143-e195-5b20-a533-770a718bdcac | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
5307c265-1201-5b8c-9e30-9bdf5c567273 | note | Test/ Inspection - Installation and Inspection
cf821021-1e77-57b0-b6b4-303b5a0ac8e1 | note | Test/Inspection Frequency - Each wet area
74f3680f-ca7b-56e4-b84d-6c1ae163cfb2 | note | Inspection: Subcontractor - WS (I)
090fe7bd-a6f0-5ffb-8e2f-3d11a71ffb4a | note | Inspection: John Holland - PE (S)
a8c980a6-2060-5065-ba91-943df2a9cbc6 | textbox | Records & Comments - Measured fall:
e2206457-d195-51bc-8f30-576a8c5c094e | checkpoint | 2.7 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
de04c6ef-df36-58c7-837c-a0b0b5fa2192 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
706806d3-6d77-55f2-abb9-abc200176bbc | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
2302b936-7e0c-549a-816c-c4376290817d | note | Test/ Inspection - Measurement
b261f3c3-056b-5194-8932-b28bdce88522 | note | Test/Inspection Frequency - Each wet area
650f98ad-a5f4-52ea-b869-f8a1d7eb4486 | note | Inspection: Subcontractor - WS (I)
8225e3d4-49df-5af8-b98a-6e428b17abe9 | note | Inspection: John Holland - PE (S)
353d1e55-ec47-5a35-aca3-b9f04188b786 | checkpoint | 2.8 - Subcontractor Pre-placement Check: Confirm equipment, personnel and temperature is acceptable for membrane installation - note equipment ref, name of applicators and temperature on checklist
96fcc4a2-d739-5893-aed1-ac97e8bf3679 | note | Specification Reference - GBA-SPE-AR-AS-0001
b6c6c891-383b-5918-8c2e-cd067ae56e07 | note | Acceptance Criteria - Everything ready to install
551b6088-222d-569e-81cc-122fcc647e86 | note | Test/ Inspection - Review & Verify
67cb20fb-4ad7-5cdd-b27c-f75f0f2d669c | note | Test/Inspection Frequency - Each wet area
55ecb822-0c48-5d41-bc76-0186c13828b0 | note | Inspection: Subcontractor - WS (I)
520b8986-5aee-5619-bc96-54977d132498 | note | Inspection: John Holland - PE (S)
fd244bd8-c64b-5bf2-abe9-1ff614bb86a2 | textbox | Records & Comments - Required size:
a9278808-c6fb-5029-a583-f71728c9301c | textbox | Measured size:
6ca4e179-a767-5262-bd17-e584a2c7364e | checkpoint | 2.9 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
0c5cd41a-adc3-526d-8475-07d8ddaa3985 | note | Specification Reference - GBA-SPE-AR-AS-0001
c0103be7-cef8-5a4f-a96d-6136cb89f195 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
9411cde0-97f2-5cef-8326-650477f83820 | note | Test/ Inspection - Visual Inspection
166b756d-004f-5681-a94d-96fde3c946b6 | note | Test/Inspection Frequency - Each wet area
9d0436c3-908e-57d8-b9ed-2267ff498d99 | note | Inspection: Subcontractor - WS (H)
8d43ec98-e0cb-5294-a9f2-f44ac650f0cf | note | Inspection: John Holland - PE (H)
58dfc272-4439-5736-b51b-2693b65e603e | textbox | Records & Comments - Applicator Names:
49577584-3669-51b8-8175-b361cd4d5d4a | textbox | Temperature at placement:
2dda1dbb-2c1a-5d24-8c5c-970c82795f57 | signoff | AUTHORITY HOLDPOINT
0750505e-99b5-51fc-9a05-f9b28f09de26 | checkpoint | 2.1 - 100% Witness Point: Watch the Subcontractor apply primer in line with MAMS - take photograph of primer container with technical details and photo/video of application
330bd17c-b8c6-5df7-a173-d80cbf867df9 | note | Specification Reference - GBA-SPE-AR-AS-0001
01c4d632-6715-51ce-87cd-2fc4e05523d1 | note | Acceptance Criteria - Correct primer applied
d41bc991-00ba-5157-a327-a9db09a5b2ae | note | Test/ Inspection - Installation and Inspection
300ce177-ab8a-5448-8924-33d39108056f | note | Test/Inspection Frequency - Each wet area
4ceb8057-87dc-5d75-b692-8a88617af2f5 | note | Inspection: Subcontractor - WS (I)
e773b966-2069-5983-9789-a156700907e1 | note | Inspection: John Holland - PE (W)
0eaea6c6-5603-5669-96aa-dcf20f0692cb | checkpoint | 2.11 - 100% Witness Point: Watch the Subcontractor apply membrane layers in line with MAMS and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
5b5df964-5e5a-54b0-acd9-5f29a63f1960 | note | Specification Reference - GBA-SPE-AR-AS-0001
71a0bce3-e460-5975-973c-47553276cfbd | note | Acceptance Criteria - Each layer applied in line with MAMS requirements, timing between layers in line with the MAMS
992c8bb7-aab1-5670-8b66-3c364cc17b56 | note | Test/ Inspection - Installation and Inspection
00b69f48-f357-5707-8943-e6c25abb7345 | note | Test/Inspection Frequency - Each wet area
22772c0e-e40c-599c-a85f-07a00c22d109 | note | Inspection: Subcontractor - WS (I)
bc537db5-8d7e-5e5b-ac9a-2e8caf7a0b74 | note | Inspection: John Holland - PE (W)
bc58b98f-5701-59dd-a34a-f2d5defcc1d1 | checkpoint | 2.12 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
ba3dba0c-10a6-50d4-adeb-590068469182 | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
0f4e498a-9d79-51eb-80bd-16d104a29fd1 | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
f34132aa-199e-5995-b820-6f3f0c3ed77e | note | Test/ Inspection - Installation and Inspection
6e852438-f48c-50e1-9e86-839474cc931b | note | Test/Inspection Frequency - Each wet area
de8ad2ce-003c-5e3b-9cf3-4365e5ed7fa8 | note | Inspection: Subcontractor - WS (H)
e86356a6-0b40-5549-bae3-b5d214af1154 | note | Inspection: John Holland - PE (H)
f284ba1f-3ca6-5055-afd3-c48f57e65780 | textbox | Records & Comments - Layer 1 time:
fa1af8e4-2411-59f9-b60b-d7bd4777739b | textbox | Layer 2 time:
4d27eccb-8b93-5095-86f8-6445e0091242 | signoff | AUTHORITY HOLDPOINT
19db4941-c873-5776-9748-8d88643656ff | checkpoint | 2.13 - Membrane compound setting time - note planned and actual setting time on checklist
6f9b6518-2ee7-559a-a3b8-5040ccd66ecb | note | Specification Reference - AS3740 cl 4.5.2 / GBA-SPE-AR-AS-0001
19e66bd9-86d0-52ca-8964-53ba27e06c65 | note | Test/ Inspection - Installation and Inspection
2b733462-0a7e-5956-a749-8b737ec2720f | note | Test/Inspection Frequency - Each wet area
87340120-e7c9-57a2-8393-ad4cb948ea19 | note | Inspection: Subcontractor - WS (I)
8a247427-88bb-59ab-92fb-289e8a5f6192 | note | Inspection: John Holland - PE (S)
05cdb90a-3775-5b6a-83d1-2f89b8550604 | checkpoint | 2.14 - HOLD POINT: Confirm that setting time for membrane has been complied with
806091a2-5c02-5463-b762-bf88537b3d8a | note | Specification Reference - AS3740 cl 4.5.2 / GBA-SPE-AR-AS-0001
43a8a105-6eb8-590c-abc7-f7e6382590ef | note | Test/ Inspection - Installation and Inspection
0ce81d9d-ce3e-5b27-b48a-6fde3bbd02ec | note | Test/Inspection Frequency - Each wet area
7c5e4942-ac19-52d5-878e-bf04d49fbb68 | note | Inspection: Subcontractor - WS (H)
860bd8dc-99c9-51c1-ad0f-4f8eb3dc28e2 | note | Inspection: John Holland - PE (H)
226c061e-6344-5dc5-acaa-c1f37497253c | textbox | Records & Comments - Planned setting time:
35b13cba-7383-5fd7-bdce-7fa1ac8b9c80 | signoff | AUTHORITY HOLDPOINT
c4699518-86d6-554a-87ca-3f02184683b8 | checkpoint | 2.15 - Membrane test - Flood / Electronic Leak Detection / Seam Probe test the area in line with the AMS instruction
92207366-3eaf-5d84-b52a-f74571274e66 | note | Specification Reference - AS3740 cl 4.5.4 / GBA-SPE-AR-AS-0001
e8217b37-78e1-54fd-a434-fd87718daf8d | note | Acceptance Criteria - Flood test - no leakage observed / measured over 24 hours Electronic Leak Detection Test - no points of electrical conduction identified Seam probe test - no seam failures reported
a05122d2-20e9-5449-b9dc-65c5b97f2af8 | note | Test/ Inspection - Test
bc649829-5c96-5d82-ba34-ad237e6094c6 | note | Test/Inspection Frequency - Each wet area
a90de1a7-f5fd-5fc3-8fb0-b42299f735bd | note | Inspection: Subcontractor - WS (I)
bea02841-3a11-51ef-8d17-297976dcb599 | note | Inspection: John Holland - PE (W)
1b042be0-18a7-5090-9536-2b3864198cc7 | note | Inspection: Nominated Authority - DC (W)
753659b0-ff7a-5daa-a88f-840029a2477b | textbox | Records & Comments - Observed setting time:
67f10b43-cb1a-5b91-a9a6-8444f0132d1b | checkpoint | 2.16 - 100% Witness Point: Supervise the follow-on Subcontractor(s) to ensure that they do not damage the membrane system.
f710e785-c6e6-58ef-9da1-33d658cad451 | note | Specification Reference - GBA-SPE-AR-AS-0001
2d6ab6c6-bb0c-53fa-9b6b-693159f04489 | note | Acceptance Criteria - Each layer applied in line with MAMS requirements - dressed into puddle flange
6c9087db-200f-50b5-a708-f7cf2d440ce0 | note | Test/ Inspection - Installation and Inspection
afd2192d-da1d-5ea6-a945-ff3a36822215 | note | Test/Inspection Frequency - Each wet area
43c1576e-4bf9-573b-98f3-fc15b56aed29 | note | Inspection: Subcontractor - WS (I)
8b53d9db-ec94-5315-b8aa-fdce58e9c541 | note | Inspection: John Holland - PE (W)
e8e789b2-7c3a-5c9f-8ac3-9a708a014fb9 | section | 3 - Close-Out
de02b7cc-2402-5a0c-9a91-005f9de3ce46 | checkpoint | 3.1 - ITP close-out.
3f231675-555e-5718-96a8-886a24d12e39 | note | Specification Reference - GBA-SPE-AR-AS-0001
cb596300-b4ac-567d-a927-caf3eac73b18 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
de6d3e28-b094-5cfd-b7e3-184dec4b9837 | note | Test/Inspection Frequency - Each Lot
fcd865b0-74b7-5f79-929c-149104a75e89 | note | Inspection: John Holland - QR (R)
35a0c847-eb1e-5865-a94f-fb840236e901 | note | Records & Comments - All records loaded into the Work Lot System and Verified.
c92161ca-e808-4d13-8f5a-cc209f702c3b | checklist | Standard ITP - Aus Standards - Wet Area Waterproofing WP-08 TREMCO VULKEM 350R/951NF |  | Standard ITP - Aus Standards - Wet Area Waterproofing WP-08 TREMCO VULKEM 350R/951NF BUILDING F Under Plinths
9e5178fe-275d-4f66-a1d8-c2dfb2595b6e | section | 2 - Construction Inspections
9b42ef48-75ff-4fe0-b45f-d63fa7a00f94 | checkpoint | Inspection Details
99147e17-537f-5b03-9da6-e50edb4527ab | textbox | Level:
bd41c8d2-bfda-534c-808b-7f0e4dc584f0 | textbox | Zone:
2fcdccd6-ea1b-4aed-8a70-0e17ed1f631d | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
96201ade-dcca-5b3d-a6c5-a3ae93feee85 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
99c3f8df-eff4-5c8d-b2f4-6f1d29088d76 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter [Vulkem 350R/951NF datasheet]
ea421e94-008a-5c8d-8b8e-a7601f157c73 | textbox | Test/ Inspection - Measurement
f86ac474-28c1-5697-be6a-e58d9bc3daf5 | note | Test/Inspection Frequency - Each wet area, every 20m2
6cf3e71d-c2ee-5a5c-ba3b-674348252abf | note | Inspection: Subcontractor - WS (I)
4565c4c6-4d2d-5474-95ab-41343318208a | note | Inspection: John Holland - PE (S)
90e49087-aac7-40a7-9806-ef8e4a339d89 | checkpoint | 2.2 - Drainage installation - puddle flange installation
2f3646ab-f896-5188-8e2d-b9987d4aec3f | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
cc328293-f678-536a-a587-7d253099f364 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
bae9c3b4-910f-5f63-ab36-ad95261ee082 | note | Test/ Inspection - Installation and Inspection
fd6c5132-e6cc-555a-914b-f6b58b43ecaa | note | Test/Inspection Frequency - Each wet area
674d7feb-eba4-5a6d-b15f-ee634970b934 | note | Inspection: Subcontractor - HS (I)
b23f7f36-3ad2-559f-908a-4d2593e464cf | note | Inspection: John Holland - PE (S)
0ffe2ed6-0447-46cf-afed-d36722c5e0ad | checkpoint | 2.3 - Substrate condition Inspection
5d6d53e5-3aa6-551c-bf8f-18cdce1ad464 | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
afe4b9f4-3b64-5a38-830b-95b79c4d457a | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
a82dd030-d95a-5c07-b8db-bfc492829914 | note | Test/ Inspection - Inspection
ac9e23b1-27d4-5e1c-ad64-e3d2eca86ca5 | note | Test/Inspection Frequency - Each wet area
ee4390cb-133c-5109-9c57-606c7eefbaee | note | Inspection: Subcontractor - WS (I)
f35105ec-12af-5c69-be4b-b4cadbd65ca1 | note | Inspection: John Holland - PE (S)
1f992917-9d30-4dfa-a190-aeab456f663c | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
92c8c68d-6b09-5dab-a8fd-05b6d5d32c88 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
da5a0942-7821-5f26-95fa-208ff67a190b | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
98fefd0d-925e-5bac-bf98-551f884c2609 | note | Test/ Inspection - Measurement
faeff10b-75b3-56af-b2d7-c899a11a825a | note | Test/Inspection Frequency - Each wet area
6f9a24e5-1fdf-589a-a5e3-636478bf997b | note | Inspection: Subcontractor - WS (I)
2b56515e-cb5f-50af-9e8a-0cb87667a866 | note | Inspection: John Holland - PE (S)
b93e8744-eb60-43cc-b6f4-0ced895eba20 | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
9ff264ad-7b1a-5588-8be7-20ea17178676 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
6e64d360-6c59-544c-a28c-b65ff527bff4 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
27a16273-0284-5da2-824e-9d581be54185 | note | Test/ Inspection - Installation and Inspection
77554298-3ff6-5ad6-bb6a-e873adddcdec | note | Test/Inspection Frequency - Each wet area
e0d31f59-aadd-56f9-909f-ce37e131c572 | note | Inspection: Subcontractor - WS (I)
90b6b4f7-00c0-580c-ac34-731f05263758 | note | Inspection: John Holland - PE (S)
757c4c65-646f-502d-a7de-8f021f3fc7b2 | textbox | Records & Comments - Measured fall:
a780a240-67e7-4191-904f-7258db7dc85f | signoff | AUTHORITY HOLDPOINT
2666ef5e-cf95-460c-ac99-83ddac1acbb4 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
79bfe317-3b2f-546e-bc6b-f5dc7d568ad1 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
f12bc53a-6929-5f5d-84e0-5bab2f48354c | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
8e5b2e9b-f4b9-5abc-87e7-9d5e03dd8622 | note | Test/ Inspection - Measurement
f89588fc-de39-52e8-8a18-7360cded0ffd | note | Test/Inspection Frequency - Each wet area
c1eba538-3d18-5187-8321-0533f090efeb | note | Inspection: Subcontractor - WS (I)
5a9359f3-994b-5135-9d9e-797967732386 | note | Inspection: John Holland - PE (S)
2be213cf-2d02-4723-97b8-f1fc23d44fa6 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
f751970f-6540-57ba-b412-8d2b32672122 | note | Specification Reference - GBA-SPE-AR-AS-0001
ebb244f2-ead3-5244-a116-dc3ad39ceefc | note | Acceptance Criteria - Everything ready to install
7cb8199d-10a8-51f6-b690-5ef87bf733fc | note | Test/ Inspection - Review & Verify
6a20f454-0874-5024-9c2f-57d9a3f1245a | note | Test/Inspection Frequency - Each wet area
4e31e055-551a-58f9-bd57-e136d261e47a | note | Inspection: Subcontractor - WS (I)
14cd3ca7-96e7-5161-a412-6f72a6f22d46 | note | Inspection: John Holland - PE (S)
d85e862b-a381-5224-b140-93cbe102eb65 | textbox | Records & Comments - Temperature Reading:
87bd8b50-8a98-481b-b23c-4939fce47521 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
512f2459-4989-57fd-ad57-d2f7979cf269 | note | Specification Reference - GBA-SPE-AR-AS-0001
ea74eded-b5d6-567b-b59e-7c1908389fc6 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
8bd7ebce-35d3-52b4-ad24-7b42f2548933 | note | Test/ Inspection - Visual Inspection
774528bc-26dc-50f5-afdf-946a3f6af122 | note | Test/Inspection Frequency - Each wet area
8eea14f0-25c6-56af-bfcc-4fb7ee102f22 | note | Inspection: Subcontractor - WS (W)
740e9fd0-54a5-5b05-8024-575c846eb791 | note | Inspection: John Holland - PE (I)
3ac9bde7-c3a0-51bd-a189-f34c7eea56df | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
c33abc46-1121-5322-ab2c-9c844f12f708 | textbox | Applicator Names:
90be6c50-2004-5485-a669-bb1c01f39847 | textbox | Temperature at placement:
867b5da5-6264-4fe9-9a76-772e0570c9b9 | signoff | AUTHORITY HOLDPOINT
35aecec2-4bb0-4d64-abc9-b30cc23777fe | checkpoint | 2.9 - Apply TREMProof Primer - take a photograph of the primer container with technical details and a photo/video of the application
5813fcff-c3fa-515d-8c3b-a671b0b2aaba | note | Specification Reference - GBA-SPE-AR-AS-0001
da34dfa3-7cf3-5726-b03e-3539abb3b1f4 | note | Acceptance Criteria - TREMProof Primer applied
91fb654c-3331-5b92-bc67-2e75291e064b | note | Test/ Inspection - Installation and Inspection
ffbdfd99-9cb3-562b-9786-45557b0c82e4 | note | Test/Inspection Frequency - Each wet area
4d1763be-d098-52a7-b459-7feefd43f296 | note | Inspection: Subcontractor - WS (I)
d8f55d01-8993-5e8c-b7d1-c95c9dced01e | note | Inspection: John Holland - PE (W)
a97bf58e-a112-485f-bc71-1e7dcfd70208 | checkpoint | 2.10 - Apply membrane layers in line with data sheet and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
4727dca9-1b29-5144-9636-2e05a8c1bd9c | note | Specification Reference - GBA-SPE-AR-AS-0001
584bbd90-8cec-55f2-baa5-0778ecd41975 | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
d8f86bb1-b253-56bd-be67-05449cda4fab | note | Test/ Inspection - Installation and Inspection
d4a7e3d7-5260-5106-88e0-52374e408355 | note | Test/Inspection Frequency - Each wet area
39a1f77a-484d-532f-a8e1-420f334a61fa | note | Inspection: Subcontractor - WS (I)
3242926e-197d-572c-8ac5-c34263573b39 | note | Inspection: John Holland - PE (W)
5c3bce6d-2258-4ac0-bf9e-b2c25e9a7551 | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
409eb6fc-ba24-5b12-aef8-22282f640cae | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
6ba4f540-26b5-5a8b-b95e-7444a69dbafe | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
9915773e-d4c5-5390-8fd3-0994e83b7b6d | note | TREMproof 90 curing times
e65ec7d0-d239-5e05-9a2d-82581ea78e41 | note | Full Cure time @23°C, 50%RH = 48 hrs
a3662691-c8f7-5906-9555-6e1be417e81a | note | Test/ Inspection - Installation and Inspection
42aebd7c-83be-5abf-8099-f271c2603b2e | note | Test/Inspection Frequency - Each wet area
bbc0a9e4-d3fb-5ad2-b79f-060bef2cb33d | note | Inspection: Subcontractor - WS (H)
40bfb9b5-2cfd-5fef-b5ae-5065c62bcca2 | note | Inspection: John Holland - PE (H)
b05401c4-2370-5fb7-9a0c-20ac18d087d3 | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
3d6cbf6a-eea2-5f3a-8aff-b4874d9ef498 | textbox | Layer 1 time:
191d1bff-9ee8-5aec-bb86-59fe48e5125a | textbox | Layer 2 time:
736b99ac-2a26-42c6-b1bd-b4b70d698769 | signoff | AUTHORITY HOLDPOINT
92a7c8f9-fb03-42a7-9c0a-bf78b6ade0eb | checkpoint | 2.12 - Membrane test - Flood / Electronic Leak Detection / Seam Probe test the area in line with the AMS instruction
a70f3f04-456a-5d95-b94f-733e238a407a | note | Specification Reference - AS3740 cl 4.5.4 / GBA-SPE-AR-AS-0001
8d065204-2c24-5ff0-a5b0-c1deb9514b2f | note | Acceptance Criteria - Flood test - no leakage observed / measured over 24 hours Electronic Leak Detection Test - no points of electrical conduction identified Seam probe test - no seam failures reported
a7ecd370-c4dd-5b17-a9e8-59d1f0816617 | note | Test/ Inspection - Test
17de7e5c-8d1b-5ff3-8bde-ce9ee18d2101 | note | Test/Inspection Frequency - Each wet area
e6b70776-4c08-5d3d-9f41-60edfa017c71 | note | Inspection: Subcontractor - WS (I)
a1f6dff6-3a6d-56fc-a144-a92cea55a68a | note | Inspection: John Holland - PE (W)
48cece36-a294-5706-8e11-9458e20903a6 | note | Inspection: Site Manager - DC (W)
3a13f252-b449-54a9-8244-0b69df2b6bed | note | Records & Comments - Pass or Fail
71bc046e-5fa3-509c-9709-59b0f5a5b4c0 | textbox | Observed setting time:
a1fd0bd2-4591-40f4-9b62-d65fc189ca73 | checkpoint | 2.13 - 100% Witness Point: Supervise the follow-on Subcontractor(s) to ensure protection has been applied to membrane.
3b37c4b4-0303-5490-aca7-bfcf22a8b8f0 | note | Specification Reference - GBA-SPE-AR-AS-0001
be089706-55a9-535f-8844-99be51d8eec5 | note | Acceptance Criteria - Each layer applied in line with MAMS requirements - dressed into puddle flange
a9451b4f-d873-5258-a2b7-f767db6fd270 | note | Test/ Inspection - Installation and Inspection
666c3517-b86b-5788-94e5-13539fda90ec | note | Test/Inspection Frequency - Each wet area
8719a4bb-f238-5b31-8e97-b63ac11a8c55 | note | Inspection: Subcontractor - WS (W)
58b90d3b-ce92-5e50-9cfa-a40bd51e9268 | note | Inspection: John Holland - PE (I)
f0f3f7eb-1b9e-408f-8d21-07a6ae596c4e | section | 3 - Close-Out
3f7be114-21b5-4663-9804-7e96ec136e3c | checkpoint | 3.1 - ITP close-out.
39405c20-c8e1-5db9-9c97-9ec5a991f525 | note | Specification Reference - GBA-SPE-AR-AS-0001
64f109d6-c70d-5778-9e73-aa6ea73d3448 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
9cacd09a-dd10-533f-90e3-5d449a776bef | note | Test/Inspection Frequency - Each Lot
f8275ed9-c757-5104-866f-cbf5da065dd1 | note | Inspection: John Holland - QR (R)
522c366e-5e74-5b50-a198-895827cd4d13 | note | Records & Comments - Check all measurements are recorded and photos attached.
6dd754f2-e1cb-5317-932b-29ae8b5f331d | note | All records loaded into the Work Lot System and Verified.
2900d8d0-1045-4b29-a3f2-488dcd8a7cba | checklist | Standard ITP - Aus Standards - Wet Area Waterproofing WP-08 TREMCO VULKEM 350R/951NF BUILDING F Under Plinths |  | Standard ITP - Aus Standards - Wet Area Waterproofing WP-08 TREMCO VULKEM 350R/951NF BUILDING F Under Plinths
9e5178fe-275d-4f66-a1d8-c2dfb2595b6e | section | 2 - Construction Inspections
9b42ef48-75ff-4fe0-b45f-d63fa7a00f94 | checkpoint | Inspection Details
99147e17-537f-5b03-9da6-e50edb4527ab | textbox | Level:
bd41c8d2-bfda-534c-808b-7f0e4dc584f0 | textbox | Zone:
2fcdccd6-ea1b-4aed-8a70-0e17ed1f631d | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
96201ade-dcca-5b3d-a6c5-a3ae93feee85 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
99c3f8df-eff4-5c8d-b2f4-6f1d29088d76 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter [Vulkem 350R/951NF datasheet]
ea421e94-008a-5c8d-8b8e-a7601f157c73 | textbox | Test/ Inspection - Measurement
f86ac474-28c1-5697-be6a-e58d9bc3daf5 | note | Test/Inspection Frequency - Each wet area, every 20m2
6cf3e71d-c2ee-5a5c-ba3b-674348252abf | note | Inspection: Subcontractor - WS (I)
4565c4c6-4d2d-5474-95ab-41343318208a | note | Inspection: John Holland - PE (S)
90e49087-aac7-40a7-9806-ef8e4a339d89 | checkpoint | 2.2 - Drainage installation - puddle flange installation
2f3646ab-f896-5188-8e2d-b9987d4aec3f | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
cc328293-f678-536a-a587-7d253099f364 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
bae9c3b4-910f-5f63-ab36-ad95261ee082 | note | Test/ Inspection - Installation and Inspection
fd6c5132-e6cc-555a-914b-f6b58b43ecaa | note | Test/Inspection Frequency - Each wet area
674d7feb-eba4-5a6d-b15f-ee634970b934 | note | Inspection: Subcontractor - HS (I)
b23f7f36-3ad2-559f-908a-4d2593e464cf | note | Inspection: John Holland - PE (S)
0ffe2ed6-0447-46cf-afed-d36722c5e0ad | checkpoint | 2.3 - Substrate condition Inspection
5d6d53e5-3aa6-551c-bf8f-18cdce1ad464 | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
afe4b9f4-3b64-5a38-830b-95b79c4d457a | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
a82dd030-d95a-5c07-b8db-bfc492829914 | note | Test/ Inspection - Inspection
ac9e23b1-27d4-5e1c-ad64-e3d2eca86ca5 | note | Test/Inspection Frequency - Each wet area
ee4390cb-133c-5109-9c57-606c7eefbaee | note | Inspection: Subcontractor - WS (I)
f35105ec-12af-5c69-be4b-b4cadbd65ca1 | note | Inspection: John Holland - PE (S)
1f992917-9d30-4dfa-a190-aeab456f663c | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
92c8c68d-6b09-5dab-a8fd-05b6d5d32c88 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
da5a0942-7821-5f26-95fa-208ff67a190b | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
98fefd0d-925e-5bac-bf98-551f884c2609 | note | Test/ Inspection - Measurement
faeff10b-75b3-56af-b2d7-c899a11a825a | note | Test/Inspection Frequency - Each wet area
6f9a24e5-1fdf-589a-a5e3-636478bf997b | note | Inspection: Subcontractor - WS (I)
2b56515e-cb5f-50af-9e8a-0cb87667a866 | note | Inspection: John Holland - PE (S)
b93e8744-eb60-43cc-b6f4-0ced895eba20 | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
9ff264ad-7b1a-5588-8be7-20ea17178676 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
6e64d360-6c59-544c-a28c-b65ff527bff4 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
27a16273-0284-5da2-824e-9d581be54185 | note | Test/ Inspection - Installation and Inspection
77554298-3ff6-5ad6-bb6a-e873adddcdec | note | Test/Inspection Frequency - Each wet area
e0d31f59-aadd-56f9-909f-ce37e131c572 | note | Inspection: Subcontractor - WS (I)
90b6b4f7-00c0-580c-ac34-731f05263758 | note | Inspection: John Holland - PE (S)
757c4c65-646f-502d-a7de-8f021f3fc7b2 | textbox | Records & Comments - Measured fall:
a780a240-67e7-4191-904f-7258db7dc85f | signoff | AUTHORITY HOLDPOINT
2666ef5e-cf95-460c-ac99-83ddac1acbb4 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
79bfe317-3b2f-546e-bc6b-f5dc7d568ad1 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
f12bc53a-6929-5f5d-84e0-5bab2f48354c | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
8e5b2e9b-f4b9-5abc-87e7-9d5e03dd8622 | note | Test/ Inspection - Measurement
f89588fc-de39-52e8-8a18-7360cded0ffd | note | Test/Inspection Frequency - Each wet area
c1eba538-3d18-5187-8321-0533f090efeb | note | Inspection: Subcontractor - WS (I)
5a9359f3-994b-5135-9d9e-797967732386 | note | Inspection: John Holland - PE (S)
2be213cf-2d02-4723-97b8-f1fc23d44fa6 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
f751970f-6540-57ba-b412-8d2b32672122 | note | Specification Reference - GBA-SPE-AR-AS-0001
ebb244f2-ead3-5244-a116-dc3ad39ceefc | note | Acceptance Criteria - Everything ready to install
7cb8199d-10a8-51f6-b690-5ef87bf733fc | note | Test/ Inspection - Review & Verify
6a20f454-0874-5024-9c2f-57d9a3f1245a | note | Test/Inspection Frequency - Each wet area
4e31e055-551a-58f9-bd57-e136d261e47a | note | Inspection: Subcontractor - WS (I)
14cd3ca7-96e7-5161-a412-6f72a6f22d46 | note | Inspection: John Holland - PE (S)
d85e862b-a381-5224-b140-93cbe102eb65 | textbox | Records & Comments - Temperature Reading:
87bd8b50-8a98-481b-b23c-4939fce47521 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
512f2459-4989-57fd-ad57-d2f7979cf269 | note | Specification Reference - GBA-SPE-AR-AS-0001
ea74eded-b5d6-567b-b59e-7c1908389fc6 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
8bd7ebce-35d3-52b4-ad24-7b42f2548933 | note | Test/ Inspection - Visual Inspection
774528bc-26dc-50f5-afdf-946a3f6af122 | note | Test/Inspection Frequency - Each wet area
8eea14f0-25c6-56af-bfcc-4fb7ee102f22 | note | Inspection: Subcontractor - WS (W)
740e9fd0-54a5-5b05-8024-575c846eb791 | note | Inspection: John Holland - PE (I)
3ac9bde7-c3a0-51bd-a189-f34c7eea56df | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
c33abc46-1121-5322-ab2c-9c844f12f708 | textbox | Applicator Names:
90be6c50-2004-5485-a669-bb1c01f39847 | textbox | Temperature at placement:
867b5da5-6264-4fe9-9a76-772e0570c9b9 | signoff | AUTHORITY HOLDPOINT
35aecec2-4bb0-4d64-abc9-b30cc23777fe | checkpoint | 2.9 - Apply Tremproof 200EC Primer in line with MAMS - take a photograph of the primer container with technical details and a photo/video of the application
5813fcff-c3fa-515d-8c3b-a671b0b2aaba | note | Specification Reference - GBA-SPE-AR-AS-0001
da34dfa3-7cf3-5726-b03e-3539abb3b1f4 | note | Acceptance Criteria - Anti Rock Primer applied
91fb654c-3331-5b92-bc67-2e75291e064b | note | Test/ Inspection - Installation and Inspection
ffbdfd99-9cb3-562b-9786-45557b0c82e4 | note | Test/Inspection Frequency - Each wet area
4d1763be-d098-52a7-b459-7feefd43f296 | note | Inspection: Subcontractor - WS (I)
d8f55d01-8993-5e8c-b7d1-c95c9dced01e | note | Inspection: John Holland - PE (W)
a97bf58e-a112-485f-bc71-1e7dcfd70208 | checkpoint | 2.10 - Apply membrane layers in line with data sheet and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
4727dca9-1b29-5144-9636-2e05a8c1bd9c | note | Specification Reference - GBA-SPE-AR-AS-0001
584bbd90-8cec-55f2-baa5-0778ecd41975 | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
d8f86bb1-b253-56bd-be67-05449cda4fab | note | Test/ Inspection - Installation and Inspection
d4a7e3d7-5260-5106-88e0-52374e408355 | note | Test/Inspection Frequency - Each wet area
39a1f77a-484d-532f-a8e1-420f334a61fa | note | Inspection: Subcontractor - WS (I)
3242926e-197d-572c-8ac5-c34263573b39 | note | Inspection: John Holland - PE (W)
5c3bce6d-2258-4ac0-bf9e-b2c25e9a7551 | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
409eb6fc-ba24-5b12-aef8-22282f640cae | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
6ba4f540-26b5-5a8b-b95e-7444a69dbafe | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
6aff068f-1423-54aa-beb2-79b14b0b2bf3 | note | 350R/951NF layer minimum curing/drying times:
85a8743a-52e9-5308-94d1-5d8c12801ec5 | note | 5C - 12C ¦¦ 24 - 72 Hours
340dad2e-64a5-5e23-b216-2a003f10450e | note | 12C - 18C ¦¦ 6 - 24 Hours
b772fa8a-9f15-54b6-a570-256123252786 | note | 18C - 29C ¦¦ 4 - 6 Hours
f1f60b17-6657-5d5a-9c9d-2c80b4049739 | note | 29C ¦¦ 4 Hours
a3662691-c8f7-5906-9555-6e1be417e81a | note | Test/ Inspection - Installation and Inspection
42aebd7c-83be-5abf-8099-f271c2603b2e | note | Test/Inspection Frequency - Each wet area
bbc0a9e4-d3fb-5ad2-b79f-060bef2cb33d | note | Inspection: Subcontractor - WS (H)
40bfb9b5-2cfd-5fef-b5ae-5065c62bcca2 | note | Inspection: John Holland - PE (H)
b05401c4-2370-5fb7-9a0c-20ac18d087d3 | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
3d6cbf6a-eea2-5f3a-8aff-b4874d9ef498 | textbox | Layer 1 time:
191d1bff-9ee8-5aec-bb86-59fe48e5125a | textbox | Layer 2 time:
736b99ac-2a26-42c6-b1bd-b4b70d698769 | signoff | AUTHORITY HOLDPOINT
92a7c8f9-fb03-42a7-9c0a-bf78b6ade0eb | checkpoint | 2.12 - Membrane test - Flood / Electronic Leak Detection / Seam Probe test the area in line with the AMS instruction
a70f3f04-456a-5d95-b94f-733e238a407a | note | Specification Reference - AS3740 cl 4.5.4 / GBA-SPE-AR-AS-0001
8d065204-2c24-5ff0-a5b0-c1deb9514b2f | note | Acceptance Criteria - Flood test - no leakage observed / measured over 24 hours Electronic Leak Detection Test - no points of electrical conduction identified Seam probe test - no seam failures reported
a7ecd370-c4dd-5b17-a9e8-59d1f0816617 | note | Test/ Inspection - Test
17de7e5c-8d1b-5ff3-8bde-ce9ee18d2101 | note | Test/Inspection Frequency - Each wet area
e6b70776-4c08-5d3d-9f41-60edfa017c71 | note | Inspection: Subcontractor - WS (I)
a1f6dff6-3a6d-56fc-a144-a92cea55a68a | note | Inspection: John Holland - PE (W)
48cece36-a294-5706-8e11-9458e20903a6 | note | Inspection: Site Manager - DC (W)
3a13f252-b449-54a9-8244-0b69df2b6bed | note | Records & Comments - Pass or Fail
71bc046e-5fa3-509c-9709-59b0f5a5b4c0 | textbox | Observed setting time:
a1fd0bd2-4591-40f4-9b62-d65fc189ca73 | checkpoint | 2.13 - 100% Witness Point: Supervise the follow-on Subcontractor(s) to ensure protection has been applied to membrane.
3b37c4b4-0303-5490-aca7-bfcf22a8b8f0 | note | Specification Reference - GBA-SPE-AR-AS-0001
be089706-55a9-535f-8844-99be51d8eec5 | note | Acceptance Criteria - Each layer applied in line with MAMS requirements - dressed into puddle flange
a9451b4f-d873-5258-a2b7-f767db6fd270 | note | Test/ Inspection - Installation and Inspection
666c3517-b86b-5788-94e5-13539fda90ec | note | Test/Inspection Frequency - Each wet area
8719a4bb-f238-5b31-8e97-b63ac11a8c55 | note | Inspection: Subcontractor - WS (W)
58b90d3b-ce92-5e50-9cfa-a40bd51e9268 | note | Inspection: John Holland - PE (I)
f0f3f7eb-1b9e-408f-8d21-07a6ae596c4e | section | 3 - Close-Out
3f7be114-21b5-4663-9804-7e96ec136e3c | checkpoint | 3.1 - ITP close-out.
39405c20-c8e1-5db9-9c97-9ec5a991f525 | note | Specification Reference - GBA-SPE-AR-AS-0001
64f109d6-c70d-5778-9e73-aa6ea73d3448 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
9cacd09a-dd10-533f-90e3-5d449a776bef | note | Test/Inspection Frequency - Each Lot
f8275ed9-c757-5104-866f-cbf5da065dd1 | note | Inspection: John Holland - QR (R)
522c366e-5e74-5b50-a198-895827cd4d13 | note | Records & Comments - Check all measurements are recorded and photos attached.
6dd754f2-e1cb-5317-932b-29ae8b5f331d | note | All records loaded into the Work Lot System and Verified.
a6a6c9ff-a9a0-57c0-8607-641a28133992 | checklist | Trims to ensuite doorways |  | Trims to ensuite doorways
a77366a4-34ea-5857-b93b-8ed281540597 | checkpoint | Supply and install trims to doorways
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
651d76b6-16c7-5db9-8466-9f604e32b27a | checklist | Under wet area screeds (50mm Set Downs) |  | Under wet area screeds (50mm Set Downs)
5a8425db-0301-546a-b456-37db56a5feb9 | checkpoint | Caulk to junctions
db6fa933-f93e-5846-99b8-fcc34b838f85 | checkpoint | Apply 2 coats Hyclad E
0763ed65-9afd-5a54-a405-622b6dfee3f7 | checkpoint | Return 150mm above screed
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
6282d6de-99b8-530b-8f94-c5c5c7019e92 | checklist | Vinyl flake epoxy system wet area setdowns |  | Vinyl flake epoxy system wet area setdowns
ad7e570b-5a48-5376-8a23-0d16f81156b3 | checkpoint | Prime screeds
a87c3c50-b678-5c7b-96f4-02fa2aca514c | checkpoint | Apply 2 coats Hychem SF20 epoxy
2e2adc51-e931-5b21-aeec-ddaed668eca6 | checkpoint | Apply vinyl flakes
45b35490-961e-53a4-9e03-672817301377 | checkpoint | Apply 2 coats Hychem PA sealer includes 150mm upstands
7f730e0e-4115-528c-b1aa-e5052addea7b | checkpoint-no-value | Danlaid Sign Off Required
f903e1a8-fd3a-5a8c-b0ff-69319a1bb8b2 | signoff | HOLDPOINT - Request Sign Off / Add Signature
8ac0feea-cebd-53fa-a314-8c00094a047b | checkpoint-no-value | John Holland Group Sign Off Required
9254e360-999a-528d-b654-568106632cba | signoff | HOLDPOINT - Request Sign Off / Add Signature
0c88c10f-0aef-4e8c-995c-db318fbf1640 | checklist | Ω (ALTERNATE) *Standard ITP - Aus Standards - Wet Area Waterproofing (WP-06 ROOF AREAS TORCH MEMBRANE BUILDING C&F) |  | *Standard ITP - Aus Standards - Wet Area Waterproofing
9e5178fe-275d-4f66-a1d8-c2dfb2595b6e | section | 2 - Construction Inspections
9b42ef48-75ff-4fe0-b45f-d63fa7a00f94 | checkpoint | Inspection Details
99147e17-537f-5b03-9da6-e50edb4527ab | textbox | Level:
bd41c8d2-bfda-534c-808b-7f0e4dc584f0 | textbox | Zone:
2fcdccd6-ea1b-4aed-8a70-0e17ed1f631d | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
96201ade-dcca-5b3d-a6c5-a3ae93feee85 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
99c3f8df-eff4-5c8d-b2f4-6f1d29088d76 | note | Acceptance Criteria - Moisture content in the concrete must be lower than 4.5% as measured using a Tramex CME Moisture Meter [Vulkem 350R/951NF datasheet]
ea421e94-008a-5c8d-8b8e-a7601f157c73 | textbox | Test/ Inspection - Measurement
f86ac474-28c1-5697-be6a-e58d9bc3daf5 | note | Test/Inspection Frequency - Each wet area, every 20m2
6cf3e71d-c2ee-5a5c-ba3b-674348252abf | note | Inspection: Subcontractor - WS (I)
4565c4c6-4d2d-5474-95ab-41343318208a | note | Inspection: John Holland - PE (S)
90e49087-aac7-40a7-9806-ef8e4a339d89 | checkpoint | 2.2 - Drainage installation - puddle flange installation
2f3646ab-f896-5188-8e2d-b9987d4aec3f | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
cc328293-f678-536a-a587-7d253099f364 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
bae9c3b4-910f-5f63-ab36-ad95261ee082 | note | Test/ Inspection - Installation and Inspection
fd6c5132-e6cc-555a-914b-f6b58b43ecaa | note | Test/Inspection Frequency - Each wet area
674d7feb-eba4-5a6d-b15f-ee634970b934 | note | Inspection: Subcontractor - HS (I)
b23f7f36-3ad2-559f-908a-4d2593e464cf | note | Inspection: John Holland - PE (S)
0ffe2ed6-0447-46cf-afed-d36722c5e0ad | checkpoint | 2.3 - Substrate condition Inspection
5d6d53e5-3aa6-551c-bf8f-18cdce1ad464 | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
afe4b9f4-3b64-5a38-830b-95b79c4d457a | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
a82dd030-d95a-5c07-b8db-bfc492829914 | note | Test/ Inspection - Inspection
ac9e23b1-27d4-5e1c-ad64-e3d2eca86ca5 | note | Test/Inspection Frequency - Each wet area
ee4390cb-133c-5109-9c57-606c7eefbaee | note | Inspection: Subcontractor - WS (I)
f35105ec-12af-5c69-be4b-b4cadbd65ca1 | note | Inspection: John Holland - PE (S)
1f992917-9d30-4dfa-a190-aeab456f663c | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
92c8c68d-6b09-5dab-a8fd-05b6d5d32c88 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
da5a0942-7821-5f26-95fa-208ff67a190b | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
98fefd0d-925e-5bac-bf98-551f884c2609 | note | Test/ Inspection - Measurement
faeff10b-75b3-56af-b2d7-c899a11a825a | note | Test/Inspection Frequency - Each wet area
6f9a24e5-1fdf-589a-a5e3-636478bf997b | note | Inspection: Subcontractor - WS (I)
2b56515e-cb5f-50af-9e8a-0cb87667a866 | note | Inspection: John Holland - PE (S)
b93e8744-eb60-43cc-b6f4-0ced895eba20 | checkpoint | 2.5 - HOLD POINT: Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
9ff264ad-7b1a-5588-8be7-20ea17178676 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
6e64d360-6c59-544c-a28c-b65ff527bff4 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
27a16273-0284-5da2-824e-9d581be54185 | note | Test/ Inspection - Installation and Inspection
77554298-3ff6-5ad6-bb6a-e873adddcdec | note | Test/Inspection Frequency - Each wet area
e0d31f59-aadd-56f9-909f-ce37e131c572 | note | Inspection: Subcontractor - WS (I)
90b6b4f7-00c0-580c-ac34-731f05263758 | note | Inspection: John Holland - PE (S)
757c4c65-646f-502d-a7de-8f021f3fc7b2 | textbox | Records & Comments - Measured fall:
a780a240-67e7-4191-904f-7258db7dc85f | signoff | AUTHORITY HOLDPOINT
2666ef5e-cf95-460c-ac99-83ddac1acbb4 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
79bfe317-3b2f-546e-bc6b-f5dc7d568ad1 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
f12bc53a-6929-5f5d-84e0-5bab2f48354c | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
8e5b2e9b-f4b9-5abc-87e7-9d5e03dd8622 | note | Test/ Inspection - Measurement
f89588fc-de39-52e8-8a18-7360cded0ffd | note | Test/Inspection Frequency - Each wet area
c1eba538-3d18-5187-8321-0533f090efeb | note | Inspection: Subcontractor - WS (I)
5a9359f3-994b-5135-9d9e-797967732386 | note | Inspection: John Holland - PE (S)
2be213cf-2d02-4723-97b8-f1fc23d44fa6 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
f751970f-6540-57ba-b412-8d2b32672122 | note | Specification Reference - GBA-SPE-AR-AS-0001
ebb244f2-ead3-5244-a116-dc3ad39ceefc | note | Acceptance Criteria - Everything ready to install
7cb8199d-10a8-51f6-b690-5ef87bf733fc | note | Test/ Inspection - Review & Verify
6a20f454-0874-5024-9c2f-57d9a3f1245a | note | Test/Inspection Frequency - Each wet area
4e31e055-551a-58f9-bd57-e136d261e47a | note | Inspection: Subcontractor - WS (I)
14cd3ca7-96e7-5161-a412-6f72a6f22d46 | note | Inspection: John Holland - PE (S)
d85e862b-a381-5224-b140-93cbe102eb65 | textbox | Records & Comments - Temperature Reading:
87bd8b50-8a98-481b-b23c-4939fce47521 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
512f2459-4989-57fd-ad57-d2f7979cf269 | note | Specification Reference - GBA-SPE-AR-AS-0001
ea74eded-b5d6-567b-b59e-7c1908389fc6 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
8bd7ebce-35d3-52b4-ad24-7b42f2548933 | note | Test/ Inspection - Visual Inspection
774528bc-26dc-50f5-afdf-946a3f6af122 | note | Test/Inspection Frequency - Each wet area
8eea14f0-25c6-56af-bfcc-4fb7ee102f22 | note | Inspection: Subcontractor - WS (W)
740e9fd0-54a5-5b05-8024-575c846eb791 | note | Inspection: John Holland - PE (I)
3ac9bde7-c3a0-51bd-a189-f34c7eea56df | note | Records & Comments - Do not apply sealant to a substate surface is below 10C or the surface temperature is above 40C.
c33abc46-1121-5322-ab2c-9c844f12f708 | textbox | Applicator Names:
90be6c50-2004-5485-a669-bb1c01f39847 | textbox | Temperature at placement:
867b5da5-6264-4fe9-9a76-772e0570c9b9 | signoff | AUTHORITY HOLDPOINT
35aecec2-4bb0-4d64-abc9-b30cc23777fe | checkpoint | 2.9 - Apply Anti Rock Primer Primer in line with MAMS - take photograph of primer container with technical details and photo/video of application
5813fcff-c3fa-515d-8c3b-a671b0b2aaba | note | Specification Reference - GBA-SPE-AR-AS-0001
da34dfa3-7cf3-5726-b03e-3539abb3b1f4 | note | Acceptance Criteria - Anti Rock Primer applied
91fb654c-3331-5b92-bc67-2e75291e064b | note | Test/ Inspection - Installation and Inspection
ffbdfd99-9cb3-562b-9786-45557b0c82e4 | note | Test/Inspection Frequency - Each wet area
4d1763be-d098-52a7-b459-7feefd43f296 | note | Inspection: Subcontractor - WS (I)
d8f55d01-8993-5e8c-b7d1-c95c9dced01e | note | Inspection: John Holland - PE (W)
a97bf58e-a112-485f-bc71-1e7dcfd70208 | checkpoint | 2.10 - Apply membrane layers in line with data sheet and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
4727dca9-1b29-5144-9636-2e05a8c1bd9c | note | Specification Reference - GBA-SPE-AR-AS-0001
584bbd90-8cec-55f2-baa5-0778ecd41975 | note | Acceptance Criteria - Each layer applied in line with data sheet requirements, timing between layers in line with the data sheet
d8f86bb1-b253-56bd-be67-05449cda4fab | note | Test/ Inspection - Installation and Inspection
d4a7e3d7-5260-5106-88e0-52374e408355 | note | Test/Inspection Frequency - Each wet area
39a1f77a-484d-532f-a8e1-420f334a61fa | note | Inspection: Subcontractor - WS (I)
3242926e-197d-572c-8ac5-c34263573b39 | note | Inspection: John Holland - PE (W)
5c3bce6d-2258-4ac0-bf9e-b2c25e9a7551 | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
409eb6fc-ba24-5b12-aef8-22282f640cae | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
6ba4f540-26b5-5a8b-b95e-7444a69dbafe | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
6aff068f-1423-54aa-beb2-79b14b0b2bf3 | note | 350R/951NF layer minimum curing/drying times:
85a8743a-52e9-5308-94d1-5d8c12801ec5 | note | 5C - 12C ¦¦ 24 - 72 Hours
340dad2e-64a5-5e23-b216-2a003f10450e | note | 12C - 18C ¦¦ 6 - 24 Hours
b772fa8a-9f15-54b6-a570-256123252786 | note | 18C - 29C ¦¦ 4 - 6 Hours
f1f60b17-6657-5d5a-9c9d-2c80b4049739 | note | 29C ¦¦ 4 Hours
a3662691-c8f7-5906-9555-6e1be417e81a | note | Test/ Inspection - Installation and Inspection
42aebd7c-83be-5abf-8099-f271c2603b2e | note | Test/Inspection Frequency - Each wet area
bbc0a9e4-d3fb-5ad2-b79f-060bef2cb33d | note | Inspection: Subcontractor - WS (H)
40bfb9b5-2cfd-5fef-b5ae-5065c62bcca2 | note | Inspection: John Holland - PE (H)
b05401c4-2370-5fb7-9a0c-20ac18d087d3 | note | Records & Comments - Pass or Fail. Record film thickness and vertical termination heights.
3d6cbf6a-eea2-5f3a-8aff-b4874d9ef498 | textbox | Layer 1 time:
191d1bff-9ee8-5aec-bb86-59fe48e5125a | textbox | Layer 2 time:
736b99ac-2a26-42c6-b1bd-b4b70d698769 | signoff | AUTHORITY HOLDPOINT
92a7c8f9-fb03-42a7-9c0a-bf78b6ade0eb | checkpoint | 2.12 - Membrane test - Flood / Electronic Leak Detection / Seam Probe test the area in line with the AMS instruction
a70f3f04-456a-5d95-b94f-733e238a407a | note | Specification Reference - AS3740 cl 4.5.4 / GBA-SPE-AR-AS-0001
8d065204-2c24-5ff0-a5b0-c1deb9514b2f | note | Acceptance Criteria - Flood test - no leakage observed / measured over 24 hours Electronic Leak Detection Test - no points of electrical conduction identified Seam probe test - no seam failures reported
a7ecd370-c4dd-5b17-a9e8-59d1f0816617 | note | Test/ Inspection - Test
17de7e5c-8d1b-5ff3-8bde-ce9ee18d2101 | note | Test/Inspection Frequency - Each wet area
e6b70776-4c08-5d3d-9f41-60edfa017c71 | note | Inspection: Subcontractor - WS (I)
a1f6dff6-3a6d-56fc-a144-a92cea55a68a | note | Inspection: John Holland - PE (W)
48cece36-a294-5706-8e11-9458e20903a6 | note | Inspection: Site Manager - DC (W)
3a13f252-b449-54a9-8244-0b69df2b6bed | note | Records & Comments - Pass or Fail
71bc046e-5fa3-509c-9709-59b0f5a5b4c0 | textbox | Observed setting time:
a1fd0bd2-4591-40f4-9b62-d65fc189ca73 | checkpoint | 2.13 - 100% Witness Point: Supervise the follow-on Subcontractor(s) to ensure protection has been applied to membrane.
3b37c4b4-0303-5490-aca7-bfcf22a8b8f0 | note | Specification Reference - GBA-SPE-AR-AS-0001
be089706-55a9-535f-8844-99be51d8eec5 | note | Acceptance Criteria - Each layer applied in line with MAMS requirements - dressed into puddle flange
a9451b4f-d873-5258-a2b7-f767db6fd270 | note | Test/ Inspection - Installation and Inspection
666c3517-b86b-5788-94e5-13539fda90ec | note | Test/Inspection Frequency - Each wet area
8719a4bb-f238-5b31-8e97-b63ac11a8c55 | note | Inspection: Subcontractor - WS (W)
58b90d3b-ce92-5e50-9cfa-a40bd51e9268 | note | Inspection: John Holland - PE (I)
f0f3f7eb-1b9e-408f-8d21-07a6ae596c4e | section | 3 - Close-Out
3f7be114-21b5-4663-9804-7e96ec136e3c | checkpoint | 3.1 - ITP close-out.
39405c20-c8e1-5db9-9c97-9ec5a991f525 | note | Specification Reference - GBA-SPE-AR-AS-0001
64f109d6-c70d-5778-9e73-aa6ea73d3448 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
9cacd09a-dd10-533f-90e3-5d449a776bef | note | Test/Inspection Frequency - Each Lot
f8275ed9-c757-5104-866f-cbf5da065dd1 | note | Inspection: John Holland - QR (R)
522c366e-5e74-5b50-a198-895827cd4d13 | note | Records & Comments - Check all measurements are recorded and photos attached.
6dd754f2-e1cb-5317-932b-29ae8b5f331d | note | All records loaded into the Work Lot System and Verified.
c3ea4640-7295-4996-abb0-d12577a26b21 | checklist | Ω (DEPRECATED) *Standard ITP - Aus Standards - Wet Area Waterproofing (version 0) |  | *Standard ITP - Aus Standards - Wet Area Waterproofing
9e5178fe-275d-4f66-a1d8-c2dfb2595b6e | section | 2 - Construction Inspections
2fcdccd6-ea1b-4aed-8a70-0e17ed1f631d | checkpoint | 2.1 - Concrete moisture content check - measure moisture content of concrete substrate - note details on checklist with photo of readout
96201ade-dcca-5b3d-a6c5-a3ae93feee85 | note | Specification Reference - ASTM F2170, AS3740 cl 4.4.3 / GBA-SPE-AR-AS-0001
99c3f8df-eff4-5c8d-b2f4-6f1d29088d76 | note | Acceptance Criteria - Slabs require a relative humidity of less than 75%
f4110f45-2faf-5ec5-a7c3-3eb9c3b5f7a3 | note | Test/ Inspection - Measurement
f86ac474-28c1-5697-be6a-e58d9bc3daf5 | note | Test/Inspection Frequency - Each wet area
6cf3e71d-c2ee-5a5c-ba3b-674348252abf | note | Inspection: Subcontractor - WS (I)
4565c4c6-4d2d-5474-95ab-41343318208a | note | Inspection: John Holland - PE (S)
90e49087-aac7-40a7-9806-ef8e4a339d89 | checkpoint | 2.2 - Drainage installation - puddle flange installation
2f3646ab-f896-5188-8e2d-b9987d4aec3f | note | Specification Reference - AS3740 fig 4.3.1 / GBA-SPE-AR-AS-0001
cc328293-f678-536a-a587-7d253099f364 | note | Acceptance Criteria - Installed rebated in substrate, undamaged, capped to prevent ingress of debris
bae9c3b4-910f-5f63-ab36-ad95261ee082 | note | Test/ Inspection - Installation and Inspection
fd6c5132-e6cc-555a-914b-f6b58b43ecaa | note | Test/Inspection Frequency - Each wet area
674d7feb-eba4-5a6d-b15f-ee634970b934 | note | Inspection: Subcontractor - HS (I)
b23f7f36-3ad2-559f-908a-4d2593e464cf | note | Inspection: John Holland - PE (S)
0ffe2ed6-0447-46cf-afed-d36722c5e0ad | checkpoint | 2.3 - Substrate condition Inspection
5d6d53e5-3aa6-551c-bf8f-18cdce1ad464 | note | Specification Reference - AS3740 cl 4.4.1, JHG ETN-00006 3.4 / GBA-SPE-AR-AS-0001
afe4b9f4-3b64-5a38-830b-95b79c4d457a | note | Acceptance Criteria - Clean and free of laitence/debris, holes patched
a82dd030-d95a-5c07-b8db-bfc492829914 | note | Test/ Inspection - Inspection
ac9e23b1-27d4-5e1c-ad64-e3d2eca86ca5 | note | Test/Inspection Frequency - Each wet area
ee4390cb-133c-5109-9c57-606c7eefbaee | note | Inspection: Subcontractor - WS (I)
f35105ec-12af-5c69-be4b-b4cadbd65ca1 | note | Inspection: John Holland - PE (S)
1f992917-9d30-4dfa-a190-aeab456f663c | checkpoint | 2.4 - Substrate falls - measurement - note actual fall on checklist, take photos
92c8c68d-6b09-5dab-a8fd-05b6d5d32c88 | note | Specification Reference - AS3740 cl 2.3.1 / 2.3.2
da5a0942-7821-5f26-95fa-208ff67a190b | note | Acceptance Criteria - Falls are to the drain - min 1:80 in shower area, otherwise 1:100
98fefd0d-925e-5bac-bf98-551f884c2609 | note | Test/ Inspection - Measurement
faeff10b-75b3-56af-b2d7-c899a11a825a | note | Test/Inspection Frequency - Each wet area
6f9a24e5-1fdf-589a-a5e3-636478bf997b | note | Inspection: Subcontractor - WS (I)
2b56515e-cb5f-50af-9e8a-0cb87667a866 | note | Inspection: John Holland - PE (S)
b93e8744-eb60-43cc-b6f4-0ced895eba20 | checkpoint | 2.5 - Waterbars installed to edge of shower area and at door openings, waterbars installed to in-wall tap and shower rose surrounds - attach photos of correct installation.
9ff264ad-7b1a-5588-8be7-20ea17178676 | note | Specification Reference - AS3740 4.5.3, 4.8, 4.9, 4.12 / GBA-SPE-AR-AS-0001
6e64d360-6c59-544c-a28c-b65ff527bff4 | note | Acceptance Criteria - Waterbars in line with approved shop drawings and AS3740 requirements.
27a16273-0284-5da2-824e-9d581be54185 | note | Test/ Inspection - Installation and Inspection
77554298-3ff6-5ad6-bb6a-e873adddcdec | note | Test/Inspection Frequency - Each wet area
e0d31f59-aadd-56f9-909f-ce37e131c572 | note | Inspection: Subcontractor - WS (I)
90b6b4f7-00c0-580c-ac34-731f05263758 | note | Inspection: John Holland - PE (S)
757c4c65-646f-502d-a7de-8f021f3fc7b2 | textbox | Records & Comments - Measured fall:
2666ef5e-cf95-460c-ac99-83ddac1acbb4 | checkpoint | 2.6 - Bond breaker/fillets for Class 1/2/3 membrane installed to wall/floor junctions - attach photos of correct size
79bfe317-3b2f-546e-bc6b-f5dc7d568ad1 | note | Specification Reference - AS3740 4.5.3, 4.10 / GBA-SPE-AR-AS-0001
f12bc53a-6929-5f5d-84e0-5bab2f48354c | note | Acceptance Criteria - Bond Breaker/fillet to XXXX size based on class of membrane
8e5b2e9b-f4b9-5abc-87e7-9d5e03dd8622 | note | Test/ Inspection - Measurement
f89588fc-de39-52e8-8a18-7360cded0ffd | note | Test/Inspection Frequency - Each wet area
c1eba538-3d18-5187-8321-0533f090efeb | note | Inspection: Subcontractor - WS (I)
5a9359f3-994b-5135-9d9e-797967732386 | note | Inspection: John Holland - PE (S)
2be213cf-2d02-4723-97b8-f1fc23d44fa6 | checkpoint | 2.7 - Subcontractor Pre-placement Check: Confirm temperature is acceptable for membrane installation
f751970f-6540-57ba-b412-8d2b32672122 | note | Specification Reference - GBA-SPE-AR-AS-0001
ebb244f2-ead3-5244-a116-dc3ad39ceefc | note | Acceptance Criteria - Everything ready to install
7cb8199d-10a8-51f6-b690-5ef87bf733fc | note | Test/ Inspection - Review & Verify
6a20f454-0874-5024-9c2f-57d9a3f1245a | note | Test/Inspection Frequency - Each wet area
4e31e055-551a-58f9-bd57-e136d261e47a | note | Inspection: Subcontractor - WS (I)
14cd3ca7-96e7-5161-a412-6f72a6f22d46 | note | Inspection: John Holland - PE (S)
d85e862b-a381-5224-b140-93cbe102eb65 | textbox | Records & Comments - Required size:
dcf63a24-7ea5-5360-8405-e0e5d683cef8 | textbox | Measured size:
87bd8b50-8a98-481b-b23c-4939fce47521 | checkpoint | 2.8 - HOLD POINT: Inspect substrate and confirm that steps above are complete and that membrane may be applied
512f2459-4989-57fd-ad57-d2f7979cf269 | note | Specification Reference - GBA-SPE-AR-AS-0001
ea74eded-b5d6-567b-b59e-7c1908389fc6 | note | Acceptance Criteria - Previous steps complete in line with the Australian Standards, specifications and ETN
8bd7ebce-35d3-52b4-ad24-7b42f2548933 | note | Test/ Inspection - Visual Inspection
774528bc-26dc-50f5-afdf-946a3f6af122 | note | Test/Inspection Frequency - Each wet area
8eea14f0-25c6-56af-bfcc-4fb7ee102f22 | note | Inspection: Subcontractor - WS (W)
740e9fd0-54a5-5b05-8024-575c846eb791 | note | Inspection: John Holland - PE (I)
c33abc46-1121-5322-ab2c-9c844f12f708 | textbox | Records & Comments - Applicator Names:
90be6c50-2004-5485-a669-bb1c01f39847 | textbox | Temperature at placement:
867b5da5-6264-4fe9-9a76-772e0570c9b9 | signoff | AUTHORITY HOLDPOINT
35aecec2-4bb0-4d64-abc9-b30cc23777fe | checkpoint | 2.9 - Apply primer in line with MAMS - take photograph of primer container with technical details and photo/video of application
5813fcff-c3fa-515d-8c3b-a671b0b2aaba | note | Specification Reference - GBA-SPE-AR-AS-0001
da34dfa3-7cf3-5726-b03e-3539abb3b1f4 | note | Acceptance Criteria - Correct primer applied
91fb654c-3331-5b92-bc67-2e75291e064b | note | Test/ Inspection - Installation and Inspection
ffbdfd99-9cb3-562b-9786-45557b0c82e4 | note | Test/Inspection Frequency - Each wet area
4d1763be-d098-52a7-b459-7feefd43f296 | note | Inspection: Subcontractor - WS (I)
d8f55d01-8993-5e8c-b7d1-c95c9dced01e | note | Inspection: John Holland - PE (W)
a97bf58e-a112-485f-bc71-1e7dcfd70208 | checkpoint | 2.10 - Apply membrane layers in line with MAMS and the figures in AS3740 - take photograph of membrane container with technical details and photo/video of application - note details of timing on checklist
4727dca9-1b29-5144-9636-2e05a8c1bd9c | note | Specification Reference - GBA-SPE-AR-AS-0001
584bbd90-8cec-55f2-baa5-0778ecd41975 | note | Acceptance Criteria - Each layer applied in line with MAMS requirements, timing between layers in line with the MAMS
d8f86bb1-b253-56bd-be67-05449cda4fab | note | Test/ Inspection - Installation and Inspection
d4a7e3d7-5260-5106-88e0-52374e408355 | note | Test/Inspection Frequency - Each wet area
39a1f77a-484d-532f-a8e1-420f334a61fa | note | Inspection: Subcontractor - WS (I)
3242926e-197d-572c-8ac5-c34263573b39 | note | Inspection: John Holland - PE (W)
5c3bce6d-2258-4ac0-bf9e-b2c25e9a7551 | checkpoint | 2.11 - HOLD POINT: - Inspection to confirm integrity of the membrane and completion of installation.
409eb6fc-ba24-5b12-aef8-22282f640cae | note | Specification Reference - AS3740 Figures, AS3740 cl 4.5.3, 4.6 / GBA-SPE-AR-AS-0001
6ba4f540-26b5-5a8b-b95e-7444a69dbafe | note | Acceptance Criteria - Continuity of the membrane, no installation defects such as pinholes, measure dry film thickness, confirm vertical termination heights and details in the standard
a3662691-c8f7-5906-9555-6e1be417e81a | note | Test/ Inspection - Installation and Inspection
42aebd7c-83be-5abf-8099-f271c2603b2e | note | Test/Inspection Frequency - Each wet area
bbc0a9e4-d3fb-5ad2-b79f-060bef2cb33d | note | Inspection: Subcontractor - WS (H)
40bfb9b5-2cfd-5fef-b5ae-5065c62bcca2 | note | Inspection: John Holland - PE (H)
3d6cbf6a-eea2-5f3a-8aff-b4874d9ef498 | textbox | Records & Comments - Layer 1 time:
191d1bff-9ee8-5aec-bb86-59fe48e5125a | textbox | Layer 2 time:
736b99ac-2a26-42c6-b1bd-b4b70d698769 | signoff | AUTHORITY HOLDPOINT
92a7c8f9-fb03-42a7-9c0a-bf78b6ade0eb | checkpoint | 2.12 - Membrane test - Flood / Electronic Leak Detection / Seam Probe test the area in line with the AMS instruction
a70f3f04-456a-5d95-b94f-733e238a407a | note | Specification Reference - AS3740 cl 4.5.4 / GBA-SPE-AR-AS-0001
8d065204-2c24-5ff0-a5b0-c1deb9514b2f | note | Acceptance Criteria - Flood test - no leakage observed / measured over 24 hours Electronic Leak Detection Test - no points of electrical conduction identified Seam probe test - no seam failures reported
a7ecd370-c4dd-5b17-a9e8-59d1f0816617 | note | Test/ Inspection - Test
17de7e5c-8d1b-5ff3-8bde-ce9ee18d2101 | note | Test/Inspection Frequency - Each wet area
e6b70776-4c08-5d3d-9f41-60edfa017c71 | note | Inspection: Subcontractor - WS (I)
a1f6dff6-3a6d-56fc-a144-a92cea55a68a | note | Inspection: John Holland - PE (W)
48cece36-a294-5706-8e11-9458e20903a6 | note | Inspection: Nominated Authority - DC (W)
71bc046e-5fa3-509c-9709-59b0f5a5b4c0 | textbox | Records & Comments - Observed setting time:
a1fd0bd2-4591-40f4-9b62-d65fc189ca73 | checkpoint | 2.13 - 100% Witness Point: Supervise the follow-on Subcontractor(s) to ensure protection has been applied to membrane.
3b37c4b4-0303-5490-aca7-bfcf22a8b8f0 | note | Specification Reference - GBA-SPE-AR-AS-0001
be089706-55a9-535f-8844-99be51d8eec5 | note | Acceptance Criteria - Each layer applied in line with MAMS requirements - dressed into puddle flange
a9451b4f-d873-5258-a2b7-f767db6fd270 | note | Test/ Inspection - Installation and Inspection
666c3517-b86b-5788-94e5-13539fda90ec | note | Test/Inspection Frequency - Each wet area
8719a4bb-f238-5b31-8e97-b63ac11a8c55 | note | Inspection: Subcontractor - WS (W)
58b90d3b-ce92-5e50-9cfa-a40bd51e9268 | note | Inspection: John Holland - PE (I)
f0f3f7eb-1b9e-408f-8d21-07a6ae596c4e | section | 3 - Close-Out
3f7be114-21b5-4663-9804-7e96ec136e3c | checkpoint | 3.1 - ITP close-out.
39405c20-c8e1-5db9-9c97-9ec5a991f525 | note | Specification Reference - GBA-SPE-AR-AS-0001
64f109d6-c70d-5778-9e73-aa6ea73d3448 | note | Acceptance Criteria - All prior items of this ITP have been complied with.
9cacd09a-dd10-533f-90e3-5d449a776bef | note | Test/Inspection Frequency - Each Lot
f8275ed9-c757-5104-866f-cbf5da065dd1 | note | Inspection: John Holland - QR (R)
6dd754f2-e1cb-5317-932b-29ae8b5f331d | note | Records & Comments - All records loaded into the Work Lot System and Verified.