## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
584c222e-715d-4605-a7e6-5bdca2cb3966 | checklist | Documentation |  | Documentation
85069665-8dec-4310-a73b-be066f7ec103 | checkpoint | Attach relevant documents
d5d60516-d0cd-4e06-8261-d9e17578125d | checklist | Inspection Test Plan |  | Inspection Test Plan
c26ad15a-bae8-4311-866f-19c46ec1fa77 | section | Set Out Penetrations
68ac672a-fe1e-4c09-9c06-5fc42304bee4 | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
c1de8d19-6114-4991-9b4d-b915b16a3574 | checkpoint | Penetrations and Fire Collars to be in accordance with specification as required for each fire compartment rating and for each fire rated element.
6a953c8e-264b-43d6-89f0-b4e85c63ccf3 | checkpoint | Ensure Fire Collars are installed as per manufacturer’s instructions. Tabs on cast in, collars to be exposed. Photos of collar and labelling referencing fire matrix if required
d9e85bb0-309d-471f-aa3a-b4a17f2fe1a7 | checkpoint | All works completed in accordance to specifications and drawings. All certificates completed and submitted
e055b3f1-5de7-5a77-b14e-b8d4b9dba068 | note | ITR 001
faaa7375-c676-4910-ad11-c8a1e19375e7 | section | In Ground Sewer Drainage
271ec311-3cf7-48b0-a35f-5da05b747eba | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
48088af1-ad9e-4096-a31e-a7152e98be47 | checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.2.2015
e7c87bc4-092f-452e-8232-67c96f068bf8 | checkpoint | All works to be set out as per approved IFC drawings. Works set out to IFC Drawings No.
d701b1f6-3b49-469e-8dde-f73780ef3c18 | checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
45f7df66-0eda-4166-a5ef-22b33024dce4 | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No
0cd27734-4a64-4123-a3c8-b5ea8fd91304 | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings
7a2fd3bf-6ffd-4411-a678-951560411009 | checkpoint | Inspection booked with VBA for in ground drainage. HP can sign off if inspector does not attend.
00109f50-474d-5647-944e-533963c4683a | note | ITR 002
b3b1c49f-0c5d-454e-83a6-06c5f11b0c66 | section | In Ground Storm Water Drainage
704a2d77-b274-4f49-99e4-acac5a891097 | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
0b42f2b5-9a85-4c19-9fba-9ccd67ae94ff | checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification and AS 3500
a4fbdf96-654f-432b-be2c-061b579a8cc4 | checkpoint | All works to be set out as per approved IFC drawings. Works set out to IFC Drawings No
de2b0717-0fd1-4fb2-892a-c694e67ba7be | checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
887de23e-8e21-4284-a278-9911ab9cb610 | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
1a8b8c37-3522-4fcd-945a-e298190a93a6 | checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted.
71a87459-597a-57a4-abf0-baaf2c91a6bf | note | ITR 003
cc0ffa3b-673f-4e21-b7f9-571601f9ee2e | section | In Ground Greasy Drainage
92be570c-d035-479c-88d0-e1b73515f460 | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
a0ba0e20-8b5e-4c53-aed4-bbbad9b1a349 | checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.2.2015
51d05fe0-8b70-4723-bc00-910611126c0c | checkpoint | All works to be set out as per approved IFC drawings. Works set out to IFC Drawings No.
738b07ed-a5d6-449b-864c-86bf39338aa9 | checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
e902c9ce-f44a-464a-aa89-5e29993a36e6 | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
fe3d1560-cfc8-43bf-b7d5-fddb3e1a3edf | checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
45830849-6653-5133-bf11-61495426d72f | note | ITR 004
b3338fbf-d60c-4089-aa0f-7ebfccfca769 | section | Fire Services
e2a9e409-9e8d-4b33-8aed-f562b6bb7fc9 | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
c2574080-1d73-4150-9058-5d97ee285192 | checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification
64b530a7-78d1-43ed-b244-007cd98d12a8 | checkpoint | All pipe work to be as per specifications and AS 2419 & AS 2441 or alternatively approved by CFA/MFB
6d8a6317-1fdf-408b-985a-c79ba54ec854 | checkpoint | All pipe work to be tested to 1700 kPA in accordance to specifications and requirements as per AS 2419 Hydrants & AS 2441 Hose Reels
1b71cf34-8fe7-4e2e-9e52-bc306ba52333 | checkpoint | Prior to handover system must be inspected & certified in accordance to drawings, code, specification, dispensation & 129 report and FER.
376d4eb3-7095-44e3-9866-c8f3a8f7788f | checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted.
217f0b3c-581e-5f84-8724-9c89f7b75be7 | note | ITR 005
f82e30de-7a78-446c-8768-e12cf5cd2827 | section | Suspended Sewer Drainage
f043c2a8-af27-49d0-90ef-0b81c7556213 | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
3988e51b-f623-427a-8fe4-658b195e7f55 | checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.2.2015
0a0032bd-1059-4ba1-895a-d1401c9d2b9a | checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
51ebc37c-d17f-4c0e-8c0d-5b992e8330df | checkpoint | Ensure acoustic lagging is installed if required to specification and acoustic engineers report
b30ef3b5-f9b1-4918-ad01-28c19d16e5a3 | checkpoint | As per AS 3500 all traps have been tested for leaks by discharging water into drains
bd338207-c978-4570-84db-8c4560362145 | checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
10267728-26bd-5ef0-ae4a-bf7005eaa22d | note | ITR 006
65b51085-4a8d-487e-adcf-7da8195a9a5d | section | Suspended Stormwater
ced945a4-0273-49cc-ad55-04d838cb42ed | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
6d3fcd5f-4359-4eca-86a4-92e2409964ba | checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.2.2015
348e8192-d279-4ad7-8905-3a406b90a276 | checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
e3741ef0-87a1-4e19-bff8-2693717b9ca9 | checkpoint | All pipework to be checked for correct invert levels, gradients & clearance levels/head height in accordance with specifications and requirements
4524bd53-4efc-42cc-8b09-3cfb8d645c6f | checkpoint | Ensure acoustic lagging is installed if required to specification and acoustic engineers report
f2b34dff-8335-4f0e-bb0a-e3f288c208d3 | checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
2551add4-f627-54db-ad66-e712adf0f9dd | note | ITR 007
e6f89517-9817-4626-b470-b5c138e803d9 | section | Domestic Cold Water In
dee2e209-778d-40e6-b6f6-a7f30dc39a70 | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
8e9159fb-bcbc-445f-853e-26cf907d34fb | checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.2.2015
22e6f7f8-dc38-49d1-a610-0b86b269573c | checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
72def0ea-141b-47d6-b966-4e6fb4172fc6 | checkpoint | All pipework to be tested to 1500 kPA for 30 minutes as per AS 3500:1 clause 18.3.1 in accordance with specifications and requirements
f30ce2ef-a8b7-408a-b7d5-d7c71286d703 | checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
84e46076-9ad2-5b20-971d-d226394a584e | note | ITR 008
5ced379d-e885-4ed9-8d97-687d598fac80 | section | Gas Service
ab9168c6-8c0a-4c19-a67f-89829d1abbbf | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
a080eb24-bb9a-43f9-b020-2447f40d1110 | checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500
57941770-9b89-4868-8082-b3f25f637668 | checkpoint | All pipe work to be as per specifications and AS 3500 or alternatively approved including road sizes, clipping configurations and methods
126c2601-de49-48e5-acf9-c7702bd883c4 | checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
d9a79137-1421-4cdd-86e2-1153fc95d98d | checkpoint | Prior to gas being turned on ESV must be notified, inspection arrange and approval issued (if required). HP Management must be notified at the completion of works.
c53437c7-dd1c-542d-8fb6-5dd0453625c4 | note | ITR 009
bc3b7f27-7538-4334-a135-04dd838b3dea | section | Hot & Cold Water Rough In
85150026-0380-466b-8855-c6706c3c524f | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
9f6449e5-9a24-43a9-859e-3adf2e0f2931 | checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.1.2015 & AS 3500.4.2015 or alternatively approved.
019c4526-c811-48ec-9188-d1c48599c04e | checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
d49f7022-1fb2-4d7e-b255-b6101a52b200 | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
14774be0-9c82-4343-a5c4-77fa6eb7216f | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings
2a7923fe-39df-48a2-be8c-31ec4da34d06 | checkpoint | All pipework to be tested in accordance with specifications and requirements namely 1500 kPA for 30 minutes as per AS 3500:1 clause 18.1.3.
843e5d40-a72b-4dfe-9125-081df8d455d3 | checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted.
aa7a40b5-76a1-5934-ad35-d312455d6edf | note | ITR 010
f6e14cb2-b305-44e4-aa86-902bfe461c6a | section | Hot Water Service
e3d195f2-13ce-4cef-afb4-df3a8818f323 | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
5d60625f-772c-4411-b7d0-de1c9039c3f1 | checkpoint | Submit all samples HWS.. Ensure all materials are in accordance to specification AS 3500.1.2015 & AS 3500.4.2015 or alternatively approved
ce17283e-babb-4e88-b9a3-612559f36a9d | checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
de2567f8-d8f9-42a7-b759-769ad2ce475e | checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
083ed1ee-3360-5f0a-8771-11a8e825bf5e | note | ITR 011
9cfe0c79-c9a9-4c7b-af73-751a7f79e68f | section | Water Meter
7710e37b-6c00-46ed-8d2e-417069bde1b0 | checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
31058f50-1b35-4f61-9164-8bd5d3d3d557 | checkpoint | Submit all samples of materials. Ensure all materials are in accordance to specification AS 3500.1.2015 & AS 3500.4.2015 or alternatively approved
5915dfe1-4e57-4fba-9123-ac99dfae9802 | checkpoint | All works to be set up as per approved IFC Drawing No:
e101168d-fc6e-4ce0-b75c-90f5b6ababd0 | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings
d782df22-8778-4155-abea-45dd3b5fcf23 | checkpoint | All meter work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
2e746625-e36e-46aa-9029-9eb73a5d1f49 | checkpoint | Tested and Commissioning completed by passing an amount of known volume (bucket) and confirm the volume of water and meter reading are the same or within the required tolerances
2b59f46b-0b8c-5362-9f07-68133bf1b57a | note | ITR 012
5ae7e7ce-c3c2-4bfd-a936-af5e77a0c29a | section | Sanitary Fit Off
251062f6-1918-4b8f-bea3-fd65abde7924 | checkpoint | Submit all sanitary fixtures and tapware. Ensure all material is in accordance with specification AS 3500 and watermarked.
0c3dadcf-00ec-555e-9b5f-518b36528a77 | note | ITR 013
8cefb7b7-c419-4903-b821-eb4dc3942aed | section | Backflow Test Report
b634466e-5b28-47fd-8f68-d73eef1f2dff | checkpoint | Submit Backflow Test Report
27e23295-57e9-567e-96f7-90bfe1c6ce87 | note | ITR 014
c35dece3-9254-43ed-8e89-ff5c193f0cc3 | section | Tempering Valve Test Report
6395ac86-5fcd-4b26-8bb8-3ad1500a4294 | checkpoint | Submit Tempering Valve Test Report
967cf20e-f422-54e5-a036-639a8625eab8 | note | ITR 015
0fc3dfb9-569a-4533-b4a2-2173f61b2bc5 | section | Thermostatic Mixing Valve Test Report
d0500973-4c7c-4feb-852f-30da315cd323 | checkpoint | Submit Thermostatic Mixing Valve Test Report
b9d0ba5a-d49b-5b8f-b5ba-7f90df30cfb7 | note | ITR 016
06ac2a40-ecb5-4f7d-9b0a-6fcb2cc66491 | section | Third Party Commissioning
ea81c14d-c5bb-4dff-8b7b-8c0d1184db09 | checkpoint | Submit any Third Party Commissioning Reports which one are applicable:
c2f82e98-5791-55c8-acee-4f9f8f003a96 | note | Ie Pumps, Tanks, HWS, Fire Hydrants
4830fc85-8e0a-5eb2-8e81-8bcc040bd589 | note | Report from Third Party
20ad7385-e93f-48f7-83b5-9e79d1fd1f8f | checklist | Internal Audit Checklist |  | Internal Audit Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2ef162fd-803d-4d96-9a72-e20cf64d44c7 | checkpoint | Drawing Register Current
65b5e07a-bc7f-4adf-9221-6f5433e40bd9 | checkpoint | Drawings as per Register
ca227693-cc58-4264-9ddc-5e21058c41b2 | checkpoint | ITP Records
b41761c6-ddc9-4371-8816-48e1438b7ee1 | checkpoint | Material Specification
8e08e983-63d6-4f85-848f-957a7b175c2b | checkpoint | Sanitary Specification
4737b048-8f50-462a-b6ad-eff178ef89df | checkpoint | Calibration records
cfed4004-2282-4f09-ae57-7627722d9bc8 | checkpoint | Sample Register
47c5773b-9ddc-509a-882e-f2825f39f831 | textbox | Comments
e65e5915-5d21-51d8-b724-2eb4529ab4f0 | textbox | Items of concern
3096bde3-a91a-5bf5-800d-b9dbc150a250 | textbox | Action required
04dc0354-3ce9-5c72-909d-9b15f8a8355b | textbox | Future recommendations
953b81ec-d5e5-4164-8f09-7a7fbe460466 | checkpoint | Signed off by Highbury Plumbing Supervisor
9a8b429b-529c-41f9-b2ee-8b3d8b724faf | checklist | ITR 001 Set Out Penetrations |  | ITR 001 Set Out Penetrations
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
02f61807-249d-424f-b936-12bb8935ab65 | checkpoint | All works to be set our as per approved IFC drawings. Works set out to IFC Drawing No.
9a57519e-0db6-437a-ab85-7302de76e475 | checkpoint | All penetrations and fire collars to be as per specifications or alternatively approved
9c6cab9e-5945-47aa-b93c-0e4c6f9e7769 | checkpoint | All penetrations set out using total station or surveyed grid points by the builder
a44177ca-2a6d-4afb-b444-a557131b0a0c | checkpoint | Ensure fire collars are installed as per manufacturer’s instructions.
3a9ba3ae-e6c6-474a-9d08-b9ae1e7959a2 | checkpoint | Tabs on cast in collar to be exposed.
4ba569f3-9fe7-4943-a043-81061556ea91 | checkpoint | Photos of collar end labelling referencing fire matrix if required
5ae75880-d484-4e12-a126-3c2431c26dab | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
1de116f9-26ff-4f53-b078-d648a1d8d93a | checklist | ITR 002 Sewer Drainage |  | ITR 002 Sewer Drainage
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6b5e260d-6905-4774-a958-feadcda9f7df | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
7dc95c33-82df-4e94-aec5-41d05bde39b9 | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
51d08f74-52fc-4c94-81d4-7d97f89872fe | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
2c91b7df-d978-4a4a-ac0a-738855adae04 | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
7010dd55-e902-43c1-b606-bbe1a5f3d1a3 | checkpoint | Notify HP Management for inspection of drainage prior to backfill.
8d0df0d7-17a0-4e4a-8202-abd01e5ee72f | checkpoint | Book inspection with VBA for in-ground drainage. HP can sign off if inspector does not attend.
ecf4c99e-6dd4-43ba-8b35-fc7a1b88f7d0 | checkpoint | Ensure all backfill is in accordance to specifications & compaction requirements.
55760b63-baaf-4ebb-a01d-eee080967f77 | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
f1c46301-e19d-4112-8552-b0b70e78c108 | checklist | ITR 003 Stormwater Drainage In Ground |  | ITR 003 Stormwater Drainage In Ground
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
c2f8f46e-46ad-40e2-a2b0-02cd884432f0 | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
a42008a9-ced0-4c53-b0c5-34036474e8f5 | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
1bf86325-4c1e-4262-bb33-1932dadd137e | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
3e32055a-b162-414c-9deb-d72e0d162921 | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
4897f28f-65ff-4b41-83c6-75e07694383f | checkpoint | All pits to be checked for correct invert levels & finished floor levels in accordance to specifications & requirements & IFC drawings.
67877eb2-921b-4440-960b-667f158ca111 | checkpoint | Ensure correct locations of pits.
264e5bce-e1ad-4c2c-ad4e-91dc86285433 | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications & requirements
4ebb3c92-5d8b-4740-aea2-7ee34c0befb1 | checkpoint | Ensure all backfill is in accordance to specifications & compaction requirements.
76f69622-c803-4ae5-a810-1ecb106b31c2 | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
05d17b20-5287-4dd1-984e-c21dabdbd2d3 | checklist | ITR 004 Greasy Drainage In Ground |  | ITR 004 Greasy Drainage In Ground
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
28c10519-ca06-45cd-9604-f73ed04b7edb | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
14870e9b-179e-4080-aa90-8855028e4bc4 | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
44522820-8dc7-473b-8d24-a7e498a82f8f | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
31355e15-bcf0-497d-af1d-c18df1b26a4c | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
6e0aba7c-a1a6-4338-a18f-f0bf4586bfcf | checkpoint | Ensure all backfill is in accordance to specifications & compaction requirements.
7f1d28d2-080b-4235-889b-72d172fa9e51 | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
56a12893-87a8-4da6-8a5f-9190c82df774 | checklist | ITR 005 Fire Service |  | ITR 005 Fire Service
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
b972e361-d93b-4c9a-8a11-2f42213bdbbf | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
ead90449-766f-4b31-963b-a7e2757fd29c | checkpoint | All pipe work to be as per specifications & Standards or alternatively approved by CFA/MFB.
2145c5c6-b83b-42b2-a91b-6db714076caa | checkpoint | All pipework to be tested TO 1700 kPA in accordance to specifications &
244091ef-e621-4256-ace0-fc9aa10bc0ee | checkpoint | requirements as per AS 2419 Hydrants & AS 2441 Hose Reels
033df96b-6170-4ed7-ba10-f1fadab9a8fb | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
aeec6bb5-144f-4eec-aefb-167d1ac071b0 | checkpoint | Prior to handover system must be inspected & certified in accordance to drawings, code, specification, dispensation, 129 report and FER
271bc434-7b8f-4cd2-9365-838e98fa0c54 | checklist | ITR 006 Suspended Sewer Drainage |  | ITR 006 Suspended Sewer Drainage
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
396e017b-ed57-4106-be29-656918ed6a0b | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
a7b4501c-5c80-486b-a099-227667064c76 | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
9f5af564-4278-4cea-8a58-df4f8fe64796 | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
e4fcf139-b320-4433-a200-7bb37dfee589 | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
e3b2ac94-b2c6-4227-a06f-75018f6fb31c | checkpoint | Ensure acoustic lagging is installed if required to specification & acoustic engineers report.
2040d3c7-e4c2-4cbb-a654-6ec64fa0e431 | checkpoint | As per AS 3500 test traps for leaks by discharging water into drains
5b03d6f2-44ff-49dd-a129-693ddcaae745 | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
512d252d-52e5-4ef4-aaaf-88582ea90a2e | checklist | ITR 007 Suspended Storm Drainage |  | ITR 007 Suspended Storm Drainage
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7628d350-591f-4b0c-94fd-27f93db6a02e | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
ecc468b5-3b73-4215-93b5-7fc1e41b0724 | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
97579519-06ae-4144-b4a7-a59f650c3081 | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
777d541d-b607-48ea-b07f-a27154072091 | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
5612230e-2079-474d-bdbb-be49b347bfa1 | checkpoint | Ensure acoustic lagging is installed if required to specification & acoustic engineers report.
5cd78bd4-1bfc-4339-90ff-81e5305b4c43 | checkpoint | As per AS 3500 test traps for leaks by discharging water into drains
85ff0101-7643-45c6-bcec-ff79db7b6a5b | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
721072ee-6157-4146-83ca-890235c7205e | checklist | ITR 008 Suspended Greasy Drainage |  | ITR 008 Suspended Greasy Drainage
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
760234ae-6b1d-4b3d-8312-49ed6270401f | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
7a93984c-5cba-41e8-bd56-a3fd6da0cdea | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
fd8550bf-513a-4c38-b481-54ea40ffa877 | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
c5e8fbca-9717-4828-b27f-eea39cf848a5 | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
67dd591a-9589-40d8-9bf0-11638d9dc4b0 | checkpoint | Ensure acoustic lagging is installed if required to specification & acoustic engineers report.
5d228940-36d1-4c98-8303-df1f6c0d9200 | checkpoint | As per AS 3500 test traps for leaks by discharging water into drains
c2f021bb-5a56-4d43-b2e6-5c182e709370 | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
b08b000d-59cb-45af-817e-9cc33657b07c | checklist | ITR 009 Domestic Cold Water In Ground |  | ITR 009 Domestic Cold Water In Ground
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
08e04c9e-96bd-4823-9c02-6e80fa5f8e66 | checkpoint | All works to be set out as per approved IFC Drawings No.
a3524a4f-d35a-4818-98e0-4acbd17ebb4e | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
54ba2df2-018c-49ef-81a2-ad3ae616452d | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
974a691b-8548-4e2f-b52f-748ac667618d | checkpoint | All pipework to be tested to 1500 kPA for 30 minutes as per AS 3500:1 clause 18.3.1 & in accordance with specifications and requirements . Ensure isolation from authority main, fixtures, tapware and appliances while undertaking testing.
e8c5206f-071d-418e-8277-a9be87b0ddaa | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
120408de-1c53-49ca-98e7-455ae8db68a8 | checklist | ITR 010 Gas Service |  | ITR 010 Gas Service
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d2cfd0b1-58b1-48ba-a7ba-7842980c1a8b | checkpoint | All works to be set out as per approved IFC Drawings No.
c99a5b12-6edc-4729-93bd-67f6c2987b06 | checkpoint | All pipe work to be as per specifications & AS5601.1 or alternatively approved including rod sizes and clipping configurations and methods
416ac6e5-c33f-4fa4-aec2-2ecc224df990 | checkpoint | All pipework to be tested in accordance with specifications and requirements & AS5601.1
2b2f2e5c-699b-4c45-b6da-8eaef81b368b | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
1a02b650-368f-40e1-aaaa-68f24ad7abce | checkpoint | Prior to gas being turned on ESV must inspect and approved installation if required, including all builders work requirements IE signage, access panels, ventilation, riser shafts etc..
99c2d2ae-6e9d-4487-ba08-4e04d01ac196 | checkpoint | Must notify HP management on completion of works.
d8656dc4-16f6-490d-bb47-e93603b062ba | checklist | ITR 011 Hot & Cold Rough In |  | ITR 011 Hot & Cold Rough In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
5225424a-8f0f-464f-9d88-8bc01a867ba0 | checkpoint | All works to be set our as per approved IFC drawings and penetrations to be installed to - IFC Drawing No.
5af9b194-daf0-4eb5-a4ef-d34e87aed115 | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
d40b031a-246e-4e30-a997-2df1fabf43b3 | checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
65ad49f3-6e75-4ff1-b990-7ba54a4083e2 | checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
417b8297-2498-4385-b79f-934bb338740d | checkpoint | All pipework to be tested to 1500 kPA for 30 minutes as per AS 3500:1 clause 18.3.1 & in accordance with specifications and requirements . Ensure isolation from authority main, fixtures, tapware and appliances while undertaking testing
e0b54e5c-9b4f-4f71-902e-8bb32c0ff1b1 | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
d76e6a3a-de15-48e4-ba75-c20c666ba77d | checklist | ITR 012 Hot Water Service |  | ITR 012 Hot Water Service
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f78c5931-b06d-450e-bc4d-b82bee1a126e | checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
6ef0bef2-a353-4c2f-a64a-7f771af2d8a4 | checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
3b04446f-7951-471b-a39b-3b1a2e1b5701 | checkpoint | All pipework to be tested in accordance to specifications and requirements namely 1500 kPA for 30 minutes
5d567733-05c9-420b-99cd-ce207f6a3d05 | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
50bbca8d-6167-4306-9c05-48f8df0dc6ca | checklist | ITR 013 Water Meter |  | ITR 013 Water Meter
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
321a16ee-f65f-4b90-9953-0486d7d708e5 | checkpoint | All works to be set out as per approved IFC Drawing No:
29b12e3e-bfca-46ac-b818-42c8eb975400 | checkpoint | All meter work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
4f7d9d60-6b66-4f52-9ae1-4c7795bb6145 | checkpoint | Ensure that all pipework to meters has been sealed and jointed, all capping adequately installed for testing.
8d86a3f0-6030-451e-acc4-34a642b1c6a3 | checkpoint | Ensure all meters are sufficient supported and installed in correct location
d13469f9-194a-4594-a00b-6eb6894f2690 | checkpoint | Pass an amount of water in a container of known volume (bucket) and confirm the volume of water and meter reading are the same or within the required tolerances
64576934-8d01-4482-8e56-d4ea9e2121c2 | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
087364df-d36b-4f47-9df0-97357244bbb1 | checklist | ITR 014 Sanitary Fit Off |  | ITR 014 Sanitary Fit Off
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1acac113-653d-4f3a-b4be-aec1f9275024 | checkpoint | All works to be set our as per approved Architectural Drawing No.
6bc8b33c-23d9-4ab5-9daa-c736416949e6 | checkpoint | Inspect for product defects.
5273c88f-f6fd-44f4-9041-8649554940fd | checkpoint | Install as per manufacturer's recommendations and requirements
f1e43fdc-232b-4c0a-9f64-927a1e6699d9 | checkpoint | All sanitary items to be tested in accordance to specifications and manufacturers requirements
8a912355-1971-4398-81cc-d48711f481aa | checkpoint | Check for leaks
635c1503-6ae0-4f1d-b36f-2d67d3c4792d | checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
3f3a43a8-77b2-4078-89e1-8bdcf0ea31c5 | checklist | ITR 015 Backflow Test Report |  | ITR 015 Backflow Test Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
ad86dc4c-70c4-4acc-a3b6-60a922db1878 | checkpoint | Backflow Test Report Completed
f30933a9-93ce-5b1f-92dc-cf5a1dca7a3a | textbox | Date of test
b589fa5b-6138-5db2-aa03-33d3cbf4aec2 | textbox | Location of test
9d438310-1337-59c5-ad3f-8a79066025ac | textbox | Licence No.
812b2599-f8cd-562a-b419-a0cb53b118e8 | textbox | Test Kit Serial No.
1488112e-335a-5348-a852-2300b80c8259 | textbox | Date test kit last certified
27d8e580-c8aa-54d7-878e-1a891d3fe3cc | textbox | Place of certification
e9ac57f5-3a3e-5b97-9c2f-1929a0bff207 | textbox | Make of device
d801f682-a58a-5687-ab33-7b58e774b7bd | textbox | Size (mm)
bf92a0c8-7547-5446-b89e-b08bc982b1e6 | textbox | Model
8c0a7379-cdbb-5363-a28b-85907dbf6e73 | textbox | Serial No.
5885115d-5aab-5fb9-96f6-b65d16cce756 | note | Initial Test Before Maintenance
6b16ca70-27dc-403b-a6f7-199e18536160 | checkpoint | Permission to shut of water
02b57561-bab3-572d-8fa4-0eb171d853bf | tickbox | Reduced Pressure Zone Device
6ed416ee-c5bc-5581-b562-cafef01ca711 | tickbox | Double Check Valve (Columns 1 & 2)
3b566cd1-309b-5a87-91ac-d097138122a8 | tickbox | Pressure Type
d6c5a3ad-c624-4fd5-ae1b-cf634bc8358d | checkpoint | Check Valve No 1
b5dbd89f-7404-5218-ae97-fde01514eddd | tickbox | Closed Tight
de6aace8-aa2e-58dd-a484-93c93541712e | tickbox | Leaked
11d4e6a9-730a-5258-be41-bd1e940ec2b5 | textbox | kPa
c7a22dd8-33e5-4a0a-8c34-0403d23054ac | checkpoint | Check Valve No 2
0aeb4603-1673-5ed3-bcd8-d4c7526f3b34 | tickbox | Closed Tight
da4d6610-22b0-53f4-aa33-71bbc60c8001 | tickbox | Leaked
9000e8c3-b378-5c5f-a4ae-b2a4847136f7 | textbox | kPa
ede773a6-e319-4965-9c94-cad7e372985a | checkpoint | Relief Valve
59c2a0cf-ca02-5d7a-9fa1-ddbc25ff847b | tickbox | Opened At
9cb42e6c-84a1-503b-b0df-2d2e63deb7bb | tickbox | Not Opened
7aa99b89-7843-52a0-8281-28122e53bdad | textbox | kPa
e4ca5b1a-b006-482c-a679-d2bba91b80c7 | checkpoint | Check Valve
ab598f9e-bb08-53eb-9d5d-d22c44892bd5 | tickbox | Closed Tight
24905ac1-d234-591b-acfd-e78577c197e8 | tickbox | Leaked
7ffd9828-94c6-56aa-9f5b-699375c08d97 | textbox | kPa
3c46c572-96b0-4422-af5f-562a38e53a20 | checkpoint | Air Inlet
84db3ec0-9cfe-5db5-ba7c-e51d7b74928a | tickbox | Opened At
f6ef8362-b80a-5e17-af55-89198388b60b | tickbox | Not Opened
59a13866-0085-555b-b3b6-c58a3f44e774 | textbox | kPa
d041ff25-7edb-455e-9f65-efc499455609 | checkpoint | Downstream Isolation Valve
1e2f4e16-ae6d-58a3-8725-3c0a3bcd6bc2 | tickbox | Closed Tight
8c6eba38-2a87-567f-ab67-5480a7945fb9 | tickbox | Leaked
2d7dfd30-415c-5294-a185-b0171655eb58 | textbox | kPa
8211891f-248f-42aa-b750-69cce5faecbf | checkpoint | Comment / Take photos of any reasons for failure (NA if not required)
7406a13e-2615-5dd6-93f6-d634274e877f | note | Re-Test After
29b45d91-1cc9-46b1-9406-b5353ad1a361 | checkpoint | Permission to shut of water
b76d76d6-70b2-503b-a89c-941cd125ee5e | tickbox | Reduced Pressure Zone Device
5b44df74-90bc-5f91-9b96-e8832d1ae731 | tickbox | Double Check Valve (Columns 1 & 2)
0ff07e17-28de-5a69-ae72-712681b9e917 | tickbox | Pressure Type
a442fbc5-2050-4b75-ae1a-be81c69f4a4a | checkpoint | Check Valve No 1
6195fee5-4c9c-57ab-9e22-eed283f88f96 | tickbox | Closed Tight
abad12d3-5c6f-5d7e-a2b5-3a915e5e146c | tickbox | Leaked
c6744b2c-52b8-5985-ad14-85e29c473225 | textbox | kPa
e98fe7d5-fbd8-44ce-aa69-880ae5def384 | checkpoint | Check Valve No 2
ef9f776a-a30e-5618-92a2-1b9c7e5b1946 | tickbox | Closed Tight
2e6759f2-8b91-5c18-9fce-4d51663f76a3 | tickbox | Leaked
7102647c-6826-5a3c-a6d7-bc42f4e83bf3 | textbox | kPa
d957f0c2-ea4a-49ae-a248-af845b778c75 | checkpoint | Relief Valve
9c945143-88cf-5b05-b84d-a25188b4c515 | tickbox | Opened At
85f81215-49cd-578f-92e9-d76ed312ab8d | tickbox | Not Opened
80df27e6-c9f6-5c15-b93b-bef8fc3aaf4c | textbox | kPa
ae4e0021-ed57-4c91-bc36-aa5a6284ef5f | checkpoint | Check Valve
1085e101-fa69-57e6-a5fc-8fa95cb1c8c7 | tickbox | Closed Tight
719bc386-46d5-5e05-ba71-9a3fe6f38685 | tickbox | Leaked
3a811b36-db13-5fa2-939f-b64edecdc08d | textbox | kPa
6c37d5d3-7962-48c1-b217-e43742d0217e | checkpoint | Air Inlet
f1f798aa-417c-5308-875d-e2ab51553844 | tickbox | Opened At
c07744f1-e431-5c27-a3aa-7e38a4cfd6ec | tickbox | Not Opened
0eaadf48-724f-5fe1-b029-39ec0a01a96f | textbox | kPa
265ed133-d610-4f5e-a392-b583ec85fe31 | checkpoint | Downstream Isolation Valve
393ec373-aa4e-56bc-b44c-861101a2d45e | tickbox | Closed Tight
c451aafe-9b82-5d3d-b10f-8f60a368706c | tickbox | Leaked
fa3f5843-8319-5b54-a0d5-5f6326e9c9c5 | textbox | kPa
76c01f8e-c435-49b5-bdbf-77257f66e00c | checkpoint | Described Maintenance - Add comments / photos
a02abe06-0ae3-510f-8a51-84e851ee3ece | textbox | Parts & Materials Used
947452ab-e0e9-5565-aee9-db4fdb87f50c | textbox | Water Meter Number
d19b9a25-3d8b-4bdc-83f8-7e5fd0c4950a | checkpoint | Testing signed off
aeb87f6e-49b1-4905-8fa8-7bf808b24d4a | checklist | ITR 016 Tempering Valve Test Report |  | ITR 016 Tempering Valve Test Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
678ff626-a73a-4d66-9ee3-9fc662da198c | checkpoint | Tempering Valve Test
0910cbe4-2515-59f2-ad26-730c535207df | textbox | Licence No.
7a6453a2-bb67-5e98-9c07-3e688618667b | textbox | Test kit serial No.
c9af3bb3-0608-5677-b37b-1217f3e2ea34 | textbox | Date test kit last certified:
bbc0cb85-2907-5120-a137-cee5fdcf5880 | textbox | Place of certification
8bccb6aa-9fa8-5765-95cf-b53784682d11 | textbox | Make
9cd01560-2755-5304-89b1-8fe7c0d4ef16 | textbox | Model
401a4a7e-4e6f-5545-a7cd-78f83f119f96 | textbox | Location of valve
b2b534f3-362f-40f1-af27-89fca623e249 | checkpoint | Flush / Clean filters
3bb192fe-a060-41f6-afdd-1ed1a4f6c179 | checkpoint | One outlet in use
31ed8b31-7bdb-55e6-9964-75354f627399 | textbox | kPa
d9c4cc96-5631-4731-8fc0-7f37e5c32eb3 | checkpoint | Temp of warm water
b0611f8c-e88e-5c03-b61b-529d7b887caa | textbox | Fixture
30a8f141-057b-5268-a130-bfd38d1b25b8 | textbox | Pre Set Temp
c62cd819-7703-4d26-ba33-6d3f91bc00f8 | checkpoint | Described Maintenance - Add comments / photos
80db3ef8-7cfe-57da-8a29-7de1b8b16b76 | textbox | Parts & Materials Used
896b068a-0f29-4d36-a279-631141bda41c | checkpoint | Testing signed off
59a75fda-6c65-429c-867e-c43c40ec0311 | checklist | ITR 017 Thermostatic Mixing Valve Test Report |  | ITR 017 Thermostatic Mixing Valve Test Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
37112242-897a-4542-ae70-f215906aa2b1 | checkpoint | Thermostatic Mixing Valve Test
a1586769-edab-5c88-9949-6ec6ae233ec2 | textbox | Licence No.
030c93bc-4960-55e4-b344-c880cba8e2e5 | textbox | Test kit serial No.
b9ab4edf-978d-5b46-936e-9089dd432351 | textbox | Date test kit last certified:
38906542-762b-5c11-a0a9-110911a8f6bf | textbox | Place of certification
138c3858-e7ee-50d9-891d-96000f06ea9a | textbox | Make
9bfbea9f-7f1f-587c-bc3d-4600fba34fb8 | textbox | Model
bddacd79-7787-5080-8e48-1d66d4f78cd8 | textbox | Location of valve
edd0c4bd-b567-4e8d-8ba0-1e0969225246 | checkpoint | Shut down test
98c66c28-0afc-4a75-81f4-dba7c601997b | checkpoint | Flush / Clean filters
7291e257-158a-4836-af55-f42a235cf82e | checkpoint | Static Test
b473ab6b-155a-52bc-b711-cb5ceee932e6 | tickbox | One outlet in use
bf215f31-072f-5766-80cf-01f7e2641a7e | textbox | kPa
c84b8f9c-5033-4750-afe3-8c6852bf0e97 | checkpoint | Temp of warm water
d6e5f423-352a-5c7e-9232-caab46725ea2 | textbox | Fixture
27cfecd3-9f53-5c2e-b8c8-7925ff7b1f78 | textbox | Pre Set Temp
5cf95e2b-e95e-432e-b8b0-270e39e1edcc | checkpoint | Described Maintenance - Add comments / photos
b6122b30-c8c6-5084-9c61-a2b31ef5d509 | textbox | Parts & Materials Used
b68e2cfc-077d-4bd5-92a7-171e33379c94 | checkpoint | Testing signed off
47509044-add7-418a-8dbe-5ab9aee713b6 | checklist | Non Conformance Report |  | Non Conformance Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
871332b9-54a1-4a70-95f9-25e026c2823a | checkpoint | Report completed
f460e516-b8eb-5c80-bdf1-f3f03fb27429 | textbox | Short description
b097c8b5-a79c-5f6c-9070-32e56d7eaf32 | textbox | NCN NO:
9e01fe9d-19a1-58cf-9f63-69416e490b69 | textbox | Level / Area
b1fd2d09-5aa7-5eb0-9935-01b725b6acbf | textbox | Grid Coord
cbd8673c-36bb-588a-a953-0a7da7f5f308 | textbox | Responsibility
3557e6fd-c971-594f-b3f9-0f66732f3e3b | textbox | Non Conformance Details
b96b3c94-aad7-4f14-a53f-6092ac307d5c | checkpoint | Method of disposition
c7638eee-f413-5e47-829f-7193598055e9 | textbox | Approval required from
c433837e-988b-400f-a1f1-9651a0d8e691 | checkpoint | Repair / Use as is
def2b64f-a9ed-5c23-8c7c-759139524f44 | textbox | Customer
973d760f-0682-4279-83db-6cec9b728e2e | checkpoint | Rework / Replace
45a0157b-38f0-5713-88ff-07f464e5f3d7 | textbox | Project Manager
777e523e-3dc6-477d-b1c1-32d4bcc94094 | checkpoint | Signed off by Highbury Plumbing Supervisor
38464fa6-869f-462d-b8a7-b817e8daba47 | checkpoint | Signed off by Scentre Group
b27c7a6c-3cf6-4e7f-bb5d-01b14fee46e4 | checklist | Passive Fire / Collars Penetration |  | Passive Fire / Collars Penetration
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
09848c04-32ff-4404-bada-a3914b541358 | checkpoint | Please take detail photos of penetration & noteling
8467037e-e8dd-5ad6-800d-1f59cd0711f1 | dropdown | Material | PVC, HDPE, CU, PEX, GAL
2dbee740-6fd3-535d-8aea-2600aa22146f | dropdown | Pipe size | 20, 25, 32, 40, 50, 56, 63, 65, 75, 80, 90, 100, 110, 125, 150, 160, 200, 225, 250, 300, 315, 375, 450
e8d96fc8-3017-5c91-9790-c2129df58c14 | dropdown | Fire Matrix Ref Number | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 22, 23, 24, 25, 26, 27, 28, 29, 30, 31, 32, 33, 34, 35, 36, 37, 38, 39, 40, 41, 42, 43, 44,45,46,47,48,49,50,51,52,53,54,55,56,57,58
d33bf4d8-d19a-4199-8bea-ed5adaea5dec | checklist | Third Party Commissioning |  | Third Party Commissioning
fc1f52ce-6268-435d-9a12-0cd12425d055 | section | Details
f344d2b8-043b-4352-9955-b156661ea39b | checkpoint | Submit any Third Party Commissioning Reports which one are applicable:
de7988af-524c-59cc-8594-4e973541f6a2 | note | Ie Pumps, Tanks, HWS, Fire Hydrants
4e5d8169-8a2f-580f-ac84-88eedb2925fa | note | Report from Third Party