## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
743b05c7-880a-4a04-861e-f12cbce2c9fc | checklist | RR-SEPD-BESS-FIC-005-01 - Drainage installation |  | RR-SEPD-BESS-FIC-005-01 - Drainage installation -
b90f311e-b0b2-48c9-a174-7f56d4271296 | section | Part 1 – Preliminaries (photos where applicable)
391a5ae1-943d-46af-b010-3140891f2ed6 | checkpoint | Review of approved construction drawings and specifications
f6342505-b25a-51ab-b27a-1de7a80e5994 | note | All drawings and specifications approved and up to date
695d8195-71a4-56d3-a8cb-1f759bcb9c54 | note | WBS-SS-CI-SPC-006
9ed20f6f-3c37-46a7-808d-0472c512ebca | checkpoint | Verification of permits
7f317b9d-2f3a-52fc-9cf4-4f15c3d34bf7 | note | All relevant permits (GDA/GDP) in place
16f9fb0e-965a-516b-a065-1d1ce54cc878 | note | GDA/GDP
db4b78dc-9188-4741-aadb-9ad9496e388b | checkpoint | Site access and safety preparation
5de02b12-6f00-58e6-8f3b-0c9d8c31442c | note | Site access cleared and made safe
3cae6661-0b8f-5857-8494-1680a6e53564 | note | WBS-SS-CI-SPC-006
9e4a987e-a2d8-4ccc-a3c1-145c04c1b7fe | checkpoint | Safety inductions and toolbox talks
5dd35bb7-3ff8-535e-af25-3598d5b7fa5e | note | All personnel inducted; safety briefings completed
2ad7e96a-24b0-5191-9492-2b12e864103b | note | Induction record
81bd5a06-6ded-49f0-8a44-ef1825b6ec98 | checkpoint | Environmental controls in place
f2c11c05-abb5-540a-9e4e-f355cf02fef2 | note | Dust, noise, and sediment barriers installed and functioning
13f28080-b447-54cf-bf7e-2d35fd7394a7 | note | SEPD environmental requirements
5044381a-9051-40ba-a2e2-7a72eb348166 | section | Part 2 – Excavation and trenching (photos where applicable)
d33a063a-7ee3-44c9-8bcd-c53950b5707d | checkpoint | Trench depth and width comply with design
f52d88ae-acd2-59fe-97dc-6749c833a45f | note | Set-out verified and matches IFC drawings
5d0206a4-3452-5b9b-a987-4a191b091c5c | note | Site IFC Drawings AS/NZS 3500
5d2aede9-3681-4177-8c6a-3b207377ea0b | checkpoint | Stable trench walls (benching, battering)
a661bbfb-56a2-583e-a2cb-b884fae5777b | note | Trenches deeper than 1.5m require benching, or battering unless certified by a geotechnical engineer.
cec9a328-06bb-5a24-8f57-c0adf54c3105 | note | WBS-SS-CI-SPC-006 AS 4744
caa23a59-8519-41ff-b58d-56296a5ccb3f | checkpoint | Pipes inspected for defects before installation
9609f655-530c-562b-aab0-3d80fb657f22 | note | Material certs from manufacturer and visual inspection
58b2f5b8-543c-5d70-9ecd-2bc37a0be3ee | note | Material to align with design drawings and load rating
2511f9eb-1e45-50f6-9884-947e883ecae2 | note | Manufacturer certifications
dcd0c819-38f4-4c54-bdb6-7790cce47add | checkpoint | No water accumulation in trenches
31e701c8-65f9-5f5a-b557-151b0554e492 | note | No standing water or excessive moisture inside the trench.
7d480db5-1694-58d1-9546-3846876c07aa | note | AS/NZS 3500
d66145f1-d0c9-4781-a50c-2f18d2cb88a4 | checkpoint | Exclusion zones around excavation established
48412728-3b5f-5fe8-9f95-9732c1e936a9 | note | Proper barricades and signage placed around excavation area.
a399bda5-4e85-5d8e-8f7e-44ee48232c05 | note | AS 1742
b1b7b6df-388b-4636-aa96-536bd09ef890 | checkpoint | Spoil stockpiles located at least 1m from trench edges
ac02685b-cbae-5afc-b66b-cc9457dd8496 | note | Stockpiles away from excavation to maintain safety of batters
99691f19-158e-5c9c-8f67-f238b1000f88 | note | WBS-SS-CI-SPC-0006
e0e68ab7-f0c1-4dab-9c36-7ad63d99fc2c | checkpoint | Access and egress (ladders, steps) provided for trenches deeper than 1.2m
d56a7f73-f97f-5078-8820-8946d887ee56 | note | Access and egress for each trench.
e8182d35-f054-596e-81ed-e79975a936b6 | note | WHS
8386bb75-7c82-431a-8e57-08b313e54864 | section | Part 3 – Bedding & Pipe Installation (photos where applicable)
60144199-262e-4cc2-a756-05bfa2e2f0b9 | checkpoint | Correct bedding material used (sand, gravel, etc.)
db99c7a9-652f-5cf0-9724-9af661dcd16b | note | Material complies with particle size, moisture content, MMDD
73d654ad-3ee3-591f-b432-c9101fffb41c | note | WBS-SS-CI-SPC-0006 Test material results
09782c34-11a5-4a9e-9e30-e783ae5407b5 | checkpoint | Bedding compacted to required density
a55f0016-0f60-5c32-adbf-53e56552bb8e | note | Layers placed in maximum 300mm (loose) thickness
61b03917-0ab7-55e9-8119-b7474f1de30f | note | WBS-SS-CI-SPC-0006
a0ed564a-7b35-4e0b-88c6-fbd56520597e | checkpoint | Pipes and materials inspected for defects before installation
8ef4ed34-b835-5d2a-b83d-0fc3d3050b13 | note | Installed to design grade ±10mm and alignment within 5mm tolerance.
62459d9f-54bd-544c-80c1-cdbd69e43b06 | note | AS/NZS 3500
34284f3d-ee67-4ddf-84b5-517703238bab | checkpoint | Pipes laid at correct grade and alignment
52e49986-886b-5de6-80a8-75185f880cad | note | Levels and grading match design tolerances (+/- 20mm)
3aea62ee-dbfc-5552-a1e7-9146e6ae6e2e | note | WBS-SS-CI-SPC-0006, Survey Report
7f81e170-de7d-496a-abcb-5e66a56c33f3 | checkpoint | Correct pipe jointing method used (rubber ring, solvent weld, etc.)
1993c0ae-d414-5d6f-a2e5-d0504f8110ff | note | Joints must be fully engaged and sealed per manufacturer specifications
49830ab0-bc4b-5ac0-8e35-f9d14d371522 | note | Manufacturer specifications
82105611-93f0-48cb-8628-a5b798a2d7b4 | section | Part 4 – Backfilling and compaction (photos where applicable)
df2d5a01-6c28-4128-93f3-7d19e08ab465 | checkpoint | Initial backfill material placed evenly around pipes
d70bc48c-a702-5e5c-bf53-2e02ba2c425d | note | Site-won material approved by geotechnical engineer
425ee2e6-77f0-5037-9181-fe483dd48bbd | note | Geotechnical report AS/NZS 3725
18926533-166a-4b01-98c3-2b09acac254b | checkpoint | No large rocks or debris in backfill
463757b1-d720-5a48-be2d-67a49c0c9b43 | note | No rocks or debris in backfill
7f27bff5-6b9a-5ded-85b0-31b69cf634dd | note | WBS-SS-CI-SPC-0006
4dbeb5fc-f40a-4394-b24f-963e180a57d9 | checkpoint | Backfilling in controlled layers (300mm lifts)
9219e637-8b0f-5421-93bf-caedc92aa540 | note | Backfill in uniform layers of maximum 300mm thickness
775486c5-cd86-528b-bed2-da0e645ab378 | note | WBS-SS-CI-SPC-0006 Drainage drawings
810b5590-0369-428d-9c60-76cd0ac443f6 | checkpoint | Backfill shall be placed to a depth of 300mm above collars of pipes or conduits
f757b803-b992-5121-a100-f97b9364a627 | note | Minimum 300mm above collars of pipes
72d22a89-b39d-5a01-aae2-f2c2bdc529bc | note | WBS-SS-CI-SPC-0006
9192aa2c-9200-427f-a148-8d48d5a509e6 | checkpoint | Compaction tests performed and passed (Proctor Density, NDM, etc.)
deffcd55-91a6-56c3-80f6-bc1a0b0685d0 | note | Compacted to 93% MMDD
1beb1f03-e395-59d0-81fd-9db86a073750 | note | WBS-SS-CI-SPC-0006 AS 1289 TQ # 66
a2bbf500-f3c1-4571-aa3f-3a6c6b2a773e | checkpoint | Surface reinstated as per project specs (concrete, asphalt, topsoil)
6cc5d391-2f1f-5061-b4ff-dc42b3a52ab5 | note | Backfill to match existing ground levels with ±10mm tolerance.
851b710e-115a-5f5b-9630-4b6700424330 | note | IFC drawings
e290f1b0-b3bd-4062-b47e-4acf56a1ec98 | section | Part 5 – Final inspections and acceptance (photos where applicable)
dce702b6-b3e5-4f2c-b399-e65644bb5a8b | checkpoint | As-built survey verification
00bb7589-acd8-5f07-a259-13bd786f2ef5 | note | As-built levels and layout match design
c3d74251-e086-5734-92df-a724048e9f92 | note | As-Built Drawings Survey Report
70f914de-1b91-4acb-8d0d-ee173fe28755 | checkpoint | Removal of temporary works
887692b2-6c9b-5dba-817e-ef973499736c | note | All temporary structures, barriers, and access points removed
a277040a-eef4-5abd-9172-da9d7e9e410a | note | Site inspection
7c4a663a-975d-46b0-851a-b70fb8b4b902 | checkpoint | Final inspection sign-off
55fb7a7c-4cd8-5a64-a6f4-8169b2909224 | note | All drainage activities completed and accepted
7b438ec9-a41f-5dfb-81b4-b72c6f9c36b7 | note | WBS-SS-CI-SPC-0006
acc738da-39a7-423a-aa7a-cf3298c9f1cc | section | Document Sign-off
3b0f4903-6b18-4b88-8b0b-1a4c5b8b5285 | checkpoint | Close-out
b90d460f-ca53-5606-a7a5-57af37cb9112 | textbox | SEPD - Name:
7f8b4e4e-e1a2-5adf-8b90-a479a7d76c0c | textbox | SEPD - Position:
44602056-170a-5ab0-bb34-4112d72e1870 | date | SEPD - Date:
6d65e662-c6c8-4040-8e2d-0040e700a3f6 | signoff | Add Signature
37219507-935a-4c78-b17e-9d67ed64aea5 | checklist | RR-SEPD-BESS-ITP-005-01 - Drainage installation | itp | RR-SEPD-BESS-ITP-005-01 - Drainage installation - Layer
436b84c5-5f97-4c42-9d84-10a9d1647409 | section | Section 1: Preliminaries & Permits
27425897-a988-45ad-a6ae-320626e3a87d | checkpoint | 1.1 - Collect and verify information (Site boundary, utilities, survey map, design drawings)
a1cbd207-60d1-5504-a29c-047d947fb0bd | note | Responsibility - SE/PE
cd2e8b13-4b7e-5152-916d-df39215c8258 | note | Specification Reference - WBS-SS-CI-SPC-0006
70d477db-3067-52ac-9afc-7dba3310bd9c | note | Conformance Criteria Summary - Results included in work pack
5caa0d97-2387-5b65-a06e-212c9eb68955 | note | Method - R
96946c0b-51ad-5cbe-852d-2bcaff053625 | note | Frequency - PW
14dd2e93-911d-55e3-b631-bbb7aa016495 | note | Hold/Witness Point Requirements: ROBAR - V
3411205a-13c7-55e8-a9fe-ada270e515db | note | Hold/Witness Point Requirements: SEPD - NA
11ea78a1-0ef0-5e25-9094-9be4422c1403 | note | Hold/Witness Point Requirements: Client - NA
50145814-37e3-5cbd-88e7-b2bf754e5a5d | note | Records or Checklist Document Number - IFC Drawings
91b6a6f1-d3f8-49b9-9646-b7b6dcdcd4e8 | checkpoint | 1.2 - Permit approval (GDA/GDP)
a1502325-b03d-5b90-bb65-fdb86c5d1131 | note | Responsibility - SE/PE
3967094b-9e01-5704-b3d6-74b450af919a | note | Specification Reference - WBS-SS-CI-SPC-0006
1cd2c4c2-997e-511b-b1ff-66057692d84c | note | Conformance Criteria Summary - Approved excavation permit (GDP) prior to commencing works
ff549d39-83c0-5ce1-a372-99fa2d513422 | note | Method - R
32465b12-87f4-59f1-8d80-089fbe8bf904 | note | Frequency - PW
3eabfb22-3fab-5a4a-a8dc-310137defcd1 | note | Hold/Witness Point Requirements: ROBAR - HP
a5eb7bab-d45a-5431-9555-557826ac1a42 | note | Hold/Witness Point Requirements: SEPD - HP
4d64df7e-b53c-549e-b6f9-3907ee8dd86e | note | Hold/Witness Point Requirements: Client - NA
bc766235-9852-56bd-97d2-d6f184ac35ae | note | Records or Checklist Document Number - RR-SEPD-CI- SOW-002-01
a196f895-2f51-4aa6-b060-89bd43235302 | signoff | HOLD POINT
ed3d672e-54f5-445a-8777-297c6dee6942 | checkpoint | 1.3 - Site set-out
c9d77067-6a33-53b5-bb64-466d72b3045a | note | Responsibility - SE/PE
ad8cabd0-502d-567a-98bc-7b4691d82d4e | note | Specification Reference - WBS-SS-CI-SPC-0006
f7fc8c42-814b-593e-aaf7-6ec0134251d8 | note | Conformance Criteria Summary - Verify levels, site boundaries, and physical bounds per IFC drawings
73f9c019-05ef-55fb-bba0-28026f6cb21a | note | Method - R
3bd9f712-13f9-502d-a1b7-6f10cbdd65b7 | note | Frequency - PW
939327aa-5239-509b-9197-f5c11b77633b | note | Hold/Witness Point Requirements: ROBAR - V
4df215c2-112c-578e-942a-6084c1b486cc | note | Hold/Witness Point Requirements: SEPD - NA
92ecc7f0-44c7-56e5-acb3-57085dcaf119 | note | Hold/Witness Point Requirements: Client - NA
707d0a65-16de-51bc-97f4-7720036f876b | note | Records or Checklist Document Number - IFC Drawings
2e008a5a-4c83-4983-aba0-59671ddccdd7 | checkpoint | 1.4 - Sediment control plan
7ed1153e-5791-5a70-b9e8-7604c781bb7a | note | Responsibility - SE/PE
e1be991a-3748-5e60-b0a2-d0cc5dec55a8 | note | Specification Reference - WBS-SS-PM-PLN-0024, WAE230103- 03-003 TM Rev0
78b6f86d-ae06-5233-8843-202e1bfab6f9 | note | Conformance Criteria Summary - Sediment control measures in place
8e1554e0-3d95-5e76-bbc4-b52d9452e0aa | note | Method - R
29ee98f9-4b0e-54b7-818c-a9df45a4a473 | note | Frequency - PW
18f79cfb-4b32-5a78-8951-6499e53a2e95 | note | Hold/Witness Point Requirements: ROBAR - V
0b6a9226-476b-555b-a743-d00ac18bad2a | note | Hold/Witness Point Requirements: SEPD - NA
69435f86-3259-5336-af96-2cd2a2aa8329 | note | Hold/Witness Point Requirements: Client - NA
79571000-21c0-5343-8a13-9cb4cca656fc | note | Records or Checklist Document Number - SEPD environmental plan
7544c3a9-c050-4a4b-82db-20123c687b3a | checkpoint | 1.5 - Dust control plan
856d3e3f-1f86-563d-b335-4a0834ce908f | note | Responsibility - SE/PE
c8c6dcce-a2a2-593a-83ef-652a816a1f16 | note | Specification Reference - PP3 section 1.5 and section 4.1
6278cd07-8c47-5a9d-b81c-e8825d38af15 | note | Conformance Criteria Summary - Dust control measures in place
665f5894-a2f5-555e-8ed2-d9a5bb8f27db | note | Method - R
b92f959c-5f49-5ea7-a33f-43e5fb7949cc | note | Frequency - PW
77bab274-b02a-53bb-85fc-143273d6f69a | note | Hold/Witness Point Requirements: ROBAR - V
499017d0-7d94-54a8-bf7c-fe86fdcdca46 | note | Hold/Witness Point Requirements: SEPD - NA
f2e80817-9172-5054-912b-65c2b66e54f9 | note | Hold/Witness Point Requirements: Client - NA
539c58d1-99eb-54f1-9394-89fcf218157a | note | Records or Checklist Document Number - SEPD environmental plan
35c072cd-f5e6-4b8c-b044-66f56b55f8dd | section | Section 2: Materials
44e5b971-523b-436d-ba6b-3ba1b21de77d | checkpoint | 2.1 - Import fill material inspection
4ca2f01c-176a-53d6-9042-f712b8178a32 | note | Responsibility - SE/PE
7469d062-0814-5af5-9a44-18b9d76fc301 | note | Specification Reference - WBS-SS-CI-SPC-0006
ef937090-994c-5657-baf5-4c0385bdd737 | note | Conformance Criteria Summary - Material certificate and test report for particle size distribution, moisture content, MMDD
c9bd8f35-6da0-5421-83cc-fc99477f5094 | note | Method - R
c1d5d48c-cf6c-519a-983c-c273e1855a27 | note | Frequency - PW
de921931-daa3-5aab-8d6d-c41f6d9ae8ae | note | Hold/Witness Point Requirements: ROBAR - V
50fe4890-9887-5d15-9567-a0af5f565a0b | note | Hold/Witness Point Requirements: SEPD - V
9ddb2807-058e-549d-8231-fb73a8cc25f4 | note | Hold/Witness Point Requirements: Client - NA
abda1ab1-5e64-54a0-a166-0e8608d54508 | note | Records or Checklist Document Number - Material certificates
fa0fd4f4-deaf-4c92-b576-2e91767056c1 | checkpoint | 2.2 - Verify suitable foundation material (compaction >95% MMDD)
dad98bb8-87c4-59ab-ba68-a58f4c2fe194 | note | Responsibility - SE/PE
d949e8bd-7902-51b3-8cad-65948b11f127 | note | Specification Reference - WBS-SS-CI-SPC-0006
27dbd875-9f99-56f9-bbad-1d97f3952ddf | note | Conformance Criteria Summary - Geotechnical test results showing compliance
e1cf5025-f304-578b-9d36-68e8e23c5016 | note | Method - R
c3e7c1de-5b62-509d-a730-60eaf3de27a1 | note | Frequency - PW
b1b90902-4e8e-5f1d-a101-dd880aa0aecb | note | Hold/Witness Point Requirements: ROBAR - HP
36497c62-a023-5fd6-984f-e5dee0a7f1c6 | note | Hold/Witness Point Requirements: SEPD - HP
c271a7e3-4f57-5be7-ba3a-87311cc8252e | note | Hold/Witness Point Requirements: Client - NA
020ad674-9509-5787-bb18-10680a6c4960 | note | Records or Checklist Document Number - Test results
27e28b80-b0ef-4e04-abe9-b0ae60bc90a3 | signoff | HOLD POINT
10269c43-5631-4827-9193-11920983f7cd | checkpoint | 2.3 - Quality documentation RCP & precast drainage pits
f7336be0-1f85-5853-a975-8d7e689e46c2 | note | Responsibility - SE/PE
bfdbd015-6582-5251-bb9f-0e35661d3d43 | note | Specification Reference - WBS-SS-CI-SPC-0006
36e8ef5f-4771-531f-98bd-07080f0a3968 | note | Conformance Criteria Summary - Supplier’s quality system certifications
f146ff8d-1314-569c-81c7-82d812b7411e | note | ○ Product of compliance to AS 4058, AS 3500, AS 3996. (Load rating & liner shall align with design drawings)
5aa39559-4c64-58ba-a5ee-4481ff441d05 | note | Method - R
2cb4e406-a79f-593d-b8b6-c81725ab9d27 | note | Frequency - PW
06468ce6-efa5-5753-abc1-1845544122d9 | note | Hold/Witness Point Requirements: ROBAR - HP
778b94f5-d8fb-5807-ba8c-b556d4ebccba | note | Hold/Witness Point Requirements: SEPD - HP
a2ee3e6e-66fd-5126-a79d-587a524fa919 | note | Hold/Witness Point Requirements: Client - NA
4e2630fd-f48a-5b2c-8891-a1002fd6d5c6 | note | Records or Checklist Document Number - Supplier’s documents
ff372579-2782-4e6a-829a-a58f0e4cc4a0 | signoff | HOLD POINT
dbf87332-95e0-41f9-b6f9-eaee689bfb3c | checkpoint | 2.4 - Delivery acceptance of RCP
159e60f0-7dbe-5490-888a-fafab9a25fe5 | note | Responsibility - SE/PE
63c141a8-600b-5985-8793-5ee08677aa19 | note | Specification Reference - WBS-SS-CI-SPC-0006, AS/NZS 4058
12df593c-7ef2-5d2f-b6e4-6c8516eb60fc | note | Conformance Criteria Summary - Acceptability of defects of RCP’s.
86bcf5af-2c2a-5cfe-a8fd-91c16ee15d92 | note | ○ Fibre RCPs shall be rejected if fractures and cracks wider than 0.1 mm and deeper than 0.3 mm are present.
8f44ce19-6ac5-5c59-befa-31290b977152 | note | Method - R
83d49955-2214-5b32-a97a-aa615a2d6137 | note | Frequency - PW
ec12fc65-b31e-56e5-a55e-3ae0c65e2129 | note | Hold/Witness Point Requirements: ROBAR - HP
5af4d6e3-8be7-5d09-8371-0998ee9b8686 | note | Hold/Witness Point Requirements: SEPD - HP
73c8edf5-1914-5dd1-b66d-c8133381f307 | note | Hold/Witness Point Requirements: Client - NA
19198e37-f175-5065-b4ee-3dadb1a3cc7d | note | Records or Checklist Document Number - Delivery dockets
fe86dcac-f2b3-41f3-b7c1-2b5d3ffeacb5 | signoff | HOLD POINT
c4bc7d20-f3d7-4cfe-add5-25d8dad41281 | section | Section 3: Construction
608a94cf-e0fa-4782-bb69-7d708d607297 | checkpoint | 3.1 - Excavated trench
ba8b4b04-b885-5b98-86d2-6308fcb4c651 | note | Responsibility - SE/PE
697d3e42-01cc-515d-8a47-0f6952b545a7 | note | Specification Reference - WBS-SS-CI-SPC-0006
de61cbb7-ba82-5daa-a1c9-480f9e239b25 | note | Conformance Criteria Summary - Inspection following excavation of trench. Wacker plate to be use for compacting base.
c90b499c-bced-5f7a-8987-d43f6c487522 | note | Method - I
29525613-b690-5678-a8b4-e6f7aab0586d | note | Frequency - PL
22a1dc34-3912-5ea2-b2f1-ee09bafd499c | note | Hold/Witness Point Requirements: ROBAR - V
31b97e46-3138-5621-b0bc-9e7f66a4fb64 | note | Hold/Witness Point Requirements: SEPD - V
2be9607e-f4be-5143-886c-552d3627dac8 | note | Hold/Witness Point Requirements: Client - NA
693deb2a-a981-5291-ad95-8cd19b749fbf | note | Records or Checklist Document Number - IFC Drawings
67678156-39ca-4ffb-8e82-f94e075a8ec0 | checkpoint | 3.2 - Bedding
9926f445-caa3-5189-a7f3-eb29343078b4 | note | Responsibility - SE/PE
2b266d57-bc01-59a5-bfd2-dc198b5e8247 | note | Specification Reference - WBS-SS-CI-0006
a489f83b-5020-581a-9702-c1426c0a97f8 | note | Conformance Criteria Summary - Material to be compacted at 100mm depth minimum.
2700aba8-c700-5a25-b029-dbf0b9f90613 | note | Method - I
9aa378f9-8cd4-58b9-8413-520aab43061f | note | Frequency - PL
dcc01783-8804-5473-9b45-c87e7c05d2c4 | note | Hold/Witness Point Requirements: ROBAR - V
1d3f44b2-62cd-5bba-b2cd-db7db88d32ed | note | Hold/Witness Point Requirements: SEPD - V
038ef79d-c2d9-5879-a61c-61cebc91ae61 | note | Hold/Witness Point Requirements: Client - NA
41f3875d-4761-5248-8cdf-aa05c9ec6f96 | note | Records or Checklist Document Number - IFC Drawings
ae1a01e4-5712-40dd-ad8f-7e96336b5557 | checkpoint | 3.3 - Placement of concrete pipes
eb5011bc-a836-55b5-b55a-14d897bccfba | note | Responsibility - SE/PE
3d1e8594-c6c9-5d6f-9437-23705c81b05f | note | Specification Reference - WBS-SS-CI-SPC-0006 IFC drawings
4f261c80-f5eb-5404-b1a0-66791d8e5c05 | note | Conformance Criteria Summary - Placed and joint in accordance with the manufacturer’s specifications
2a737901-a66d-5be1-b163-d62a7b3cb15b | note | ○ Female ends upstream and lifting holes uppermost. Lifting holes in pipes shall be filled with plugs provided by pipe manufacturer
3b040e3a-e874-55ce-876c-0b4280116817 | note | Method - T
db633bf1-c313-5572-bcab-1a995ca99081 | note | Frequency - PL
e8a223fc-f20c-5109-b042-5931d3550ec0 | note | Hold/Witness Point Requirements: ROBAR - HP
dc94c861-0eff-5fa9-8300-7fa693cc5b8e | note | Hold/Witness Point Requirements: SEPD - HP
5c63ae49-f4c5-5ea6-ad1a-27e0346c9242 | note | Hold/Witness Point Requirements: Client - NA
bd74e0cc-63c9-5371-a5ca-90a8f2e89191 | note | Records or Checklist Document Number - This ITP
ea627f23-940c-4b9a-b5f3-4e95933677d0 | signoff | HOLD POINT
f5001589-f059-44de-9090-7e3b01c00563 | checkpoint | 3.4 - As-built survey prior to backfilling
05830a50-7c88-594a-bba8-7d36b5bdcbd9 | note | Responsibility - SE E
b0222b04-5906-526a-9e70-922f8ea5eecd | note | Specification Reference - WBS-SS-CI-0006
3989c0e7-1301-5427-baa8-421707525c08 | note | Conformance Criteria Summary - Variation of reduced level of invert from specified level:
3bc145cc-f26f-5cfc-851f-760995af4db4 | note | ○ Whitin +/- 10 mm of specified position. Invert of structure shall not impede the gravity flow of water into or from structure
1991bfac-e089-5ee5-b646-aac91d38202b | note | Method - I
f2b3bd5e-0674-5364-85d4-35e8becefcb8 | note | Frequency - PL
baa504ac-aae4-5294-a31a-7e0759f0dd2e | note | Hold/Witness Point Requirements: ROBAR - V
99b29e5f-bb58-5124-bdc9-7d9fd6bd450c | note | Hold/Witness Point Requirements: SEPD - V
0ace67fb-dec2-57a8-9a1f-d7c304dce237 | note | Hold/Witness Point Requirements: Client - NA
4ca19525-339b-550d-a2e5-1971a8b309f0 | note | Records or Checklist Document Number - Survey report
f3ce8f28-30ee-4c36-a41e-4f9498babdd4 | checkpoint | 3.5 - Installation of precast drainage structures
563dc397-7b00-5406-b27d-d98b6428771f | note | Responsibility - SE/PE
357b8452-fe0c-578f-a15b-f5731f26dd54 | note | Specification Reference - WBS-SS-CI-SPC-0006, AS 3500 Design drawings
25043b90-feaa-5e76-a0eb-50dbd18a1345 | note | Conformance Criteria Summary - Inspection pit cover to be installed flush with the final surface
fff2bdbe-3026-58b4-b53d-9296ad931b34 | note | ○ Where precast drainage structure is used, the external joint with pipe shall be strengthened with a concrete fill circling the joint.
76b295eb-9ccd-56e6-a997-2e25c745c510 | note | Method - T
16d40b8a-da10-582a-a15a-5d0d55b2bc5b | note | Frequency - PL
ac6a6e78-c307-54eb-bc6e-92e0768a75c0 | note | Hold/Witness Point Requirements: ROBAR - HP
1ae6030a-64fc-510c-ac1b-f37cbfb36105 | note | Hold/Witness Point Requirements: SEPD - HP
b0aef2ea-8257-5480-95e1-017995ee46b6 | note | Hold/Witness Point Requirements: Client - NA
8c206332-52f1-5d7a-8637-a69987b046ad | note | Records or Checklist Document Number - Test results, NER engineer specifications
f3bebc3d-a678-471a-848e-c525727f6e7b | signoff | HOLD POINT
| checkpoint | 3.6 - Drainage runs and pits fully installed and ready for backfilling
| note | Responsibility - SE/PE
| note | Specification Reference - WBS-SS-CI-SPC-0006, AS 3500 Design drawings
| note | Conformance Criteria Summary - NER engineer signoff prior to backfilling.
| note | ○ Drainage installed as per design drawings.
| note | Method - T
| note | Frequency - PL
| note | Hold/Witness Point Requirements: ROBAR - HP
| note | Hold/Witness Point Requirements: SEPD - HP
| note | Hold/Witness Point Requirements: Client - NA
| note | Records or Checklist Document Number - NER engineer specifications
| signoff | HOLD POINT
79fffcd6-9d0c-4f84-9df1-fb9594a607f7 | checkpoint | 3.7 - Trench/Precast drainage item backfill
019b45de-2787-569f-b62e-311318a60a1f | note | Responsibility - SE/PE
44985f41-c191-5d10-b1bc-2fade7f607a4 | note | Specification Reference - WBS-SS-CI-SPC-0006, PPR
2e554f5b-5fec-529b-848f-7775ac71adc2 | note | Conformance Criteria Summary - Unless specified otherwise, backfill layers shall be maximum 300 mm layers.
bfeeddd6-a41d-5663-86c4-af9573897ac2 | note | Method - S
63c02950-4e13-59be-9b86-d56bcccb268e | note | Frequency - PL
504c65b9-d339-5ebf-b899-31af4e663ec7 | note | Hold/Witness Point Requirements: ROBAR - V
69f0dd69-4caa-5f34-a66c-00dd980a564e | note | Hold/Witness Point Requirements: SEPD - V
07b2aa3d-6a77-5fb0-91fe-947462c4f8aa | note | Hold/Witness Point Requirements: Client - NA
9e64d17e-099b-5187-b97b-e6d5540bd099 | note | Records or Checklist Document Number - Compaction report
916be4fe-368d-4f67-a16e-d5f4a2e58d6e | section | Section 4: Final Inspection
908e64b5-47d7-4909-b4a1-1fcf92e59222 | checkpoint | 4.1 - Finish level compliance with design drawings
c1aca4b5-1051-551b-955c-debd3d956642 | note | Responsibility - SE/PE
1d7f5d50-6a75-5821-ba2a-780445846d0c | note | Specification Reference - WBS-SS-CI-SPC-0006
63518ed5-77ba-581e-8ef5-6045c5dbc5d9 | note | Conformance Criteria Summary - As-built drawings.
776c70cd-9f07-574e-a667-f971db6d671c | note | Method - S
169fb815-b773-5e5c-a002-8ab5318fa45c | note | Frequency - PL
4727fae2-1742-5287-91a3-3b728e9cf88b | note | Hold/Witness Point Requirements: ROBAR - V
0252ddf9-87fc-5f5d-9006-d1441de00421 | note | Hold/Witness Point Requirements: SEPD - V
864d9857-88f0-5da9-b26a-bd7c152ee1d2 | note | Hold/Witness Point Requirements: Client - NA
54473b72-d517-554d-ac12-6cf95e714cc9 | note | Records or Checklist Document Number - WBS-SS-CI- ITP-920049
b3004b26-9d8e-4afb-a541-5485c7be617f | checkpoint | 4.2 - Final Inspection Checklist (FIC) completion
12f63595-f802-5de4-a53f-c95faac00c2f | note | Responsibility - SE/PE
9c4fc9e6-34ec-53b8-87c6-c0bdd2e6fc4a | note | Specification Reference - WBS-SS-CI-SPC-0006
5952f050-ff53-53fd-92b7-b0393136cb7a | note | Conformance Criteria Summary - Signed FIC
b0eacdcd-b24c-557a-bc13-79f60442892d | note | Method - R
90aecb69-dc4e-5eb2-a55a-dd071f1a096d | note | Frequency - PL
675eeda5-4680-5350-ac04-f78ed10e33ab | note | Hold/Witness Point Requirements: ROBAR - V
6056fc06-c9ee-5f38-8599-262efd26c829 | note | Hold/Witness Point Requirements: SEPD - V
700d2c9d-63e5-50aa-b143-8fc9fb448d9b | note | Hold/Witness Point Requirements: Client - NA
0862c071-c7dd-5b8c-9bad-0b61eb2f597a | note | Records or Checklist Document Number - WBS-SS-CI- ITP-920049
625ec812-a878-4353-9dd5-b44d2268a565 | section | Document Sign-off
d946f204-738b-4c02-8744-bb054961bc70 | checkpoint | Close-out
7c5360b7-ef89-5b6b-9544-618892e6106a | textbox | SEPD - Name:
6c694594-4a96-5f9d-8365-9ba69a3b132d | textbox | SEPD - Position:
c4f48618-6811-581b-9f84-edb06b13d199 | date | SEPD - Date:
78de3a49-b1b2-4c51-a2dd-00cacc052bbd | signoff | Add Signature