## Resources
type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist | QA - ERV |  |  |  |  | Yes | QA - ERV | 792f0250-66cb-4c2c-a9f2-5db2cfa6cd09
section | Pre-Start ERV
checkpoint | Area clear, access good, enough space for install
checkpoint | Duct Route clear, Penetrations complete
checkpoint | Nogs/Supports in place
section | First Fix ERV
checkpoint | ERV installed straight and level and correct orientation.
checkpoint | Fan or Cowl sealed to Upstand
checkpoint | Correct ERV installed | MANDATORY PHOTO
checkpoint | ERV serial No. recorded | MANDATORY PHOTO
checkpoint | ERV seismically braced
checkpoint | Access Panels in duct for fire dampers, filters, cleaning etc
checkpoint | Ductwork straight/level and well supported including any seismic restraints | PLEASE DELETE RED TEXT ONLY
checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
checkpoint | Flexible ducts run straight/tight/well supported/secured close to grille location
checkpoint | Flexible ducts taped
checkpoint | Supply cable installed correctly, protected and secured
checkpoint | Coms Cable Installed
checkpoint | Plans marked up for As Builts and 2nd fix grille locations
section | Second Fix ERV
checkpoint | Grilles installed square and level
checkpoint | Flexible ducts taped then cable tied to grilles/boots
checkpoint | Boots sealed to grilles
checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
checkpoint | Controllers fitted off.
checkpoint | Power fitted off
checkpoint | Area left clean and tidy, fingerprints removed
checkpoint | Plant and controllers labelled
section | Commission ERV
checkpoint | Commissioning paperwork reviewed and accepted by Project Manager
checkpoint | Electrical testing complete
checkpoint | COC issued
checklist | QA - Fan Coil Units |  |  |  |  | Yes | QA - Fan Coil Units | 9e3a6ae4-d492-47c2-b5ea-269d68c99bb1
section | Unit First Fix QA
checkpoint | Correct Unit Installed | MANDATORY PHOTO
checkpoint | Unit at correct height
checkpoint | Mounting and Springs Installed
checkpoint | Correct Hanger Spacing
checkpoint | Fridge or Water Pipes connected to unit, correct valves and fittings
checkpoint | Unit Plenum Boxes to be installed
checkpoint | Filters installed
checkpoint | Seismic Bracing Installed
checkpoint | Drawing information uploaded
textbox | Drawing Reference Number
checkpoint | P - trap installed
checkpoint | Drip tray installed
checkpoint | Condensate Drains installed
checkpoint | Tundish provided by others
checkpoint | Correct Fall to tundish , and water flow tested
section | Unit Second Fix QA
checkpoint | Grilles installed square and level
checkpoint | Flexible ducts taped then cable tied to grilles/boots
checkpoint | Boots sealed to grilles
checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
checkpoint | Controllers fitted off.
checkpoint | Transmission cable fitted off and labelled to and from if daisy chained
checkpoint | Power fitted off
checkpoint | Area left clean and tidy, fingerprints removed
checkpoint | Dip switches set
checkpoint | Plant and controllers labelled
section | E4M QA
checkpoint | Wiring First Fix Complete
checkpoint | Cable Tray Installed Correctly
checkpoint | Electrical Isolators installed in Correct location
checkpoint | Units Terminated | MANDATORY PHOTO
checkpoint | Controllers Installed
checkpoint | All transmission or Interconnecting cables labelled where they go and come from | PLEASE DELETE THIS CHECKPOINT
checkpoint | Units Tested and Running
checklist | QA - Water Cassette Units |  |  |  |  | Yes | QA - Water Cassette Units | af953e9e-626e-4d64-a8d9-821eb070bd27
section | Unit First Fix QA
checkpoint | Correct Unit Installed | MANDATORY PHOTO
checkpoint | Unit at correct height
checkpoint | Mounting and Springs Installed
checkpoint | Correct Hanger Spacing
checkpoint | Pipes labelled at each end
checkpoint | Fridge or Water Pipes connected to unit, correct valves and fittings
checkpoint | Seismic Bracing Installed
checkpoint | Drawing information
textbox | Drawing Reference Number
checkpoint | P - trap installed
checkpoint | Drip tray installed
checkpoint | Condensate Drains installed
checkpoint | Tundish provided by others
checkpoint | Unit protected from dust and debris
checkpoint | Correct Fall to tundish , and water flow tested
section | Unit Second Fix QA
checkpoint | Face Plate installed square and level
checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
checkpoint | Controllers fitted off.
checkpoint | Power fitted off
checkpoint | Area left clean and tidy, fingerprints removed
checkpoint | Plant and controllers labelled
section | E4M QA
checkpoint | Wiring First Fix Complete
checkpoint | Cable Tray Installed Correctly
checkpoint | Electrical Isolators installed in Correct location
checkpoint | Units Terminated | MANDATORY PHOTO
checkpoint | Controllers Installed
checkpoint | Units Tested and Running
checklist | QA - General Pipework |  |  |  |  | Yes | QA - General Pipework | c562e6a2-931b-4584-b349-cf989ddfb939
checkpoint | All pipework lagged
checkpoint | Pipework supported
checkpoint | Pipework labelled where needed
checkpoint | Pressure test complete (with photos)
checklist | QA - VRV High Wall |  |  |  |  | Yes | QA - VRV High Wall | c6205301-5897-4e3b-8234-3490f67a9bda
section | Pre-Start HW
checkpoint | Area clear, access good, enough space for install
checkpoint | Pipework route from Outdoor to Indoor unit all clear, penetrations complete
section | First Fix HW
checkpoint | Pipework connected to Outdoor unit
checkpoint | Pipework connected to Indoor unit
checkpoint | Pipework Insulated complete length
checkpoint | Insulation Joins Glued and taped
checkpoint | Pipework supported including any seismic restraints
checkpoint | Drain installed and insulated
checkpoint | Supply cable installed correctly, protected and secured
checkpoint | Interconnecting cables correctly installed, labelled and protected
checkpoint | Remote controller cable installed
section | Second Fix HW
checkpoint | Indoor unit secure, level and tight to wall
checkpoint | Correct Indoor unit installed
checkpoint | Indoor unit serial no. recorded
checkpoint | Installer confirmed drain tested
checkpoint | Controller installed
checkpoint | Area left clean and tidy, fingerprints removed
checkpoint | Plant and controller labelled
checkpoint | Access for future maintenance all clear. Filter can be easily removed
checklist | QA - Mechanical Duct |  |  |  |  | Yes | QA - Mechanical Duct | dde6f0e6-26d1-4867-832b-75db8c380416
section | First Fix QA
checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint | Outside duct to have capping installed
checkpoint | Ducting / equipment connections including flexibles, nuts, bolts and washers correct and tight.
checkpoint | U/S of duct heights correct as per Workshop Drawings.
checkpoint | Locations marked on plans for second fix
checkpoint | Ducts to be removed relocated / relocated as per drawings
checkpoint | Duct Hangers (is spacing correct, installed level etc)
checkpoint | Duct jointing (Joints sealed, cleats fitted etc)
checkpoint | Fire Dampers installed in open position c/w access panel.
checkpoint | Sound attenuators installed
checkpoint | Filter box installed
checkpoint | Transfer ducts installed
section | Second Fix QA
checkpoint | Motorized dampers orientation to be installed correct way for sealing purpose
checkpoint | Access Panels to be installed as per drawing
checkpoint | All volume control dampers set fully open.
checkpoint | Butterfly and outlet dampers installed as per drawing and in open position.
checkpoint | Seismic bracing installed as per Drawing
section | Fit Off QA
checkpoint | Flexible ducting installed c/w supports.
checkpoint | Correct Equipment / Correct Grills / Diffuser Installed
checklist | QA - VRV Cassette |  |  |  |  | Yes | QA - VRV Cassette | e63466b7-2487-4245-9a77-c9cd70ad8e5a
section | Pre-Start VRV Cass
checkpoint | Area clear, access good, enough space for install
checkpoint | Pipework route to Indoor unit riser all clear.
section | First Fix VRV Cass
checkpoint | Pipework connected to BS Box/Outdoor and Indoor unit
checkpoint | Pipework Insulated complete length
checkpoint | Pipework supported including any seismic restraints
checkpoint | Indoor unit level, secure, vibration isolated and seismically restrained
checkpoint | Correct Indoor unit installed
checkpoint | Indoor unit serial no. recorded
checkpoint | Drain installed and insulated
checkpoint | Supply cable installed correctly, protected and secured
checkpoint | Interconnecting cables correctly installed, labelled and protected
checkpoint | Remote controller cable installed
checkpoint | Access Panel requirements are marked and given to builders
checkpoint | Plans marked up for As Builts
checkpoint | Indoor unit covered and protected (to prevent dust and debris)
checkpoint | Install Seismic Restraints
section | Second Fix VRV Cass
checkpoint | Face plate installed flush and square
checkpoint | Controller installed
checkpoint | Area left clean and tidy, fingerprints removed
checkpoint | Plant and controller labelled
checklist | QA - Fire Dampers |  |  |  |  | Yes | QA - Fire Dampers | fe7ec19f-64b0-40ca-9e2d-0b027eb5fb85
section | First Fix QA
checkpoint | Correct FD Installed
checkpoint | Access Panel installed
section | Second Fix QA
checkpoint | Drop Tested
checkpoint | Track is Clear
checkpoint | Fire damper info sticker is visible
checkpoint | Builder to Fire Sealed
checkpoint | Signed off
checklist | QA - Fans |  |  |  |  | Yes | QA - Fans | 1c386e62-6796-4e66-9779-8fa9f1d4d91c
section | Fans
checkpoint | Correct Equipment / plant installed
checkpoint | Mountings / springs installed
checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint | Model and serial numbers recorded
checkpoint | U/S of Fan heights correct as per Workshop Drawings.
section | E4M QA
checkpoint | Wiring First Fix Complete
checkpoint | Cable Tray Installed Correctly
checkpoint | Electrical Isolators installed in Correct location
checkpoint | Units Terminated
checkpoint | Temp Sensors and Controllers Installed
checkpoint | Units Tested and Running
checklist | QA - AHU |  |  |  |  | Yes | QA - AHU | 30b129f1-383d-492a-8828-610d76a3ed21
checkpoint | Safety covers installed
checkpoint | Unit fixed down
checkpoint | Access to unit is adequate
checkpoint | Fan wired
checklist | QA - Condensate Pumps |  |  |  |  | Yes | QA - Condensate Pumps | 3fdee09f-4dbe-4acd-b141-b78f7cff2bd4
checkpoint | Drain connections have hose clamps
checkpoint | Drain tube is installed and not kinked
checkpoint | Drain tube is secured
checkpoint | Pump is accessible
checkpoint | Pump is wired correct
checkpoint | Drain breather/overflow installed
checkpoint | Pump is installed correct
checkpoint | Drain tube is within limits of pump
checklist | QA - Chiller |  |  |  |  | Yes | QA - Chiller | 43027cef-139e-4cf5-9612-ef02b8145e3e
section | Chiller QA
checkpoint | Mounting Area/Platform Level
checkpoint | Power Cables Run
checkpoint | Comms Cables Run
checkpoint | Pipework Complete
checkpoint | External Valves installed as per plan
section | E4M QA
checkpoint | Isolator Installed
checkpoint | Power Cables Fit off and tested
checkpoint | Control Cables Fit off.
checklist | QA - VRV Outdoor Unit |  |  |  |  | Yes | QA - VRV Outdoor Unit | 59099ec3-ec22-4017-8fbf-59d718bfb752
section | Pre-Start VRV OU
checkpoint | Area/base ready for outdoor unit
checkpoint | Outdoor unit area accessible
checkpoint | Pipework route from OU to BS box/Indoor Unit all clear, penetrations complete
checkpoint | Area clear for BS Box installation
section | First Fix VRV OU
checkpoint | Outdoor unit brackets/feet/strut in place
checkpoint | Unit level, secure, bolted down, seismically restrained
checkpoint | Correct outdoor unit installed
checkpoint | Clearance under unit for cleaning
checkpoint | Pipework connected from OU unit to BS box/Indoor Units
checkpoint | Pipework Insulated
checkpoint | Pipework lengths measured for Refrigerant Charge
checkpoint | Insulation joins glued and taped
checkpoint | Pipework supported including any seismic restraints
checkpoint | BS Box level, secure and seismically restrained
checkpoint | Correct BS Box installed
checkpoint | BS Box serial no. recorded
checkpoint | Drain 1m from BS Box location by plumber
checkpoint | Drain installed and insulated
checkpoint | Supply cable installed correctly, labelled, protected and secured
checkpoint | Interconnecting cables correctly installed, labelled and protected
checkpoint | Remote controller cable installed
checkpoint | Access Panel requirements are marked and given to builders
checkpoint | Plans marked up for As Builts
section | Commission VRV OU
checkpoint | Access to OU unit is good
checkpoint | Access to BS Box is good
checkpoint | Drain tested
checkpoint | Access to Indoor units is good
checkpoint | Commissioned by Manufacturer
checkpoint | OU model and serial number(write in comments and take photo)
checkpoint | All plant labelled including OU/BS/Indoors/Controllers/Pipework
checklist | QA - General Electrical |  |  |  |  | Yes | QA - General Electrical | 69547254-817f-4a8e-9ba4-4a4b727ebc68
section | E4M First Fix
checkpoint | Catenary Wires secure with hangers as required
checkpoint | Heights marked for Flush boxes
checkpoint | Nogs installed as required
checkpoint | Framing For DB fixing
checkpoint | Cables labelled at DB
checkpoint | Cables secured with cable ties
checkpoint | Mechanical protection as required
checkpoint | Plans Marked For Cable Direction and Loops
section | E4M Fit Off
checkpoint | Cables terminated in DB as per schedule
checkpoint | Test cables and record results
checkpoint | COC Filled out
checkpoint | Cables labelled to and from
checkpoint | Central controller installed
checkpoint | Fire Relays Tested
checklist | QA - Cowls |  |  |  |  | Yes | QA - Cowls | 72f9df3b-e577-4cdd-b3a1-44801630baf2
checkpoint | Outside Air Roof Cowl Installed
checkpoint | Builder - Waterproof and Seal to be installed
checklist | QA - Extract Fan |  |  |  |  | Yes | QA - Extract Fan | 7bbc3d20-9da3-411c-9928-f88df86ee895
section | Pre-Start Ext Fan
checkpoint | Area clear, access good, enough space for install
checkpoint | Duct Route clear, Penetrations complete
checkpoint | Nogs/Supports in place
section | First Fix Ext Fan
checkpoint | Fan installed straight and level and correct orientation.
checkpoint | Fan or Cowl sealed to Upstand
checkpoint | Correct Fan installed
checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
checkpoint | Flexible ducts run straight/tight/well supported/secured close to grille location
checkpoint | Flexible ducts taped then cable tied
checkpoint | PIR cables run to DB
checkpoint | Supply cable installed correctly, labelled, protected and secured
checkpoint | Plans marked up for As Builts and 2nd fix grille locations
section | Second Fix Ext Fan
checkpoint | Grilles installed square and level
checkpoint | Flexible ducts taped then cable tied to grilles/boots
checkpoint | Boots sealed to grilles
checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
checkpoint | PIR fit off
checkpoint | Power fitted off
checkpoint | Area left clean and tidy, fingerprints removed
checkpoint | Plant labelled
section | Commission Ext Fan
checkpoint | Commissioning paperwork reviewed and accepted by Project Manager
checkpoint | Electrical testing complete
checkpoint | COC issued
checklist | QA - Split High Wall |  |  |  |  | Yes | QA - Split High Wall | 7f97b8ec-9380-426a-ae4f-35344d0bf7e8
section | Pre-Start SHW
checkpoint | Area clear, access good, enough space for install
checkpoint | Area/base ready for outdoor unit
checkpoint | Any required drains for outdoor unit in place
checkpoint | Pipework route all clear, penetrations complete
checkpoint | Nogs in place
section | First Fix SHW
checkpoint | Pipework Run and Insulated complete length
checkpoint | Drain installed
checkpoint | Supply cable installed correctly, protected and secured
checkpoint | Remote Controller cable installed if required
checkpoint | Interconnecting cables correctly installed and protected
section | Second Fix SHW
checkpoint | System pressure checked and still holding 1st fix pressure
checkpoint | Indoor unit secure, level and tight to wall
checkpoint | Correct Indoor unit installed
checkpoint | Outdoor unit secure and level
checkpoint | Correct Outdoor unit installed
checkpoint | Indoor unit serial no. recorded
checkpoint | Outdoor Unit serial no. recorded
checkpoint | Area left clean and tidy, fingerprints removed