## Checklists
Type | Name | Values | Prefix | Postfix | Usage Count | User Addable | Template Name
checklist | JHA - Job Hazard Analysis
section | Job details
checkpoint-no-status | Job details
date | Date:
textbox | Permit No.
textbox | Job No.
textbox | Site
textbox | Activity Location
textbox | Asset:
textbox | Work Details:
section | Prompts for Hazards - Mark all that apply.
checkpoint-no-status | Prompts for Hazards - Mark all that apply.
button | Sparks/Open flame | YES,NO
button | Disabled safety device(s) | YES,NO
button | Uneven surfaces | YES,NO
button | Fatigue, over-exertion | YES,NO
button | Crane movements | YES,NO
button | Moving/Rotating parts | YES,NO
button | Remote area, working alone | YES,NO
button | Conflicting work/SIMOPS | YES,NO
button | Electrical arc flash | YES,NO
button | Sharp objects/materials | YES,NO
button | Restricted/Difficult Entry/Exit | YES,NO
button | Overhead obstacles | YES,NO
button | Ignition sources (other) | YES,NO
button | Access/Egress | YES,NO
button | Water body | YES,NO
button | Live equipment | YES,NO
button | Slippery surfaces | YES,NO
button | Suspended loads | YES,NO
button | Hazardous substances (chemicals) | YES,NO
button | Use of non-intrinsically safe equipment | YES,NO
button | Weather extremes | YES,NO
button | Moving vehicles | YES,NO
button | Task related noise | YES,NO
button | Engulfment | YES,NO
button | General waste | YES,NO
button | Hazardous waste | YES,NO
button | Hazardous/toxic substance, fumes, gas | YES,NO
button | Flammable materials - Gas, liquids, solids | YES,NO
button | Reduced visibility, lighting | YES,NO
button | Electricity | YES,NO
button | Static electricity | YES,NO
button | Work at height | YES,NO
button | Underground services | YES,NO
button | O2 Deficiency/Excess | YES,NO
button | Temperature extremes | YES,NO
button | Heavy objects | YES,NO
button | Radiation | YES,NO
button | Potential energy - Tension/Compression | YES,NO
button | Flying particles/Dust/Objects | YES,NO
button | Vehicle entry | YES,NO
button | Exposure to process temperatures. | YES,NO
section | Prompts for Initial Consequences - Mark all that apply
checkpoint-no-status | Prompts for Initial Consequences - Mark all that apply
button | Falling/Dropped objects | YES,NO
button | Fall from height | YES,NO
button | Trip/Slip/Fall | YES,NO
button | Gas release | YES,NO
button | Pressure release | YES,NO
button | Struck by object | YES,NO
button | Exceeding tool limits | YES,NO
button | Overloading people | YES,NO
button | Unplanned shutdown | YES,NO
button | Exposure to O2 deficiency/excess | YES,NO
button | Exposure to hazardous substance | YES,NO
button | Entanglement | YES,NO
button | Flying objects | YES,NO
button | Loss of control | YES,NO
button | Loss of containment | YES,NO
button | Excess exposure to Emissions, dust, fumes, noise, fibres, heat | YES,NO
button | Loss of structural integrity | YES,NO
button | Equipment failure | YES,NO
button | Uncontrolled ignition source | YES,NO
button | Collision | YES,NO
button | Ignition/Fire | YES,NO
button | Back strain/Injury | YES,NO
button | Burns | YES,NO
button | Heat exhaustion | YES,NO
section | Initial controls - Mark all that apply.
checkpoint-no-status | Initial controls - Mark all that apply.
note | People controls | YES,NO
button | Safety/Fire watch person | YES,NO
button | Barriers/Flagging | YES,NO
button | Warning signs | YES,NO
note | Equipment controls | YES,NO
button | Master tags and locks | YES,NO
button | Scaffolding for access | YES,NO
button | Radio communication | YES,NO
note | Environmental controls | YES,NO
button | Ventilation | YES,NO
button | Lighting | YES,NO
button | Gas Testing | YES,NO
note | High risk controls | YES,NO
button | WSCS Work permit | YES,NO
button | WSCS Certificates | YES,NO
button | Critical lift/Fall protection plan | YES,NO
button | Specialised PPE | YES,NO
button | Spill kit | YES,NO
button | Fire extinguisher | YES,NO
section | Signatures
checkpoint-no-status | Signatures
textbox | Applicant name
signoff | Applicant signature
checklist | JHA - Job Step
section | Task Step - add task step for each individual task
checkpoint-no-status | Task Step - add task step for each individual task
date | Date:
textbox | Task step number (eg. Step 1, Step 2 etc):
textbox | Task details:
textbox | Hazards:
dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
textbox | Potential consequence:
textbox | Controls:
textbox | Recovery steps:
dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
checklist | Toolbox Meeting
section | Toolbox meeting
checkpoint-no-status | Toolbox meeting
date | Date:
textbox | Meeting location:
textbox | Meeting conducted by:
textbox | Meeting attendees:
textbox | Today's work scope/Hazards
textbox | Hazard controls:
signoff | PICWS Signoff
checklist | As-Built Drawings
section | As-Built Drawings - attach scanned documents
checkpoint-no-status | As-Built Drawings - attach scanned documents
textbox | Drawing no.
checklist-flat | Cable Test Record
checkpoint | Upload completed ITR scans
checklist-flat | Certificate of compliance (COC)
checkpoint | Please upload Certificate of Compliance here when complete (COC)
checklist-flat | Record of Inspection (ROI)
checkpoint | Please upload Record of Inspection here when complete (ROI)
checklist | ITR-CL-1-100 General Electrical Equipment
section | General Electrical Equipment
checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint | No mechanical damage and paintwork in good condition.
checkpoint | Installation is clean and tidy
checkpoint | Mounting arrangement correct
checkpoint | All internal cabling and wiring correctly installed and labelled.
checkpoint | External cabling is correctly installed and labelled.
checkpoint | Check that Equipment is correctly earthed.
checkpoint | Check gland, plate, frame & door earth continuity
checkpoint | All spare entries blanked off with correct plugs.
checkpoint | Check item is suitably rated for area (E.g. IP rating, Ex rating)
checkpoint | Conforms to Specifications and Drawings.
checkpoint | As-builts complete.
section | Electrical Checks
checkpoint | IR and Earth tests
textbox | Insulation Resistance (P/N to E) |  |  | MegaOhms
textbox | Earth Continuity: |  |  | Ohms
textbox | Earth Bonding: |  |  | Ohms
textbox | Other checks:
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-101 Conduit, Ducting, Unistrut, Cable Tray & Ladder Installation
section | Conduit/Ducting Installation Below Ground
checkpoint | Check equipment details are correct and in accordance with the data sheet and equipment schedule.
checkpoint | Check conduit cable enclosure installation is as-per design, layout drawings and specifications.
checkpoint | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed.
checkpoint | Confirm that there are no obstructions, and that the installation will be accessible for maintenance.
checkpoint | Check all fixings are tight and secure.
checkpoint | Check bends do not exceed the maximum cable bend radius.
section | Cable Supports Above Ground
checkpoint | Verify cable support has been installed as per relevant drawings.
checkpoint | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection.
checkpoint | All covers fitted if applicable.
checkpoint | Check cable support structures are adequately fixed and present no hazard to personnel.
checkpoint | Correct cable support size and type used.
checkpoint | Welded support brackets have been wire-brushed and painted to completion.
checkpoint | Splice plates, barriers, earthing system secure.
checkpoint | Trays / ladders, supports, brackets not interfering with other disciplines.
checkpoint | Check bends do not exceed the maximum cable bending radius.
checkpoint | Cables have adequate mechanical protection as and where required.
checkpoint | Inspect for system rigidity, and check levels to correct plane.
checkpoint | Earth bonding straps have been fitted to any sections that are split, hinged or flexible.
checkpoint | Tray bonded to structure at correct locations.
textbox | Earth bonding continuity tested – record result: |  |  | Ohms
section | Cable Transits
checkpoint | Transit frame installed as per drawings.
checkpoint | Transit frame identification marked correctly and visible.
checkpoint | Frame correctly packed with correct sized blocks and infills.
checkpoint | Correct stay plates fitted (non-ferrous for single core power cables.)
checkpoint | Rated insulation installed to transit (where required.)
checkpoint | Cables entering and leaving transits adequately supported and protected.
checkpoint | Cables pass through frames without strain on blocks.
checkpoint | All cables identified on both sides of transit and visible.
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-102 Distribution Board Installation
section | Distribution Board Installation
checkpoint | Inspect for mechanical damage from freight and handling
checkpoint | Check mounting arrangement is adequate.
checkpoint | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct.
checkpoint | Check IP rating is correct for location.
textbox | IP Rating:
checkpoint | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order.
checkpoint | Confirm main isolator operates with associated switches and auxiliaries
checkpoint | Confirm main isolator operates all active conductors
checkpoint | Confirm main isolator and sub-circuit MCB’s can be padlocked open if required.
checkpoint | Check number and rating of sub-circuits as per design and specifications.
checkpoint | Ensure different Voltage segregation is correct.
checkpoint | Heaters installed and functioning.
textbox | Record IR of heater circuit |  |  | MegaOhms
checkpoint | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar.
checkpoint | Check internal cables properly terminated and labelled
checkpoint | DB properly labelled, sub circuit MCB correct rating and application
checkpoint | Check cable penetration is correct. (E.g. sealed correctly, correct size/type of glands)
checkpoint | Active, Neutral and Earth bar properly identified and labelled
checkpoint | DB legend card correct and updated, As-built
checkpoint | Confirm panel is readily accessible for inspection and maintenance.
checkpoint | Confirm panel is clean and tidy
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist-flat | ITR-CL-1-103 Schedule of Test Results DB
checkpoint | Upload completed ITR scans
checklist | ITR-CL-1-104 Cable Installation
section | Cable Installation
checkpoint | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule.
checkpoint | Check dressing/cleating.
checkpoint | Check cable for damage.
checkpoint | Check cable cores correctly identified and labelled.
checkpoint | Cable terminated with correct lugs and crimped with the correct die.
checkpoint | Check that cable phasing is correct and point-to-point each core for continuity.
checkpoint | Check Armour/Screen correctly made off.
checkpoint | Check armour continuity /earthing is maintained by the correct use of serrated washers and/or earth tags.
checkpoint | Glanding/Locknuts correctly installed.
section | Gland type - from:
checkpoint-no-status | Gland type - from:
textbox | Haz. Area Rating:
textbox | Haz. Area Cert Details:
section | Gland type - to:
checkpoint-no-status | Gland type - to:
textbox | Haz. Area Rating:
textbox | Haz. Area Cert Details.
section | Electrical Testing
checkpoint | IR Testing - LV Cables
label | (Test voltage 1,000 VDC for LV cables and 5KVDC for HV cables)
textbox | L1 – Earth |  |  | MegaOhms
textbox | L2 – Earth |  |  | MegaOhms
textbox | L3 – Earth |  |  | MegaOhms
textbox | L1 – L2 |  |  | MegaOhms
textbox | L1 – L3 |  |  | MegaOhms
textbox | L2 – L3 |  |  | MegaOhms
textbox | N – Earth |  |  | MegaOhms
checkpoint | IR Testing - Multiple conductor cables (Record lowest readings)
textbox | Between Conductors |  |  | MegaOhms
textbox | Conductors to GND |  |  | MegaOhms
textbox | Measure gland body continuity to earth. (Max 0.1 Ohm) |  |  | Ohm
checkpoint | Confirm cable routing and segregation is correct.
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-105 Control Panel
section | Control Panel
checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint | Check holding down/mounting arrangement is correct.
checkpoint | Check for mechanical damage.
checkpoint | Check that panel is correctly earthed.
textbox | Check earth continuity between panel and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint | Check tightness of circuit connections.
checkpoint | All internal cabling and wiring is correctly numbered, colour coded and terminated
checkpoint | Ammeter scale and current transformer correct.
checkpoint | Check internals for cleanliness.
checkpoint | Check manual operation of selector switches, MCB, push buttons, etc.
checkpoint | Incoming cables correctly glanded, terminated and labelled.
checkpoint | Unused holes are sealed.
checkpoint | Heaters correctly installed.
textbox | Heater circuit Insulation Resistance: |  |  | MegaOhm
checkpoint | Fuse rating correct.
checkpoint | Padlocking facilities correct (if applicable).
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-106 Junction Box
section | Junction Box
checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint | Check holding down/mounting arrangement and accessibility for maintenance.
checkpoint | Check for mechanical damage
checkpoint | Check that Junction box is correctly earthed.
textbox | Test and confirm the earth resistance between junction box and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint | Check all internal cabling and wiring is correct and tight, including segregation (e.g. IS to NON IS circuits).
checkpoint | Check cables for Voltage segregation. Ensure clearance, labelling, colour coding is to standard
checkpoint | Incoming/Outgoing cables are glanded and terminated correctly
checkpoint | Spare entries plugged correctly.
checkpoint | Check internals for cleanliness
checkpoint | All cover bolts and gasket undamaged
checkpoint | Verify ingress protection is suitable for area (IP rating)
textbox | IP Rating:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-107 Heat Tracing Circuit
section | Heat Tracing Circuit
checkpoint | Circuit installed, connected & identified according to design drawings.
checkpoint | End caps and connection kits correctly installed.
checkpoint | All junction boxes properly supported, and all cables protected against sharp edges.
checkpoint | Cable termination and glanding at all junction boxes correct.
checkpoint | All spare entries blanked off correctly.
checkpoint | Insulation resistance to earth after installation:
textbox | Insulation resistance: |  |  | MegaOhms
checkpoint | Phase to Neutral resistance
textbox | Insulation resistance: |  |  | MegaOhms
checkpoint | Equipment certification meets the area classification requirements.
checkpoint | Confirm warning labels are fixed on outside of pipe lagging
checkpoint | Check correct rating of protection device against design drawings.
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-108 Electrical Switch Rooms
section | Electrical Switch Rooms
checkpoint | Substation construction finished
checkpoint | All floor, wall & ceiling penetrations sealed.
checkpoint | Danger, warning & resuscitation signs installed
checkpoint | All equipment installed
checkpoint | Lighting & general power installation complete
checkpoint | All earth busbars installed satisfactorily & connections tight
checkpoint | All telecommunication equipment is installed & operational
checkpoint | Smoke / Heat detectors installed (Including Vesda / Alarm Panel)
checkpoint | Substation fire alarm panel installed
checkpoint | HVAC equipment installed & operational
checkpoint | Illuminated exit signs installed & operational
checkpoint | Hand-held fire extinguishers installed with correct type available
checkpoint | All doors and locks operational (including emergency)
checkpoint | All keys available and handed to Commissioning E&I Superintendent
checkpoint | All safety equipment supplied – rubber mats, voltage sticks etc
checkpoint | Single line diagram detailing main power is fitted to wall
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-109 Electrical Equipment Package
section | Electrical Equipment Package
checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint | Check equipment is correctly rated for the area.
checkpoint | Check if package is complete with all accessories.
checkpoint | No mechanical damage and paintwork in good condition.
checkpoint | All transportation supports, stops and fastenings removed.
checkpoint | Package fixing down bolts/shims/washers installed and tensioned.
checkpoint | Check package location.
checkpoint | Check package is installed on a level plane.
checkpoint | External cabling (if required) correctly installed.
checkpoint | Internal equipment installed and all tests complete and accepted.
checkpoint | Verify package using vendor and/or project P&IDs.
checkpoint | Check that equipment is correctly earthed.
textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint | All spare entries blanked off with correct plugs.
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-110 Generator Package (LV)
section | Generator Package (LV)
checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint | No mechanical damage and paintwork in good condition.
checkpoint | Check terminal boxes and glanding correct.
checkpoint | Check earthing is correct.
textbox | Test and confirm the generator earth to local earth system is <1.0 Ohm |  |  | Ohm
checkpoint | Instruments correctly installed.
checkpoint | Heaters correctly installed.
textbox | Heater circuit Insulation Resistance: |  |  | MegaOhms
checkpoint | Check unit for cleanliness.
checkpoint | Check manual operation of selector switches, MCB, push buttons etc.
checkpoint | External cabling correctly installed.
checkpoint | Protection of live parts adequate.
checkpoint | Main terminal box complete and terminations correct torque.
checkpoint | Ensure direction of rotation is clearly marked.
checkpoint | Check gasket and seals are not damaged.
checkpoint | Unused cable entries are correctly sealed.
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-111 Electrical Earthing
section | Earthing System
checkpoint-no-status | Earthing System
textbox | Electrode type
textbox | Electrode length/size
textbox | Location of Electrodes
textbox | Method of installing electrode
textbox | Method of attaching to electrode (e.g Clamp, Cad Weld, Lug & Bolt)
textbox | Number of electrodes
section | General Items
checkpoint | Confirm earth grid layout
checkpoint | Ensure grid layout is in accordance with design drawings
checkpoint | Record number of grid interconnections
checkpoint | Ensure all metalwork is earthed as required
checkpoint | Check welding of earth bosses and associated surface finish
checkpoint | Ensure that earth cables/conductors have adequate mechanical protection i.e. conduits, kick-plates, PVC duct through concrete etc. at points of high exposure.
checkpoint | Ensure that brazing or welding of all joints has been completed correctly.
checkpoint | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, Cad (thermal) welds and earth bosses
checkpoint | Ensure that earth electrodes are located within a protected, covered and identified surround.
checkpoint | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating.
checkpoint | MEN Link Installed (If applicable)
section | Earthing Conductors
checkpoint | Ensure that earthing conductor size is correct in accordance with approved installation drawings.
checkpoint | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly.
checkpoint | Check terminations to ensure that all connections are correct, clean, greased and tight.
checkpoint | Check that all bi-metal connections have been performed correctly to manufacturer's requirements.
checkpoint | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar.
checkpoint | Ensure that earth cable identification markings are in place.
checkpoint | Ensure that earth connections are not multi-coiled or 'pig-tailed' but are terminated as straight as possible.
section | Earth Bar Installation
checkpoint | Check for correct assembly of equipment
checkpoint | Check fixings and mounting points conform to project specification and are secure
checkpoint | Check for equipment levels and alignment
section | Earth System Testing
checkpoint | Using an Earth Resistance tester, measure earth resistance between electrodes or main earth bars & the earth body.
textbox | Record results:
checkpoint | Measure earth continuity from each earth point and/or equipment earth frame to the nearest electrode or main earth bar
label | Note: Sketch a layout of earth electrodes showing electrode numbers and distances and attach below
checkpoint | Earth Grid Test Results (electrodes connected)
textbox | HV Earth grid:
textbox | LV Earth grid:
textbox | Combined HV/LV Earth grids:
textbox | Instrument Earth:
checkpoint | Earth Resistivity Tests
textbox | From (Main Earth Bar or Auxiliary Earth Point): |  |  | To Earth Body
textbox | Result: |  |  | Ohms
textbox | From (Main Earth Bar or Auxiliary Earth Point): |  |  | To Earth Body
textbox | Result: |  |  | Ohms
checkpoint | Earth Continuity Tests
textbox | From: (Main Earth Bar Location)
textbox | To: (Earth Electrode number/description)
textbox | Record Resistance: |  |  | Ohms
textbox | From: (Main Earth Bar Location)
textbox | To: (Earth Electrode number/description)
textbox | Record Resistance: |  |  | Ohms
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-112 Motors
section | Inspection
checkpoint | Tag number correct
checkpoint | Area Classification correct
textbox | IP Rating: |  | IP
textbox | Hazardous area cert:
checkpoint | Electrical Connections correct
button | Space heater | YES,NO
textbox | Space heater Volts:
textbox | Space heater Power (Watts) |  |  | W
checkpoint | General condition
section | Nameplate Details
checkpoint-no-status | Nameplate Details
textbox | Tag No:
textbox | Manufacturer:
textbox | Motor Serial Number:
dropdown | Phases: | Single-Phase, Three-Phase
textbox | Frame:
textbox | Enclosure:
textbox | Voltage: |  |  | V
textbox | Current: |  |  | A
textbox | kW: |  |  | kW
textbox | Speed:
textbox | PF:
textbox | No. of Poles:
textbox | Insulation Class:
dropdown | Rotation direction (looking down shaft) | Clockwise, Counter-Clockwise
checkpoint | Bearing Specs
textbox | Drive end
textbox | Non Drive end
section | Checklist items
checkpoint | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets
checkpoint | Check Equipment and Nameplate details are correct in accordance with the data sheet.
checkpoint | Identification Tag and Rotation Plate correctly fitted
checkpoint | Motor electrical coupling (Delta /Star) as per voltage is correct.
checkpoint | Check for mechanical condition, air ducts and fan free of debris
checkpoint | Correct glanding for area classification.
checkpoint | Holding down bolts fitted correctly.
checkpoint | Check bearing lubrication.
checkpoint | Check free rotation with driven equipment uncoupled
checkpoint | Cable(s) correctly terminated, labelled and colour identification
checkpoint | Terminations/ connections torqued correctly to data sheets.
section | Motor Installation Testing
checkpoint | LV Motor winding insulation resistance with cables disconnected
checkpoint | 1 Minute
textbox | Winding "U" |  |  | MegaOhms
textbox | Winding "V" |  |  | MegaOhms
textbox | Winding "W" |  |  | MegaOhms
checkpoint | 10 Minutes
textbox | Winding "U" |  |  | MegaOhms
textbox | Winding "V" |  |  | MegaOhms
textbox | Winding "W" |  |  | MegaOhms
checkpoint | Motor continuity between windings
textbox | U1 - U2 |  |  | Ohms
textbox | V1 - V2 |  |  | Ohms
textbox | W1 - W2 |  |  | Ohms
checkpoint | Space heater continuity & resistance check
textbox | Continuity: |  |  | Ohms
textbox | Insulation Resistance: |  |  | MegaOhms
checkpoint | Thermostat or RTD wiring resistance check
textbox | Resistance: |  |  | Ohms
checkpoint | Check motor is earthed correctly and record motor earth bond:
textbox | External bond continuity: |  |  | Ohms
section | Additional checks
checkpoint | Visual Inspections
checkpoint | Winding temperature detector
checkpoint | Air temp detectors
checkpoint | Bearing temp indicators
checkpoint | Vibration Monitors
checkpoint | Condensation detector
checkpoint | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable)
checkpoint | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable)
checkpoint | Installation conforms to specification and drawings
checkpoint | As-Builts complete
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-113 Motor Control
section | General Motor Control
checkpoint | Check all labelling and warning signs are correctly installed and visible
checkpoint | Check control equipment is clean and free from dust, debris and tools
checkpoint | Check preservation and transit items are removed
checkpoint | Check there are no mechanical damage and no damage to paintwork
checkpoint | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor
checkpoint | Check all cabling to control gear and motor is undamaged, supported and tidy
checkpoint | Check earthing bar and connections are correct and tight
checkpoint | Check incoming and outgoing power cables are terminated and glanded correctly
checkpoint | Check phase identification on power cables is correct and visible
checkpoint | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque
checkpoint | Check all other nuts and bolts are tight
checkpoint | Check spare gland entries are plugged with correct rated plugs
checkpoint | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected
section | Variable Speed Drives (VSD)
checkpoint | Record VSD Nameplate Details
textbox | Volts (Input) |  |  | V
textbox | Amps (Input) |  |  | A
textbox | Amps (Output) |  |  | A
checkpoint | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input)
checkpoint | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used.
checkpoint | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged
checkpoint | Check control signal cables use twisted pairs
checkpoint | Check control signal and profibus cables shield is earthed at one end
checkpoint | Check analogue and digital signals are run in separate cables
section | Check that voltage segregation is applied along the length of cables:
checkpoint | Distance between input power and motor cable >300mm
checkpoint | Distance between input power and control signal cable >200mm
checkpoint | Distance between motor cable and control signal cable >500mm
checkpoint | Check there is no power factor compensation capacitors installed on the outgoing power cables
checkpoint | Check gland plates with single core power cables are non-magnetic at VSD and LIS
checkpoint | Check mains voltage cannot be applied to the VSD output by means of a bypass connection
checkpoint | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC
checkpoint | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position)
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-114 UPS Installation
section | UPS Installation
checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint | Check for mechanical damage.
checkpoint | Panel IP rating is correct:
textbox | IP Rating: |  | IP
checkpoint | Holding down arrangement and seat alignment correct.
checkpoint | Panels aligned correctly.
checkpoint | Earth alignment to vendor specification & connecting link bolts torqued to the manufacturers recommendations & marked.
checkpoint | External bonding correct
checkpoint | Bus bar alignment to vendor specifications & connecting link bolts torqued to the manufacturers recommendations & marked.
textbox | Nm.
checkpoint | Phase identification correct.
checkpoint | Instrument, indication lamps & interlocks correct.
checkpoint | Main switches, contactors, fuses etc. sized & identified correctly as per Single-
checkpoint | Line Drawings.
checkpoint | Check main isolator switch operation.
checkpoint | Check bypass isolator switch operation.
checkpoint | Check DC UPS battery isolator switch operation.
checkpoint | COM Interface & Mod Link.
checkpoint | Padlocking facilities correct.
checkpoint | Check internals for cleanliness.
checkpoint | Check manual operation of selector switch, MCB, push button, etc.
checkpoint | Incoming cable correctly installed, terminated & supported.
checkpoint | Unused cable entries sealed.
checkpoint | All internal cabling & wiring neat, correct & tight.
checkpoint | Heaters correctly installed.
checkpoint | Fans correctly installed.
checkpoint | Verify continuity of earth bar to frame
textbox | Earth continuity: |  |  | Ohms
checkpoint | Check Busbar Insulation resistance between Phases & Phases & Earth (690V-2500VDC, 400V -1000VDC)
textbox | L3-L2 |  |  | MegaOhms
textbox | L3-L1 |  |  | MegaOhms
textbox | L3-N |  |  | MegaOhms
textbox | L2-L1 |  |  | MegaOhms
textbox | L2-N |  |  | MegaOhms
textbox | L2-E |  |  | MegaOhms
textbox | L1-N |  |  | MegaOhms
textbox | L1-E |  |  | MegaOhms
textbox | N-E |  |  | MegaOhms
checkpoint | Drawings marked up with relevant changes
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-115 Lightning Protection
section | Lightning protection checks
checkpoint-no-status | Lightning protection checks
note | These checks shall be conducted in accordance with the requirements of AS/NZS 1768:2007
checkpoint | Check lightning conductor is 2 metres or more above the entire protected area
checkpoint | Check the materials and equipment used for the down conductors are suitable
checkpoint | Check the down conductors are routed, located and electrically bonded as required
checkpoint | Check all installed components are firmly secured
checkpoint | Check the method of protection against electric shock, including the measurement of distances
checkpoint | Check the resistance of all connections at the location of the connection. The resistance of each connection shall not exceed 0.05 Ohm
Checkpoint | Earth termination system resistance is correct
textbox | Resistance value: |  |  | Ohm
checkpoint | Insulation resistance of the electrical installation
textbox | IR |  |  | MegaOhms
checkpoint | Continuity of main and supplementary bonding
textbox | Main bonding: |  |  | Ohm
textbox | Supplementary bonding: |  |  | Ohm
checkpoint | Check earth termination systems are interconnected
checkpoint | Check isolating and switching devices correctly located
checkpoint | Check warning signs and diagrams are installed
checkpoint | Check accessibility for operation and maintenance
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-116 Fire and Gas Detection Alarms
section | Checklist items
checkpoint-no-status | Checklist items
textbox | Manufacturer
textbox | Make and Model
textbox | Type
checkpoint | Labelling/Number correct
checkpoint | Component & Type / Model correct
checkpoint | Cable connection & termination correct
checkpoint | Mechanical damage
checkpoint | Glanding condition
checkpoint | E.O.L Installation
checkpoint | Installation of Test tubing
checkpoint | Location correct
checkpoint | Detection Path Clear
section | Inspection
checkpoint | Tag No. Correct
textbox | Tag No:
textbox | RX Tag No:
checkpoint | Area Classification correct
textbox | Hazardous Area Certificate:
textbox | Detector Type:
textbox | Gas Type:
checkpoint | Body Material Correct:
checkpoint | General Condition Satisfactory
textbox | Supply Voltage:
textbox | Output Signal:
section | Functional Check
checkpoint | Self Test
checkpoint | Alarm Operation
checkpoint | Fault Relay Operation
textbox | Measured output (clear path)
textbox | Measured output (blocked path)
textbox | Measured output (filter in place)
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-117 Instrument Tubing Installation
section | Information
checkpoint-no-status | Information
textbox | Equipment:
textbox | Location:
textbox | Tag Numbers:
textbox | Process Fluid:
textbox | Reference Drawings:
textbox | Max Process Pressure:
textbox | Max Supply Pressure:
textbox | Max Signal Pressure:
textbox | Process Temperature:
textbox | Other:
button | Inspection | Yes, No
textbox | Percentage of installed items to be checked:
section | Checks Pre-Installation
checkpoint | Tubing connection drawings and details available
checkpoint | Client site specific changes noted, agreed and sketched
checkpoint | Tube material type, size, gauge and standard confirmed and available
checkpoint | Tube fitting size and type confirmed and available
checkpoint | Torque wrench - Current calibration certificate
section | Checks During and Post-Installation
checkpoint | Correct thread compatibility and engagement
checkpoint | Correct thread tape and sealant used on fittings
checkpoint | Check fitting ferrule orientation and confirm prior to connection
checkpoint | Tube installation is in compliance with the client specification.
label | (Supports, bracketry, slope, expansion, vibration, access, cables)
checkpoint | Tube bent correctly, sufficient straight section into fitting
checkpoint | Tube cut clean and straight, de-burred, reamed, and blown through
checkpoint | Depth insertion tool used; witness mark visible at all stages of process
checkpoint | Tube fitting hexes marked to ensure correct swage tightness
checkpoint | Random check with No-Go gap gauge
checkpoint | In service leak test performed and passed
checkpoint | Fitting completion tag completed and applied to each fitting
note | Refer to Swagelok book for tube/thread size pressure ratings
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-118 Instrument Pressure/Leak Test
section | Checklist items
checkpoint | Tube identification correct
checkpoint | Check mechanical damage
checkpoint | Flow direction and instrument orientation correct
checkpoint | Tubing installed correctly
checkpoint | Tubing size
section | Testing
checkpoint-no-status | Testing
note | Verify test pressure and medium is correct per project and manufacture specification prior to test
dropdown | Test fluid: | Air, N2, Water, Hydro-oil, Other
textbox | Test pressure:
textbox | Max design pressure:
dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
textbox | Duration: |  |  | Minutes
checkpoint | Confirm all impulse lines have been drained and cleaned
checkpoint | Confirm any temporary test connections, valve etc. are rated for the intended test.
checkpoint | Confirm pneumatic, test gas and aspirator lines have been blown clear.
checkpoint | Check hydraulic lines flushed to project specification.
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation)
section | Equipment
checkpoint | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No.
checkpoint | Equipment checked for additional items as applicable
section | Valve
checkpoint-no-status | Valve
textbox | Size:
textbox | Flange type:
checkpoint | Material certification correct
checkpoint | Trim material correct
textbox | Rating:
textbox | Service:
checkpoint | Body material correct
textbox | Leakage class:
section | Actuator
checkpoint-no-status | Actuator
textbox | Input range: |  |  | kPa
checkpoint | Failure action
checkpoint | Hand wheel operation correct
section | Positioner
checkpoint-no-status | Positioner
textbox | Signal range
textbox | Output range
section | I/P Converter
checkpoint-no-status | I/P Converter
textbox | Signal range
textbox | Output range
section | Filter/Regulator/On-Off Valve
checkpoint-no-status | Filter/Regulator/On-Off Valve
textbox | Range |  |  | kPa
textbox | Pressure setting |  |  | kPa
checkpoint | Stroke Time
textbox | Open |  |  | sec
textbox | Close |  |  | sec
checkpoint | Open/Close times conform to commissioning specifications
section | Fail Action
checkpoint-no-status | Fail Action
dropdown | Electrical Fail Action | FO, FC, FL
dropdown | Motive Force | FO, FC, FL
section | Valve Field Calibration and Hysteresis Check
checkpoint | Confirm test equipment is within calibration period prior to testing
note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
note | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100%
section | Proximity Detectors
checkpoint | Open switch set
checkpoint | Open switch mode setting correct
checkpoint | Closed switch set
checkpoint | Closed switch mode setting correct
checkpoint | Electrical connections correct
checkpoint | Electrical certification correct
section | Solenoid Valve
checkpoint | Operation correct
checkpoint | Electrical connections correct
checkpoint | Electrical certification correct
textbox | Voltage: |  |  | V
checkpoint | Pneumatic connections correct
textbox | Pneumatic pressure |  |  | kPa
section | Pilot Valve
checkpoint | Pneumatic connections correct
checkpoint | Operation correct
checkpoint | Action/Lockup
section | Hydraulic Actuator
checkpoint-no-status | Hydraulic Actuator
textbox | Working pressure
textbox | Manifold pressure
textbox | Fluid type
checkpoint | Hydraulic connections correct
textbox | Regulator pressure setting
checkpoint | Pilot operation correct
section | Accumulator
checkpoint | N2 Charge required
textbox | N2 Pre-charge pressure
textbox | Pressure switch setting
textbox | Working pressure
textbox | Output range
checkpoint | Volume tank & check valve installed correctly
section | Electric Actuator
checkpoint-no-status | Electric Actuator
textbox | Voltage:
textbox | Electrical certification correct
textbox | Electrical connections correct
textbox | Remote operation correct
textbox | Local hand operation correct
textbox | Torque switches and travel stops set
section | Miscellaneous Equipment
checkpoint-no-status | Miscellaneous Equipment
textbox | Description
textbox | Manufacturer
textbox | Model No:
textbox | Serial No:
textbox | Range:
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation)
section | Equipment
checkpoint | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No.
checkpoint | Equipment checked for additional items as applicable
checkpoint | Complete ITR-CL-1-121A and attach
section | Valve
checkpoint-no-status | Valve
textbox | Size:
textbox | Flange type:
checkpoint | Material certification correct
checkpoint | Trim material correct
textbox | Rating:
textbox | Service:
checkpoint | Body material correct
textbox | Leakage class:
section | Actuator
checkpoint-no-status | Actuator
textbox | Input range:
checkpoint | Failure action
checkpoint | Hand wheel operation correct
section | Positioner
checkpoint-no-status | Positioner
textbox | Signal range
textbox | Output range
section | I/P Converter
checkpoint-no-status | I/P Converter
textbox | Signal range
textbox | Output range
section | Filter/Regulator
checkpoint-no-status | Filter/Regulator
textbox | Range |  |  | kPa
textbox | Pressure setting |  |  | kPa
section | Fail Action
checkpoint-no-status | Fail Action
dropdown | Electrical Fail Action | FO, FC, FL
dropdown | Motive Force | FO, FC, FL
section | Proximity Detectors
checkpoint | Open switch set
checkpoint | Open switch mode setting correct
checkpoint | Closed switch set
checkpoint | Closed switch mode setting correct
checkpoint | Electrical connections correct
checkpoint | Electrical certification correct
section | Solenoid Valve
checkpoint | Operation correct
checkpoint | Electrical connections correct
checkpoint | Electrical certification correct
textbox | Voltage: |  |  | V
checkpoint | Pneumatic connections correct
textbox | Pneumatic pressure |  |  | kPa
section | Pilot Valve
checkpoint | Pneumatic connections correct
checkpoint | Operation correct
checkpoint | Action/Lockup
section | Hydraulic Actuator
checkpoint-no-status | Hydraulic Actuator
textbox | Working pressure
textbox | Manifold pressure
textbox | Fluid type
checkpoint | Hydraulic connections correct
textbox | Regulator pressure setting
checkpoint | Pilot operation correct
section | Accumulator
checkpoint | N2 Charge required
textbox | N2 Pre-charge pressure
textbox | Pressure switch setting
textbox | Working pressure
textbox | Output range
checkpoint | Volume tank & check valve installed correctly
section | Electric Actuator
checkpoint-no-status | Electric Actuator
textbox | Voltage:
textbox | Electrical certification correct
textbox | Electrical connections correct
textbox | Remote operation correct
textbox | Local hand operation correct
textbox | Torque switches and travel stops set
section | Miscellaneous Equipment
checkpoint-no-status | Miscellaneous Equipment
textbox | Description
textbox | Manufacturer
textbox | Model No:
textbox | Serial No:
textbox | Range:
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-121 Instrument Installation
section | Checklist items
checkpoint | Check instrument nameplate details are correct in accordance with instrument index
textbox | Make:
textbox | Model:
textbox | Serial No:
checkpoint | Ingress protection is suitable for area
textbox | IP rating:
checkpoint | Instrument rating is correct for hazardous area
textbox | Haz Rating:
checkpoint | Instrument mounted correctly, elevation correct and free from vibration
checkpoint | Instrument is accessible for maintenance and clear of obstruction
checkpoint | Vent lines are directed into a safe area
checkpoint | Cable glands rated and installed correctly. Spare entries plugged with correctly rated plug
checkpoint | Impulse, hydraulic, pneumatics, lines and air headers correctly installed and supported
checkpoint | Instrument earthed according to client specification
checkpoint | Relevant ITRs for type of instrument completed in conjunction with this (if applicable)
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-122 Instrument Calibration
section | Required Data
checkpoint-no-status | Required Data
textbox | Type and Size:
textbox | Make:
textbox | Serial No:
textbox | Instrument Type:
textbox | Instrument designation/equipment no
textbox | Calibration interval
textbox | Calibration method
textbox | Calibrated at
section | Instrument Power Supply
checkpoint-no-status | Instrument Power Supply
dropdown | Supply type | VAC, 2 Wire DC, Other, None
textbox | Supply value:
checkpoint | Calibration sheet completed and attached below
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-123 Instrument Pre-Commissioning
section | Checklist items
checkpoint | Verify transmitter loop connection - Remove wre on transmitter and confirm at Control System interface
checkpoint | Relevant individual control system/ESD loops have been checked and test sheets completed
section | Analogue Input:
checkpoint-no-status | Analogue Input:
textbox | Input range & units:
textbox | Indication range & units:
checkpoint | 0% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint | 25% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint | 50% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint | 75% Rising
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint | 100% Peak
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint | 75% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint | 50% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint | 25% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
checkpoint | 0% Falling
textbox | Input Signal:
textbox | Control Interface Indication:
section | Digital Input/Analogue Alarm Trip Points
checkpoint | Alarm Lo:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint | Alarm Lo-Lo:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint | Alarm Hi:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint | Alarm Hi-Hi:
textbox | Alarm setting
textbox | Measured Alarm Point
textbox | Filter/Time Delay
textbox | Result
checkpoint | Control loop set points correct:
textbox | Set Point 1:
textbox | Set Point 2:
textbox | Set Point 3:
textbox | Set Point 4:
section | Startup, Shutdown and Override functions
checkpoint | Control system graphic display
checkpoint | Control system point display
checkpoint | ESD graphic display
checkpoint | Alarm Recording and Text
section | Additional checks
checkpoint | Control system display and alarms are correct as per control functions
checkpoint | Transmitter fail direction and burnout are to spec (Upscale/Downscale)
checkpoint | Switch action verified, including power loss
checkpoint | Drawings, documents and As-Builts scanned and attached
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-124 Commissioning Instruments
section | Required Data
checkpoint-no-status | Required Data
textbox | Instrument range:
checkpoint | Installation complete
checkpoint | Point-to-point
checkpoint | Haz. Inspected
checkpoint | Tag correct
checkpoint | Hook-up correct
section | Alarms & Set points
checkpoint | Alarm Lo
textbox | Activated:
checkpoint | Alarm Lo-Lo
textbox | Activated:
checkpoint | Alarm Hi
textbox | Activated:
checkpoint | Alarm Hi-Hi
textbox | Activated:
checkpoint | Set Point 1
textbox | Activated:
checkpoint | Set Point 2
textbox | Activated:
checkpoint | Set Point 3
textbox | Activated:
checkpoint | Set Point 4
textbox | Activated:
section | Calibration settings
checkpoint-no-status | Calibration settings
textbox | Zero
textbox | Range
textbox | Other (Specify)
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-125 Cone and Thread Tubing Installation
section | General Data
checkpoint-no-status | General Data
textbox | Location:
textbox | Duty:
textbox | Reference Drawings:
textbox | Hook-up drawing:
textbox | Related instrument tag no:
textbox | Tube diameter and wall thickness:
textbox | Instrument location drawing:
section | Cone and Thread installation - Stainless fittings
checkpoint | Correct thread compatibility and engagement
checkpoint | Correct thread lubricant used on fittings
checkpoint | Check fitting collar prior to connection - 1 to 2 threads visible at cone
checkpoint | Tube installation follows the client specification.
label | (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables)
checkpoint | Tube bent correctly, sufficient straight section into fitting
checkpoint | Tube cut clean and straight, de-burred, reamed, and blown through
checkpoint | Lubricate collar, cone and gland thread at assembly to prevent galling
checkpoint | Correct Tube nut used for the right sized tube
checkpoint | Ensure No thread tape or sealant are used on tube nuts
checkpoint | Tube fitting hex torqued to ensure correct tightness, marked with pen
checkpoint | Ensure Weep hole is unobstructed and clean
checkpoint | In service leak test performed and passed
checkpoint | Fitting completion tag completed and applied to each fitting
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-126 Cone and Thread Pressure Testing
section | General Data
checkpoint-no-status | General Data
textbox | Location:
textbox | Duty:
textbox | Reference Drawings:
textbox | Hook-up drawing:
textbox | Related instrument tag no:
textbox | Tube diameter and wall thickness:
textbox | Instrument location drawing:
section | Checklist items
checkpoint | Tubing orientation as per hook up drawing.
checkpoint | Checked with a Torque Wrench and marked and tagged
checkpoint | Ensure Area is barricaded off to restrict unauthorized entry to personnel
checkpoint | Tube as per specification and hook up drawings.
textbox | Max design pressure:
textbox | Test medium used:
textbox | Record Testing pressure:
textbox | Test pressure duration: | Minutes
textbox | Test leak rate: | Litres/minute
checkpoint | Chart recorder used and attached (where applicable).
checkpoint | Confirm all Tubing lines have been pigged / cleaned.
checkpoint | Check all plugs are replaced (if removed), vents are closed, and isolation valves are in correct positions.
checkpoint | Ensure equipment is left clean and in a safe state for handover to operations to the standard of ITP-I-08 Cone and Thread cleaning procedure
section | Test Equipment
checkpoint-no-status | Test Equipment
textbox | Make:
textbox | Model:
textbox | Serial No:
textbox | Calibration Expiry:
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-127 Telecommunications Equipment Panel
section | Telecommunications Equipment Panel
checkpoint | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings:
checkpoint | Check tag number is in accordance with Telecommunications Equipment List.
checkpoint | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order.
checkpoint | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation.
checkpoint | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified.
checkpoint | Check panel air vents are clean and free of dust and dirt.
checkpoint | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar.
checkpoint | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar.
checkpoint | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s).
checkpoint | Check sealing of all cable penetration (where applicable).
checkpoint | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel.
checkpoint | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable).
checkpoint | Confirm panel is readily accessible for inspection and maintenance.
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-128 Temperature Instrument Installation
section | Temperature Instrument Installation
checkpoint | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint | Temperature instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration)
dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
checkpoint | Thermowell details including flange size are correct in accordance with the specifications
checkpoint | Internal depth of thermowell checked and recorded
textbox | Depth:
checkpoint | Bar material and tag number stamped on thermowell flange/exposed surface
button | Thermowell CE marked | YES,NO
checkpoint | EOL resistor fitted and correctly rated where applicable
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-129 Flow Meter Installation
section | Flow Meter Installation
checkpoint | Check instrument nameplate details are correct in accordance with the instrument index
checkpoint | Flow meter calibrated before installation (ITR-CL-1-123 Instrument Calibration)
checkpoint | Ensure location and tapping point is verified as per P&ID & location drawings
checkpoint | Ensure direction of flow is correct with respect to flow meter
checkpoint | Check mechanical clearance is adequate for installation of flow meter
checkpoint | Verify type and size of gasket is correct between process line and measuring unit flange
checkpoint | Ensure correct nut and bolt grade and material for connecting unit to process line
checkpoint | Verify display/cover is oriented for ease of use for operators and access for technicians
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-130 Pressure Instrument Installation
section | Pressure Instrument Installation
checkpoint | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint | Pressure Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration)
checkpoint | Instrument mounted as per hook-up drawings
checkpoint | Air line/Impulse line are correct material to site specifications
checkpoint | Air line/Impulse line are routed tidily and as per hook-up drawings
checkpoint | Correct bolt size and material/grade used
checkpoint | Local indicator is mounted and easy to read, easy access for technicians
checkpoint | Instrument and tubing are adequately supported as per drawings
checkpoint | Isolation valve installed
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed
checklist | ITR-CL-1-131 Level Instrument Installation
section | Level Instrument Installation
checkpoint | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration)
checkpoint | Level instrument mounting equipment is adequately sturdy and correct materials used
checkpoint | Bolts and studs are to site specification
checkpoint | Ensure location and tapping point is verified per relevant drawings
checkpoint | Ensure gasket and studs are used as per specifications
checkpoint | Verify contact type sensor probes are installed without any resistance
checkpoint | Verify antenna/source are installed correctly
checkpoint | Ensure display is easily readable by operations and access is easy for technicians
section | Acceptance Signatures
checkpoint | Test/Inspection carried out by:
textbox | Test/Inspection carried out by:
signoff | Signed
checkpoint | Test/Inspection approved by:
textbox | Test/Inspection approved by:
signoff | Signed
checkpoint | Client Representative
textbox | Client Representative
signoff | Signed

## Examples
Command | Description
checklist | complex checklist with progress bar
checklist-flat | simple checklist
section | breaks checklist into sections
checkpoint | Pass/Fail/NA checkpoint
checkpoint-no-status
textbox | Textbox for inputting data for above checkpoint/section
dropdown | Select from a dropdown range of options. Enter options in "Values" tab separated by commas eg. Item 1, Item 2, Item 3
date | users can select date from a calendar
label | Creates a label for relevant checkpoint/section, good for additional notes or instruction e.g "Test 230v circuits at 500VDC for IR test"
button | Buttons with defined labels, enter options in "Values" tab separated by commas eg. Yes, No or option A, option B, option C, etc
signoff | creates touchscreen signature input section, for signing off documents