## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Cable Test Record |  |  |  |  | Yes | Cable Test Record | 03b139ce-b949-4f24-a386-5791893bb1cb
checkpoint-status |  |  | checkpoint | Upload completed ITR scans
checklist-sectioned |  |  | checklist | JHA - Job Step |  |  |  |  | Yes | JHA - Job Step | 053f0436-6852-47dd-9e93-0993a7c77bb4
checkpoint-group |  |  | section | Task Step - add task step for each individual task
checkpoint-no-status |  |  | checkpoint | Task Step - add task step for each individual task
date | 6734cd2e-2206-5ca4-9825-09919459f774 |  | date | Date:
text | 7c0c04a8-15e2-57de-b473-a4a22d6676c7 |  | textbox | Task step number (eg. Step 1, Step 2 etc):
text | 61da84e8-bbc9-5e82-b357-b40ecb217fc3 |  | textbox | Task details:
text | 3ba9c266-803d-57f0-aa37-0a75d6afda1a |  | textbox | Hazards:
select | 20f7194b-8f6a-52e7-a8da-fae01d4ddd2a |  | dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
text | 8db88eb8-4276-5be8-9739-b0d310aa9b67 |  | textbox | Potential consequence:
text | 626146a5-5c08-5236-8659-52f3a795560e |  | textbox | Controls:
text | 3704a4d9-6eee-5d0b-9021-d594ddd290d6 |  | textbox | Recovery steps:
select | 8acb308c-ba1b-5706-862d-9323ec8cad92 |  | dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
checklist-sectioned |  |  | checklist | ITR-I-03 Instrument Pressure/Leak Test |  |  |  |  | Yes | ITR-I-03 Instrument Pressure/Leak Test | 0a505eac-9036-4ef6-9fc4-b1fe1de9b477
checkpoint-group |  |  | section | Checklist items
checkpoint-status |  |  | checkpoint | Tube identification correct
checkpoint-status |  |  | checkpoint | Check mechanical damage
checkpoint-status |  |  | checkpoint | Flow direction and instrument orientation correct
checkpoint-status |  |  | checkpoint | Tubing installed correctly
checkpoint-status |  |  | checkpoint | Tubing size
checkpoint-group |  |  | section | Testing
checkpoint-no-status |  |  | checkpoint | Testing
label | 8785f304-76e9-5cd4-9214-9e6e5774c1ad |  | note | Verify test pressure and medium is correct per project and manufacture specification prior to test
select | f9b69bbc-79cc-5035-8fca-40bb768c187c |  | dropdown | Test fluid: | Air, N2, Water, Hydro-oil, Other
text | 8904c053-d0d0-53e6-80c8-fb3b384d483b |  | textbox | Test pressure:
text | 31491d4a-ac78-54c0-b00e-4f541659fad8 |  | textbox | Max design pressure:
select | e47ada78-1119-5992-a200-01d86c2dd20b |  | dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
text | bfe0ce00-9cbb-5e1f-9b2b-69418434e4ca |  | textbox | Duration: |  |  | Minutes
checkpoint-status |  |  | checkpoint | Confirm all impulse lines have been drained and cleaned
checkpoint-status |  |  | checkpoint | Confirm any temporary test connections, valve etc. are rated for the intended test.
checkpoint-status |  |  | checkpoint | Confirm pneumatic, test gas and aspirator lines have been blown clear.
checkpoint-status |  |  | checkpoint | Check hydraulic lines flushed to project specification.
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 860b27a8-e871-51ef-840e-7ad58c1b0fce |  | textbox | Make:
text | 2c1d1d57-e07d-530c-9147-abcd3693cf54 |  | textbox | Model:
text | efed6203-e909-595e-92f4-722f10997588 |  | textbox | Serial No:
text | 475dfc19-8ce3-53e0-8a57-98fb86ca27bc |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | da71e8de-84ce-5b6f-b5cb-47fe0749e657 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 0af3dfb4-b257-5f76-aec1-e676ee874884 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 22abe41b-7484-5c04-a753-8aa78c4bf351 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-06 Control Panel |  |  |  |  | Yes | ITR-E-06 Control Panel | 1347300a-6c9e-4864-b64d-0892f0d5d037
checkpoint-group |  |  | section | Control Panel
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | Check holding down/mounting arrangement is correct.
checkpoint-status |  |  | checkpoint | Check for mechanical damage.
checkpoint-status |  |  | checkpoint | Check that panel is correctly earthed.
text | eb09ef70-eea8-5c5c-87bb-f0c4d720706d |  | textbox | Check earth continuity between panel and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status |  |  | checkpoint | Check tightness of circuit connections.
checkpoint-status |  |  | checkpoint | All internal cabling and wiring is correctly numbered, colour coded and terminated
checkpoint-status |  |  | checkpoint | Ammeter scale and current transformer correct.
checkpoint-status |  |  | checkpoint | Check internals for cleanliness.
checkpoint-status |  |  | checkpoint | Check manual operation of selector switches, MCB, push buttons, etc.
checkpoint-status |  |  | checkpoint | Incoming cables correctly glanded, terminated and labelled.
checkpoint-status |  |  | checkpoint | Unused holes are sealed.
checkpoint-status |  |  | checkpoint | Heaters correctly installed.
text | 2572bac0-7f95-5a71-b47d-b7546026a7f7 |  | textbox | Heater circuit Insulation Resistance: |  |  | MegaOhm
checkpoint-status |  |  | checkpoint | Fuse rating correct.
checkpoint-status |  |  | checkpoint | Padlocking facilities correct (if applicable).
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 8586d15a-8b90-5f10-9680-f50929c2e7d0 |  | textbox | Make:
text | ea64452b-37c3-5405-91f3-74a7c3fe0571 |  | textbox | Model:
text | 455daaf9-c807-53ed-9537-b127bf7a1205 |  | textbox | Serial No:
text | 734b1f3e-7a92-5a15-913b-535a3817d1ea |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 9d34de85-de5d-511d-9cfc-350cdcaf2dc2 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 49965e2e-aa95-59cb-9b8e-ef8615c64e46 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 9d4257f9-81d6-5a1f-914f-4b05bec7ea30 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-07 Junction Box |  |  |  |  | Yes | ITR-E-07 Junction Box | 188126b5-391d-4d4d-9ea1-7c6d9ee76ca8
checkpoint-group |  |  | section | Junction Box
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | Check holding down/mounting arrangement and accessibility for maintenance.
checkpoint-status |  |  | checkpoint | Check for mechanical damage
checkpoint-status |  |  | checkpoint | Check that Junction box is correctly earthed.
text | 60438b60-08ab-5c43-b263-949cc25473de |  | textbox | Test and confirm the earth resistance between junction box and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status |  |  | checkpoint | Check all internal cabling and wiring is correct and tight, including segregation (e.g. IS to NON IS circuits).
checkpoint-status |  |  | checkpoint | Check cables for Voltage segregation. Ensure clearance, labelling, colour coding is to standard
checkpoint-status |  |  | checkpoint | Incoming/Outgoing cables are glanded and terminated correctly
checkpoint-status |  |  | checkpoint | Spare entries plugged correctly.
checkpoint-status |  |  | checkpoint | Check internals for cleanliness
checkpoint-status |  |  | checkpoint | All cover bolts and gasket undamaged
checkpoint-status |  |  | checkpoint | Verify ingress protection is suitable for area (IP rating)
text | 83ef924a-801b-5d86-98d9-7bab447b6a2d |  | textbox | IP Rating:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 04506c0d-17c0-5b07-b751-8fa45aef5931 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 74432548-773c-5061-8015-681dfc7465d6 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 22bfde7e-b8c8-5bd3-bf37-34a02c0b78e3 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-02 Conduit, Ducting, Unistrut, Cable Tray & Ladder Installation |  |  |  |  | Yes | ITR-E-02 Conduit, Ducting, Unistrut, Cable Tray & Ladder Installation | 1905b8c0-2106-4fe2-9c2b-f5c3e27ab6b5
checkpoint-group |  |  | section | Conduit/Ducting Installation Below Ground
checkpoint-status |  |  | checkpoint | Check equipment details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | Check conduit cable enclosure installation is as-per design, layout drawings and specifications.
checkpoint-status |  |  | checkpoint | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed.
checkpoint-status |  |  | checkpoint | Confirm that there are no obstructions, and that the installation will be accessible for maintenance.
checkpoint-status |  |  | checkpoint | Check all fixings are tight and secure.
checkpoint-status |  |  | checkpoint | Check bends do not exceed the maximum cable bend radius.
checkpoint-group |  |  | section | Cable Supports Above Ground
checkpoint-status |  |  | checkpoint | Verify cable support has been installed as per relevant drawings.
checkpoint-status |  |  | checkpoint | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection.
checkpoint-status |  |  | checkpoint | All covers fitted if applicable.
checkpoint-status |  |  | checkpoint | Check cable support structures are adequately fixed and present no hazard to personnel.
checkpoint-status |  |  | checkpoint | Correct cable support size and type used.
checkpoint-status |  |  | checkpoint | Welded support brackets have been wire-brushed and painted to completion.
checkpoint-status |  |  | checkpoint | Splice plates, barriers, earthing system secure.
checkpoint-status |  |  | checkpoint | Trays / ladders, supports, brackets not interfering with other disciplines.
checkpoint-status |  |  | checkpoint | Check bends do not exceed the maximum cable bending radius.
checkpoint-status |  |  | checkpoint | Cables have adequate mechanical protection as and where required.
checkpoint-status |  |  | checkpoint | Inspect for system rigidity, and check levels to correct plane.
checkpoint-status |  |  | checkpoint | Earth bonding straps have been fitted to any sections that are split, hinged or flexible.
checkpoint-status |  |  | checkpoint | Tray bonded to structure at correct locations.
text | ddd9aa9f-2956-581f-b481-00ec57f865db |  | textbox | Earth bonding continuity tested – record result: |  |  | Ohms
checkpoint-group |  |  | section | Cable Transits
checkpoint-status |  |  | checkpoint | Transit frame installed as per drawings.
checkpoint-status |  |  | checkpoint | Transit frame identification marked correctly and visible.
checkpoint-status |  |  | checkpoint | Frame correctly packed with correct sized blocks and infills.
checkpoint-status |  |  | checkpoint | Correct stay plates fitted (non-ferrous for single core power cables.)
checkpoint-status |  |  | checkpoint | Rated insulation installed to transit (where required.)
checkpoint-status |  |  | checkpoint | Cables entering and leaving transits adequately supported and protected.
checkpoint-status |  |  | checkpoint | Cables pass through frames without strain on blocks.
checkpoint-status |  |  | checkpoint | All cables identified on both sides of transit and visible.
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | cb38406b-985f-54db-9df0-5ca771ec3518 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | da9d518f-1ed4-5efd-b802-e42bd12421db |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | f896fa29-7b70-5405-ac24-c18cb9a7548f |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-flat |  |  | checklist | Certificate of compliance (COC) |  |  |  |  | Yes | Certificate of compliance (COC) | 21c0af86-390e-4816-a68a-4a2599146f16
checkpoint-status |  |  | checkpoint | Please upload Certificate of Compliance here when complete (COC)
checklist-sectioned |  |  | checklist | ITR-I-04 Valve & Ancillaries (Pre-Installation) |  |  |  |  | Yes | ITR-I-04 Valve & Ancillaries (Pre-Installation) | 3175b8a8-f8b3-45cc-b424-a062a5cb0a16
checkpoint-group |  |  | section | Equipment
checkpoint-status |  |  | checkpoint | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No.
checkpoint-status |  |  | checkpoint | Equipment checked for additional items as applicable
checkpoint-group |  |  | section | Valve
checkpoint-no-status |  |  | checkpoint | Valve
text | 403f9abc-4e38-5bd6-826f-f15359ab90d9 |  | textbox | Size:
text | 1e984136-3360-520b-9a09-cc56a7400d08 |  | textbox | Flange type:
checkpoint-status |  |  | checkpoint | Material certification correct
checkpoint-status |  |  | checkpoint | Trim material correct
text | 2e9d99d9-931c-5009-9cad-7441994a2d73 |  | textbox | Rating:
text | 65fa1f84-c129-5ec4-a0bf-fde2ca29b544 |  | textbox | Service:
checkpoint-status |  |  | checkpoint | Body material correct
text | 4fec773d-e81d-50e8-a808-df5f349ff3a1 |  | textbox | Leakage class:
checkpoint-group |  |  | section | Actuator
checkpoint-no-status |  |  | checkpoint | Actuator
text | c6e1380a-f000-5e65-8166-d6dd336e44ad |  | textbox | Input range: |  |  | kPa
checkpoint-status |  |  | checkpoint | Failure action
checkpoint-status |  |  | checkpoint | Hand wheel operation correct
checkpoint-group |  |  | section | Positioner
checkpoint-no-status |  |  | checkpoint | Positioner
text | 624ac7a5-e599-51b0-8ec4-b47a29819fd5 |  | textbox | Signal range
text | a882e465-e539-5109-9bf7-9916d750c7c2 |  | textbox | Output range
checkpoint-group |  |  | section | I/P Converter
checkpoint-no-status |  |  | checkpoint | I/P Converter
text | f294ee0d-eebd-5864-9232-d5d7e8345bd9 |  | textbox | Signal range
text | f3381e3c-e7ea-5eec-a9ac-eb8971543186 |  | textbox | Output range
checkpoint-group |  |  | section | Filter/Regulator/On-Off Valve
checkpoint-no-status |  |  | checkpoint | Filter/Regulator/On-Off Valve
text | c45ee1b4-e9f1-5c3e-9332-716defcf5e38 |  | textbox | Range |  |  | kPa
text | cb31919b-8944-50ec-b548-735a0f8c32b5 |  | textbox | Pressure setting |  |  | kPa
checkpoint-status |  |  | checkpoint | Stroke Time
text | 7f46782c-fe7b-5308-a532-412c5b10496d |  | textbox | Open |  |  | sec
text | 415d3b9b-5ece-5822-acd1-1d54f5f83de6 |  | textbox | Close |  |  | sec
checkpoint-status |  |  | checkpoint | Open/Close times conform to commissioning specifications
checkpoint-group |  |  | section | Fail Action
checkpoint-no-status |  |  | checkpoint | Fail Action
select | ddc00b4a-4604-5878-960b-aadc58fba5de |  | dropdown | Electrical Fail Action | FO, FC, FL
select | e99de0a8-83da-57ce-bb53-2c84f6758b06 |  | dropdown | Motive Force | FO, FC, FL
checkpoint-group |  |  | section | Valve Field Calibration and Hysteresis Check
checkpoint-status |  |  | checkpoint | Confirm test equipment is within calibration period prior to testing
label | bb5dc46f-2aa7-588c-a4a6-a253c91d8272 |  | note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
label | 1bb03b47-5238-505b-9cf8-1ed482701421 |  | note | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100%
checkpoint-group |  |  | section | Proximity Detectors
checkpoint-status |  |  | checkpoint | Open switch set
checkpoint-status |  |  | checkpoint | Open switch mode setting correct
checkpoint-status |  |  | checkpoint | Closed switch set
checkpoint-status |  |  | checkpoint | Closed switch mode setting correct
checkpoint-status |  |  | checkpoint | Electrical connections correct
checkpoint-status |  |  | checkpoint | Electrical certification correct
checkpoint-group |  |  | section | Solenoid Valve
checkpoint-status |  |  | checkpoint | Operation correct
checkpoint-status |  |  | checkpoint | Electrical connections correct
checkpoint-status |  |  | checkpoint | Electrical certification correct
text | 1de836a1-2ca3-5815-8a77-f0a6cb49a0e1 |  | textbox | Voltage: |  |  | V
checkpoint-status |  |  | checkpoint | Pneumatic connections correct
text | c2f4d88e-51d3-5e87-a893-e46f3afa550a |  | textbox | Pneumatic pressure |  |  | kPa
checkpoint-group |  |  | section | Pilot Valve
checkpoint-status |  |  | checkpoint | Pneumatic connections correct
checkpoint-status |  |  | checkpoint | Operation correct
checkpoint-status |  |  | checkpoint | Action/Lockup
checkpoint-group |  |  | section | Hydraulic Actuator
checkpoint-no-status |  |  | checkpoint | Hydraulic Actuator
text | 9007523c-92d0-56f2-9c2c-45a37a04c4c7 |  | textbox | Working pressure
text | 0200b600-f0f8-5558-b097-ffa28ba51b83 |  | textbox | Manifold pressure
text | caa2d8b1-eb86-57f1-8635-d8a12885d4b5 |  | textbox | Fluid type
checkpoint-status |  |  | checkpoint | Hydraulic connections correct
text | c1f8fd3c-8501-5d9a-8e16-f1933c7d369d |  | textbox | Regulator pressure setting
checkpoint-status |  |  | checkpoint | Pilot operation correct
checkpoint-group |  |  | section | Accumulator
checkpoint-status |  |  | checkpoint | N2 Charge required
text | cdb06971-ad41-5648-bd84-ade3f806db04 |  | textbox | N2 Pre-charge pressure
text | eadefd8d-3080-5ecd-8ef7-edc25ba3f723 |  | textbox | Pressure switch setting
text | f0a626fa-7026-5f30-929b-278a3a04ba26 |  | textbox | Working pressure
text | aeafe65e-c93c-5031-a6ef-875155e83cb3 |  | textbox | Output range
checkpoint-status |  |  | checkpoint | Volume tank & check valve installed correctly
checkpoint-group |  |  | section | Electric Actuator
checkpoint-no-status |  |  | checkpoint | Electric Actuator
text | 275b01a2-927e-54e9-a53f-ce5b4368c4a7 |  | textbox | Voltage:
text | 4c73f166-b6a4-57b9-a366-94322094392e |  | textbox | Electrical certification correct
text | a13abf99-546d-59ea-8e91-c99c8d793206 |  | textbox | Electrical connections correct
text | 1190f259-1501-5a27-9ee6-00619d36e920 |  | textbox | Remote operation correct
text | 90ac399f-5d38-5b55-a3f9-cc9fb170709b |  | textbox | Local hand operation correct
text | b47fc2ee-92f6-5bf0-abfe-8c239b97d93e |  | textbox | Torque switches and travel stops set
checkpoint-group |  |  | section | Miscellaneous Equipment
checkpoint-no-status |  |  | checkpoint | Miscellaneous Equipment
text | 06285bf3-1d48-53fc-b291-48c35ff38416 |  | textbox | Description
text | 5db8dab8-5d6a-52e3-9909-1f4ac340b1c0 |  | textbox | Manufacturer
text | 3065f8aa-8969-57ff-b235-685afdfa2973 |  | textbox | Model No:
text | bf8a2362-05c0-5675-a54f-0a7584690a3e |  | textbox | Serial No:
text | 8f4ddb79-d5f5-5d7d-aa5e-2fd990c83a23 |  | textbox | Range:
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | d34593b2-8e2b-53d5-a6da-2e14f1db6d14 |  | textbox | Make:
text | 8f8e0f76-bd1d-518d-b9ad-c0f6f33a2917 |  | textbox | Model:
text | 431cc600-1152-55ea-828c-ac7860eda4f2 |  | textbox | Serial No:
text | 29cb60c3-5f47-5548-87af-57f242ac69a1 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | c19b15d2-a653-5f09-a097-654fc95a7496 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 945a9420-1100-5ab4-8668-40493e4b779b |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | bca75e1d-3cce-50b4-a767-3406622c8adb |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-14 Motor Control |  |  |  |  | Yes | ITR-E-14 Motor Control | 3635b871-0f91-463d-add9-0c0253b49535
checkpoint-group |  |  | section | General Motor Control
checkpoint-status |  |  | checkpoint | Check all labelling and warning signs are correctly installed and visible
checkpoint-status |  |  | checkpoint | Check control equipment is clean and free from dust, debris and tools
checkpoint-status |  |  | checkpoint | Check preservation and transit items are removed
checkpoint-status |  |  | checkpoint | Check there are no mechanical damage and no damage to paintwork
checkpoint-status |  |  | checkpoint | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor
checkpoint-status |  |  | checkpoint | Check all cabling to control gear and motor is undamaged, supported and tidy
checkpoint-status |  |  | checkpoint | Check earthing bar and connections are correct and tight
checkpoint-status |  |  | checkpoint | Check incoming and outgoing power cables are terminated and glanded correctly
checkpoint-status |  |  | checkpoint | Check phase identification on power cables is correct and visible
checkpoint-status |  |  | checkpoint | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque
checkpoint-status |  |  | checkpoint | Check all other nuts and bolts are tight
checkpoint-status |  |  | checkpoint | Check spare gland entries are plugged with correct rated plugs
checkpoint-status |  |  | checkpoint | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected
checkpoint-group |  |  | section | Variable Speed Drives (VSD)
checkpoint-status |  |  | checkpoint | Record VSD Nameplate Details
text | 9495ddd6-29fe-54c6-aed9-72ee83a27853 |  | textbox | Volts (Input) |  |  | V
text | 4e0586f4-0e73-5592-afd1-89f4538c9aa3 |  | textbox | Amps (Input) |  |  | A
text | fc6c8685-0d35-506a-a6d5-90f89a8a1c3f |  | textbox | Amps (Output) |  |  | A
checkpoint-status |  |  | checkpoint | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input)
checkpoint-status |  |  | checkpoint | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used.
checkpoint-status |  |  | checkpoint | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged
checkpoint-status |  |  | checkpoint | Check control signal cables use twisted pairs
checkpoint-status |  |  | checkpoint | Check control signal and profibus cables shield is earthed at one end
checkpoint-status |  |  | checkpoint | Check analogue and digital signals are run in separate cables
checkpoint-group |  |  | section | Check that voltage segregation is applied along the length of cables:
checkpoint-status |  |  | checkpoint | Distance between input power and motor cable >300mm
checkpoint-status |  |  | checkpoint | Distance between input power and control signal cable >200mm
checkpoint-status |  |  | checkpoint | Distance between motor cable and control signal cable >500mm
checkpoint-status |  |  | checkpoint | Check there is no power factor compensation capacitors installed on the outgoing power cables
checkpoint-status |  |  | checkpoint | Check gland plates with single core power cables are non-magnetic at VSD and LIS
checkpoint-status |  |  | checkpoint | Check mains voltage cannot be applied to the VSD output by means of a bypass connection
checkpoint-status |  |  | checkpoint | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC
checkpoint-status |  |  | checkpoint | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position)
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 8cb263c3-06f9-5bf1-90a1-6186fcc1691e |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 446e4715-61cf-5a97-8f6a-0877ff40afa2 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 0fb25c74-9558-5ece-993a-9db29fa3e94b |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-I-09 Commissioning Instruments |  |  |  |  | Yes | ITR-I-09 Commissioning Instruments | 39a663de-3908-4cd1-805b-9c3a736b5bad
checkpoint-group |  |  | section | Required Data
checkpoint-no-status |  |  | checkpoint | Required Data
text | 39978199-2208-5474-b087-1b307aacd251 |  | textbox | Instrument range:
checkpoint-status |  |  | checkpoint | Installation complete
checkpoint-status |  |  | checkpoint | Point-to-point
checkpoint-status |  |  | checkpoint | Haz. Inspected
checkpoint-status |  |  | checkpoint | Tag correct
checkpoint-status |  |  | checkpoint | Hook-up correct
checkpoint-group |  |  | section | Alarms & Set points
checkpoint-status |  |  | checkpoint | Alarm Lo
text | 187cc798-cbf2-5683-a3b2-e19a7eb80bdf |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Alarm Lo-Lo
text | 7bbfd632-aff4-59bf-99db-15fcb0205fd8 |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Alarm Hi
text | 84384302-7c2c-512f-b894-c0f93bc68275 |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Alarm Hi-Hi
text | b3b52c3e-baa6-540c-9082-2a0758a47220 |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Set Point 1
text | acb3b942-7665-52db-9074-3d55545edc61 |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Set Point 2
text | 79a10a2f-5619-574f-9b4e-0d5d0a66590b |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Set Point 3
text | 6caaa7b3-3bdd-5009-a153-cbfe77b5d2c9 |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Set Point 4
text | 5efd1583-761b-5354-ba45-65fdbf7c48c9 |  | textbox | Activated:
checkpoint-group |  |  | section | Calibration settings
checkpoint-no-status |  |  | checkpoint | Calibration settings
text | eeabd224-a0e8-5f38-a816-46bc1c49325f |  | textbox | Zero
text | de56346a-e439-55ab-91e0-f377ac0ad07c |  | textbox | Range
text | b6ff40a4-2651-5acf-9e8a-9a1e226860a2 |  | textbox | Other (Specify)
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 1745b146-a958-57a0-a6b9-564218df0bed |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 1f2f1237-db75-5e25-8164-3943228e9f0c |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 219c0fc9-67a9-5f55-98aa-d2259a5be495 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-I-02 Instrument Tubing Installation |  |  |  |  | Yes | ITR-I-02 Instrument Tubing Installation | 3cd2a96d-a2ed-48d8-a159-1048651ae490
checkpoint-group |  |  | section | Information
checkpoint-no-status |  |  | checkpoint | Information
text | e4ca7637-baee-507c-931d-66f4482f88be |  | textbox | Equipment:
text | 89543a54-92fa-5c73-891f-2fdab3b7688b |  | textbox | Location:
text | 455c88b6-1451-5eae-9928-7d4c74906613 |  | textbox | Tag Numbers:
text | 2345ae9d-1466-556f-9fa4-e0c914481405 |  | textbox | Process Fluid:
text | c7ce44da-12c7-5995-8537-5fdd3ca96059 |  | textbox | Reference Drawings:
text | cfd01fcc-e32d-5763-a77f-137dc1418239 |  | textbox | Max Process Pressure:
text | a169afa8-3927-56db-9d0b-7e5434c7719b |  | textbox | Max Supply Pressure:
text | e5fed497-7939-52ac-80ff-2c2688466e8c |  | textbox | Max Signal Pressure:
text | 9bec04bb-d12e-555c-aef9-fd50ff224015 |  | textbox | Process Temperature:
text | 160ba958-06bb-5a69-9f3e-b3e1acccffd7 |  | textbox | Other:
button | ed6684ef-1c87-5e66-8684-34f07b4c780c |  | button | Inspection | Yes, No
text | 17bcca9b-2c71-53b6-9d1b-e6e02f21ca08 |  | textbox | Percentage of installed items to be checked:
checkpoint-group |  |  | section | Checks Pre-Installation
checkpoint-status |  |  | checkpoint | Tubing connection drawings and details available
checkpoint-status |  |  | checkpoint | Client site specific changes noted, agreed and sketched
checkpoint-status |  |  | checkpoint | Tube material type, size, gauge and standard confirmed and available
checkpoint-status |  |  | checkpoint | Tube fitting size and type confirmed and available
checkpoint-status |  |  | checkpoint | Torque wrench - Current calibration certificate
checkpoint-group |  |  | section | Checks During and Post-Installation
checkpoint-status |  |  | checkpoint | Correct thread compatibility and engagement
checkpoint-status |  |  | checkpoint | Correct thread tape and sealant used on fittings
checkpoint-status |  |  | checkpoint | Check fitting ferrule orientation and confirm prior to connection
checkpoint-status |  |  | checkpoint | Tube installation is in compliance with the client specification.
label | 33b87a60-2646-507a-8e79-bc46abe0559e |  | note | (Supports, bracketry, slope, expansion, vibration, access, cables)
checkpoint-status |  |  | checkpoint | Tube bent correctly, sufficient straight section into fitting
checkpoint-status |  |  | checkpoint | Tube cut clean and straight, de-burred, reamed, and blown through
checkpoint-status |  |  | checkpoint | Depth insertion tool used; witness mark visible at all stages of process
checkpoint-status |  |  | checkpoint | Tube fitting hexes marked to ensure correct swage tightness
checkpoint-status |  |  | checkpoint | Random check with No-Go gap gauge
checkpoint-status |  |  | checkpoint | In service leak test performed and passed
checkpoint-status |  |  | checkpoint | Fitting completion tag completed and applied to each fitting
label | b3ba7257-a67b-52a9-b445-3ff05a6701f3 |  | note | Refer to Swagelok book for tube/thread size pressure ratings
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 1e79072e-5677-5b2b-8afd-59da3184b5a8 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | f6bc42c3-4383-5ec0-b32f-3e74ad9fec60 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 50bcde76-398c-599f-83a2-65145627288d |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-I-16 Level Instrument Installation |  |  |  |  | Yes | ITR-I-16 Level Instrument Installation | 3f637b0c-d82f-460b-ba0f-ae8a20d1ccfe
checkpoint-group |  |  | section | Level Instrument Installation
checkpoint-status |  |  | checkpoint | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint-status |  |  | checkpoint | Level Instrument calibrated before installation (ITR-I-07 Instrument Calibration)
checkpoint-status |  |  | checkpoint | Level instrument mounting equipment is adequately sturdy and correct materials used
checkpoint-status |  |  | checkpoint | Bolts and studs are to site specification
checkpoint-status |  |  | checkpoint | Ensure location and tapping point is verified per relevant drawings
checkpoint-status |  |  | checkpoint | Ensure gasket and studs are used as per specifications
checkpoint-status |  |  | checkpoint | Verify contact type sensor probes are installed without any resistance
checkpoint-status |  |  | checkpoint | Verify antenna/source are installed correctly
checkpoint-status |  |  | checkpoint | Ensure display is easily readable by operations and access is easy for technicians
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 40735889-3cbe-52b1-bda8-91d0fe946c31 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 73d9dc97-7afe-50cd-bf4d-ba0920d3e997 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 201e7f4a-4ad6-51e6-91ce-66f8cb42bc61 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-I-14 Flow Meter Installation |  |  |  |  | Yes | ITR-I-14 Flow Meter Installation | 4683066a-28c3-4661-8af1-72622fea4790
checkpoint-group |  |  | section | Flow Meter Installation
checkpoint-status |  |  | checkpoint | Check instrument nameplate details are correct in accordance with the instrument index
checkpoint-status |  |  | checkpoint | Flow meter calibrated before installation (ITR-I-07 Instrument Calibration)
checkpoint-status |  |  | checkpoint | Ensure location and tapping point is verified as per P&ID & location drawings
checkpoint-status |  |  | checkpoint | Ensure direction of flow is correct with respect to flow meter
checkpoint-status |  |  | checkpoint | Check mechanical clearance is adequate for installation of flow meter
checkpoint-status |  |  | checkpoint | Verify type and size of gasket is correct between process line and measuring unit flange
checkpoint-status |  |  | checkpoint | Ensure correct nut and bolt grade and material for connecting unit to process line
checkpoint-status |  |  | checkpoint | Verify display/cover is oriented for ease of use for operators and access for technicians
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | b888c287-e6c9-5482-87e4-4fb0d1f07914 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | c4213855-9588-5335-8f40-12788eda6496 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | ed1a2b21-72c9-5181-a005-cc84d14e9e30 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-05 Low Voltage Cables |  |  |  |  | Yes | ITR-E-05 Low Voltage Cables | 4fb91b0f-5517-4dfc-b1eb-024517bf58a3
checkpoint-group |  |  | section | Low Voltage Cables
checkpoint-status |  |  | checkpoint | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule.
checkpoint-status |  |  | checkpoint | Check dressing/cleating.
checkpoint-status |  |  | checkpoint | Check cable for damage.
checkpoint-status |  |  | checkpoint | Check cable cores correctly identified and labelled.
checkpoint-status |  |  | checkpoint | Cable terminated with correct lugs and crimped with the correct die.
checkpoint-status |  |  | checkpoint | Check that cable phasing is correct and point-to-point each core for continuity.
checkpoint-status |  |  | checkpoint | Check Armour/Screen correctly made off.
checkpoint-status |  |  | checkpoint | Check armour continuity /earthing is maintained by the correct use of serrated washers and/or earth tags.
checkpoint-status |  |  | checkpoint | Glanding/Locknuts correctly installed.
checkpoint-group |  |  | section | Gland type - from:
checkpoint-no-status |  |  | checkpoint | Gland type - from:
text | 1d3a513d-293d-5260-8dad-f7de66058c26 |  | textbox | Haz. Area Rating:
text | 386079ae-a5c5-5eb5-8f11-fea434f10374 |  | textbox | Haz. Area Cert Details:
checkpoint-group |  |  | section | Gland type - to:
checkpoint-no-status |  |  | checkpoint | Gland type - to:
text | c8429c87-1c09-5551-95ff-83ebc4fa5aec |  | textbox | Haz. Area Rating:
text | 899f05ea-1c19-50df-99eb-3300caf260d4 |  | textbox | Haz. Area Cert Details.
checkpoint-group |  |  | section | Electrical Testing
checkpoint-status |  |  | checkpoint | IR Testing - LV Cables
label | 116600f5-7f9a-51b9-82d2-9404496e17df |  | note | (Test voltage 1,000 VDC for LV cables and 5KVDC for HV cables)
text | 9cff0a72-5a58-52db-a032-8903b4708196 |  | textbox | L1 – Earth |  |  | MegaOhms
text | 9271fa5e-3ff1-519c-b9d4-69a4b6a2dcc1 |  | textbox | L2 – Earth |  |  | MegaOhms
text | 26f63269-2321-50d2-97da-818a773aeb9e |  | textbox | L3 – Earth |  |  | MegaOhms
text | 34cd7b0b-cd34-5800-9c83-50bf3d60d765 |  | textbox | L1 – L2 |  |  | MegaOhms
text | 45ac5963-cca7-59c7-b60d-6412cb649911 |  | textbox | L1 – L3 |  |  | MegaOhms
text | cc5496fe-5543-5cd5-8add-b17770933c32 |  | textbox | L2 – L3 |  |  | MegaOhms
text | 1c378fc4-b149-531b-9e3c-4cf21f080179 |  | textbox | N – Earth |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | IR Testing - Multiple conductor cables (Record lowest readings)
text | 8fed800a-7dcc-5b9f-a87a-5aa2e006a2e6 |  | textbox | Between Conductors |  |  | MegaOhms
text | d1e24e47-f838-5f50-82fc-3235878c0747 |  | textbox | Conductors to GND |  |  | MegaOhms
text | fc33089a-ed13-5fbc-8902-9f2cb0af8783 |  | textbox | Measure gland body continuity to earth. (Max 0.1 Ohm) |  |  | Ohm
checkpoint-status |  |  | checkpoint | Confirm cable routing and segregation is correct.
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 04b13fff-a395-558c-a86d-6ff16355532b |  | textbox | Make:
text | 504f468b-acee-5b72-869b-47999079b009 |  | textbox | Model:
text | ad17aa8a-7884-57ea-843e-51255134e4c4 |  | textbox | Serial No:
text | 8efa2ef4-7a25-57ef-9617-84213ecd8e7a |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 12629112-3eff-5949-8e1b-f4feeaff9fb9 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 61f9e1fa-8873-5af6-b007-023d895783c7 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 11b59595-26fb-53d4-981a-ebb2d5d126e3 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-13 Motors |  |  |  |  | Yes | ITR-E-13 Motors | 5c5ef672-98ed-4724-8be8-87d1aff60f3b
checkpoint-group |  |  | section | Inspection
checkpoint-status |  |  | checkpoint | Tag number correct
checkpoint-status |  |  | checkpoint | Area Classification correct
text | f35163e3-3196-5018-9692-a3b3ef4d9bcc |  | textbox | IP Rating: |  | IP
text | 79ada5a6-27cf-5ac0-8333-5f8bbede04fe |  | textbox | Hazardous area cert:
checkpoint-status |  |  | checkpoint | Electrical Connections correct
button | 4e8cd901-edd7-5706-86d3-1f6bfe8704f5 |  | button | Space heater | YES,NO
text | 3e664232-72d6-5923-84eb-426dba8f559e |  | textbox | Space heater Volts:
text | b3079073-864d-5260-8483-4bffdb3a2adc |  | textbox | Space heater Power (Watts) |  |  | W
checkpoint-status |  |  | checkpoint | General condition
checkpoint-group |  |  | section | Nameplate Details
checkpoint-no-status |  |  | checkpoint | Nameplate Details
text | c4d0b585-e57a-55d4-8069-8f030bbf8d5c |  | textbox | Tag No:
text | cdb3dd83-473e-5eaf-bea9-84a71c89d969 |  | textbox | Manufacturer:
text | 59c1d94e-632d-53b0-8d78-1dabdfb6a2ed |  | textbox | Motor Serial Number:
select | c42803f4-ecfb-5e45-9a05-9c61d4de2a73 |  | dropdown | Phases: | Single-Phase, Three-Phase
text | 062b79f9-f108-5a73-a76a-1d0a159b01fe |  | textbox | Frame:
text | 1b291d76-1cdc-5e82-bc67-20ae3047575d |  | textbox | Enclosure:
text | 2ab7ebb3-313b-59b5-a18a-1539538a71c9 |  | textbox | Voltage: |  |  | V
text | 2fd96ee0-70bd-527d-b7e6-d27b393ab42a |  | textbox | Current: |  |  | A
text | 945c30d9-a01d-5171-82c5-ae72e5fce23e |  | textbox | kW: |  |  | kW
text | d5428272-7980-5ee1-93ed-243856688b6c |  | textbox | Speed:
text | ae00c7cb-1779-55fd-b303-b95b08883ba6 |  | textbox | PF:
text | cc42c541-9fc7-573a-98a5-170408bd2518 |  | textbox | No. of Poles:
text | 3353184d-04dd-572e-863c-b1c529d4c4d6 |  | textbox | Insulation Class:
select | 8f47a19b-d20f-53ea-ae47-82e9afa6f042 |  | dropdown | Rotation direction (looking down shaft) | Clockwise, Counter-Clockwise
checkpoint-status |  |  | checkpoint | Bearing Specs
text | 9c8931f2-a498-5223-91bf-d17f6ffa6efb |  | textbox | Drive end
text | 5c752565-0199-5b99-80e4-d2058e19f72f |  | textbox | Non Drive end
checkpoint-group |  |  | section | Checklist items
checkpoint-status |  |  | checkpoint | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets
checkpoint-status |  |  | checkpoint | Check Equipment and Nameplate details are correct in accordance with the data sheet.
checkpoint-status |  |  | checkpoint | Identification Tag and Rotation Plate correctly fitted
checkpoint-status |  |  | checkpoint | Motor electrical coupling (Delta /Star) as per voltage is correct.
checkpoint-status |  |  | checkpoint | Check for mechanical condition, air ducts and fan free of debris
checkpoint-status |  |  | checkpoint | Correct glanding for area classification.
checkpoint-status |  |  | checkpoint | Holding down bolts fitted correctly.
checkpoint-status |  |  | checkpoint | Check bearing lubrication.
checkpoint-status |  |  | checkpoint | Check free rotation with driven equipment uncoupled
checkpoint-status |  |  | checkpoint | Cable(s) correctly terminated, labelled and colour identification
checkpoint-status |  |  | checkpoint | Terminations/ connections torqued correctly to data sheets.
checkpoint-group |  |  | section | Motor Installation Testing
checkpoint-status |  |  | checkpoint | LV Motor winding insulation resistance with cables disconnected
checkpoint-status |  |  | checkpoint | 1 Minute
text | d3d76c93-d2aa-56ce-b70e-e90500dd1d31 |  | textbox | Winding "U" |  |  | MegaOhms
text | 5cb6e9e7-98ec-5d6d-ba29-53007002fc92 |  | textbox | Winding "V" |  |  | MegaOhms
text | a96cc25b-ec40-5208-b083-1c5ad06ce496 |  | textbox | Winding "W" |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | 10 Minutes
text | 4b17187a-be03-542b-8b05-18d242fe2d6c |  | textbox | Winding "U" |  |  | MegaOhms
text | 6878b440-741c-5ab7-88c3-16bd8eafcd5f |  | textbox | Winding "V" |  |  | MegaOhms
text | 985bbdb3-418c-5f7d-acb3-48e71a5a9461 |  | textbox | Winding "W" |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Motor continuity between windings
text | 419a093e-5894-5379-9430-210df6871a13 |  | textbox | U1 - U2 |  |  | Ohms
text | 5ba63647-548d-5cb9-8f03-b374ac11fa09 |  | textbox | V1 - V2 |  |  | Ohms
text | b29f9b6a-a503-5fbe-976c-3d4dc0bb7e0b |  | textbox | W1 - W2 |  |  | Ohms
checkpoint-status |  |  | checkpoint | Space heater continuity & resistance check
text | a0ae03cf-673a-527b-8826-82609bc65d71 |  | textbox | Continuity: |  |  | Ohms
text | 86149e67-5608-54ae-bbe7-6e372555812b |  | textbox | Insulation Resistance: |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Thermostat or RTD wiring resistance check
text | 93eb3289-dafc-5b93-99e5-af3db8d01af9 |  | textbox | Resistance: |  |  | Ohms
checkpoint-status |  |  | checkpoint | Check motor is earthed correctly and record motor earth bond:
text | 3c467247-15d8-5fc9-8d55-372ec9977083 |  | textbox | External bond continuity: |  |  | Ohms
checkpoint-group |  |  | section | Additional checks
checkpoint-status |  |  | checkpoint | Visual Inspections
checkpoint-status |  |  | checkpoint | Winding temperature detector
checkpoint-status |  |  | checkpoint | Air temp detectors
checkpoint-status |  |  | checkpoint | Bearing temp indicators
checkpoint-status |  |  | checkpoint | Vibration Monitors
checkpoint-status |  |  | checkpoint | Condensation detector
checkpoint-status |  |  | checkpoint | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable)
checkpoint-status |  |  | checkpoint | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable)
checkpoint-status |  |  | checkpoint | Installation conforms to specification and drawings
checkpoint-status |  |  | checkpoint | As-Builts complete
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | a4460616-4091-58eb-9b57-a6073f964162 |  | textbox | Make:
text | 76f5d8cc-69ba-54fc-a14d-f53d68968696 |  | textbox | Model:
text | 6fbb7a21-1e6a-5d24-a836-eea62a962520 |  | textbox | Serial No:
text | cda487c3-a066-5316-9b2b-83d326a68997 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | b21f3d8e-1e13-5696-af96-ce2e4222e8f7 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 4cdd66d7-ea70-54b3-ba91-26a11b292dd1 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | e41e733c-44b7-5da0-b5dc-1d3c59239929 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | As-Built Drawings |  |  |  |  | Yes | As-Built Drawings | 64679f71-076c-4492-809e-8a1c8d094902
checkpoint-group |  |  | section | As-Built Drawings - attach scanned documents
checkpoint-no-status |  |  | checkpoint | As-Built Drawings - attach scanned documents
text | 4d923f01-d7e2-5269-9ad5-ab2bae8951f0 |  | textbox | Drawing no.
checklist-sectioned |  |  | checklist | ITR-I-01 Fire and Gas Detection Alarms |  |  |  |  | Yes | ITR-I-01 Fire and Gas Detection Alarms | 78bc54b9-be16-46b3-9580-4aaeac23ce23
checkpoint-group |  |  | section | Checklist items
checkpoint-no-status |  |  | checkpoint | Checklist items
text | bc7ca676-25e3-5051-9560-d2a0afe19f78 |  | textbox | Manufacturer
text | f279317e-50cd-5d60-bf41-6e11d286150b |  | textbox | Make and Model
text | 788c64f0-5af2-5a85-bcc4-934f0efd99b8 |  | textbox | Type
checkpoint-status |  |  | checkpoint | Labelling/Number correct
checkpoint-status |  |  | checkpoint | Component & Type / Model correct
checkpoint-status |  |  | checkpoint | Cable connection & termination correct
checkpoint-status |  |  | checkpoint | Mechanical damage
checkpoint-status |  |  | checkpoint | Glanding condition
checkpoint-status |  |  | checkpoint | E.O.L Installation
checkpoint-status |  |  | checkpoint | Installation of Test tubing
checkpoint-status |  |  | checkpoint | Location correct
checkpoint-status |  |  | checkpoint | Detection Path Clear
checkpoint-group |  |  | section | Inspection
checkpoint-status |  |  | checkpoint | Tag No. Correct
text | 281e6085-4da2-544f-8dd5-b1224766626c |  | textbox | Tag No:
text | fd6e790c-8dcc-53c0-bfbe-bac4e9ca5143 |  | textbox | RX Tag No:
checkpoint-status |  |  | checkpoint | Area Classification correct
text | 5f018b3d-637b-5aff-a374-58f84772b0ae |  | textbox | Hazardous Area Certificate:
text | 85333827-ba12-5d60-aa4a-46bc503b9e95 |  | textbox | Detector Type:
text | bdcfa7b9-c509-5f71-960e-e5175eac79c9 |  | textbox | Gas Type:
checkpoint-status |  |  | checkpoint | Body Material Correct:
checkpoint-status |  |  | checkpoint | General Condition Satisfactory
text | b8633f53-3760-571c-85a8-f5e7615a8ef3 |  | textbox | Supply Voltage:
text | 945f5109-1111-54ab-b30b-0a25f89021f1 |  | textbox | Output Signal:
checkpoint-group |  |  | section | Functional Check
checkpoint-status |  |  | checkpoint | Self Test
checkpoint-status |  |  | checkpoint | Alarm Operation
checkpoint-status |  |  | checkpoint | Fault Relay Operation
text | 63e35d05-3a11-53e3-8ffb-bdf916d64792 |  | textbox | Measured output (clear path)
text | ff4ec4f0-9176-5412-b59e-a1d9f0927dd4 |  | textbox | Measured output (blocked path)
text | 8f63fac4-6c19-53cb-bf4e-bb8773cdbda1 |  | textbox | Measured output (filter in place)
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | cc690d4a-5632-5509-8eff-bc4b99060cda |  | textbox | Make:
text | 4c9b507c-31fd-559c-be1a-37071a82ce1d |  | textbox | Model:
text | 2d1ffcb8-048a-51df-b3f2-ab06a41f27a1 |  | textbox | Serial No:
text | 052e2dd8-f8f3-58d4-9b91-d5b6903ce964 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 21f94ce3-d3a7-51f4-aa34-c6bd7c98b3f1 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | c7e547d9-0c1f-5bd8-8c3a-7ebc2c14706f |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 6ee7b9ef-cdc9-5aaa-bbdb-08e309ce9267 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-03 Distribution Board Installation |  |  |  |  | Yes | ITR-E-03 Distribution Board Installation | 7978b564-7fb3-4bfa-b24d-9a527271e105
checkpoint-group |  |  | section | Distribution Board Installation
checkpoint-status |  |  | checkpoint | Inspect for mechanical damage from freight and handling
checkpoint-status |  |  | checkpoint | Check mounting arrangement is adequate.
checkpoint-status |  |  | checkpoint | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct.
checkpoint-status |  |  | checkpoint | Check IP rating is correct for location.
text | 150deeeb-d299-5b2a-ba50-218243f37e8d |  | textbox | IP Rating:
checkpoint-status |  |  | checkpoint | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order.
checkpoint-status |  |  | checkpoint | Confirm main isolator operates with associated switches and auxiliaries
checkpoint-status |  |  | checkpoint | Confirm main isolator operates all active conductors
checkpoint-status |  |  | checkpoint | Confirm main isolator and sub-circuit MCB’s can be padlocked open if required.
checkpoint-status |  |  | checkpoint | Check number and rating of sub-circuits as per design and specifications.
checkpoint-status |  |  | checkpoint | Ensure different Voltage segregation is correct.
checkpoint-status |  |  | checkpoint | Heaters installed and functioning.
text | 2abba178-bd10-59a1-9186-b6539e1f86fd |  | textbox | Record IR of heater circuit |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar.
checkpoint-status |  |  | checkpoint | Check internal cables properly terminated and labelled
checkpoint-status |  |  | checkpoint | DB properly labelled, sub circuit MCB correct rating and application
checkpoint-status |  |  | checkpoint | Check cable penetration is correct. (E.g. sealed correctly, correct size/type of glands)
checkpoint-status |  |  | checkpoint | Active, Neutral and Earth bar properly identified and labelled
checkpoint-status |  |  | checkpoint | DB legend card correct and updated, As-built
checkpoint-status |  |  | checkpoint | Confirm panel is readily accessible for inspection and maintenance.
checkpoint-status |  |  | checkpoint | Confirm panel is clean and tidy
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | cb461909-cb99-5cff-a710-62ab6821a1e0 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 42a7d62a-b0e1-5160-be41-42e9bfb1756f |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | e190a380-36c2-55f0-8cde-56f48fea4b4b |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | Toolbox Meeting |  |  |  |  | Yes | Toolbox Meeting | 8e103eca-896a-4955-838b-f88db4eeea6d
checkpoint-group |  |  | section | Toolbox meeting
checkpoint-no-status |  |  | checkpoint | Toolbox meeting
date | 2c0a993e-f99e-58f8-82b3-a8b9363cce24 |  | date | Date:
text | 431b7a52-59a8-592d-8820-f867681ed483 |  | textbox | Meeting location:
text | 54c1f10c-3596-5894-8da3-cdfd94eda52e |  | textbox | Meeting conducted by:
text | fb984eb8-0017-572c-9362-e4f83a0a5df8 |  | textbox | Meeting attendees:
text | 004fa6c9-9b51-585d-8e21-2455d8f3cfe8 |  | textbox | Today's work scope/Hazards
text | f34a2114-1481-54aa-8dcc-269d98a8e4ea |  | textbox | Hazard controls:
holdpoint |  |  | signoff | PICWS Signoff
checklist-sectioned |  |  | checklist | ITR-I-12 Telecommunications Equipment Panel |  |  |  |  | Yes | ITR-I-12 Telecommunications Equipment Panel | 937d7072-823c-4cd5-86e5-8c804942b163
checkpoint-group |  |  | section | Telecommunications Equipment Panel
checkpoint-status |  |  | checkpoint | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings:
checkpoint-status |  |  | checkpoint | Check tag number is in accordance with Telecommunications Equipment List.
checkpoint-status |  |  | checkpoint | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order.
checkpoint-status |  |  | checkpoint | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation.
checkpoint-status |  |  | checkpoint | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified.
checkpoint-status |  |  | checkpoint | Check panel air vents are clean and free of dust and dirt.
checkpoint-status |  |  | checkpoint | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar.
checkpoint-status |  |  | checkpoint | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar.
checkpoint-status |  |  | checkpoint | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s).
checkpoint-status |  |  | checkpoint | Check sealing of all cable penetration (where applicable).
checkpoint-status |  |  | checkpoint | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel.
checkpoint-status |  |  | checkpoint | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable).
checkpoint-status |  |  | checkpoint | Confirm panel is readily accessible for inspection and maintenance.
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | d1c36a00-275c-585f-91cb-272a5777d200 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | acadcf40-b99c-55ca-80fc-0499ce75439b |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 4dafa0b2-24c7-589d-b4c2-6a637b1b563d |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-10 Electrical Equipment Package |  |  |  |  | Yes | ITR-E-10 Electrical Equipment Package | 95198baf-c955-498c-87d6-937080599c4d
checkpoint-group |  |  | section | Electrical Equipment Package
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | Check equipment is correctly rated for the area.
checkpoint-status |  |  | checkpoint | Check if package is complete with all accessories.
checkpoint-status |  |  | checkpoint | No mechanical damage and paintwork in good condition.
checkpoint-status |  |  | checkpoint | All transportation supports, stops and fastenings removed.
checkpoint-status |  |  | checkpoint | Package fixing down bolts/shims/washers installed and tensioned.
checkpoint-status |  |  | checkpoint | Check package location.
checkpoint-status |  |  | checkpoint | Check package is installed on a level plane.
checkpoint-status |  |  | checkpoint | External cabling (if required) correctly installed.
checkpoint-status |  |  | checkpoint | Internal equipment installed and all tests complete and accepted.
checkpoint-status |  |  | checkpoint | Verify package using vendor and/or project P&IDs.
checkpoint-status |  |  | checkpoint | Check that equipment is correctly earthed.
text | 161d9ce9-9127-5408-bbd6-34252a94cfae |  | textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status |  |  | checkpoint | All spare entries blanked off with correct plugs.
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 85585ba4-8272-51db-b812-4885d40ee927 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | d2950fb1-2fbc-5623-8852-6b76678e2817 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | a64bd496-8818-5001-9908-0aee792c7322 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-I-06 Instrument Installation |  |  |  |  | Yes | ITR-I-06 Instrument Installation | 9610b598-18f9-469c-95e5-439b7a2df664
checkpoint-group |  |  | section | Checklist items
checkpoint-status |  |  | checkpoint | Check instrument nameplate details are correct in accordance with instrument index
text | bd75fef7-f263-5cb7-86b4-a99951830826 |  | textbox | Make:
text | 382baf95-287d-5fc0-92ac-12a04ab17449 |  | textbox | Model:
text | ba964efa-a3b6-51f0-ac88-f3139466ba12 |  | textbox | Serial No:
checkpoint-status |  |  | checkpoint | Ingress protection is suitable for area
text | 81bad210-c471-5619-b8b1-178bab93f8b2 |  | textbox | IP rating:
checkpoint-status |  |  | checkpoint | Instrument rating is correct for hazardous area
text | 69686a82-ba5b-5bea-9828-975517fddd54 |  | textbox | Haz Rating:
checkpoint-status |  |  | checkpoint | Instrument mounted correctly, elevation correct and free from vibration
checkpoint-status |  |  | checkpoint | Instrument is accessible for maintenance and clear of obstruction
checkpoint-status |  |  | checkpoint | Vent lines are directed into a safe area
checkpoint-status |  |  | checkpoint | Cable glands rated and installed correctly. Spare entries plugged with correctly rated plug
checkpoint-status |  |  | checkpoint | Impulse, hydraulic, pneumatics, lines and air headers correctly installed and supported
checkpoint-status |  |  | checkpoint | Instrument earthed according to client specification
checkpoint-status |  |  | checkpoint | Relevant ITRs for type of instrument completed in conjunction with this (if applicable)
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | e2b6de16-38cc-53cc-8cbb-eae65d62411d |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | ae0d86af-9ec2-59fe-b777-b26a84dac9f6 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 4124632a-eb32-5020-865b-48fdeeda8749 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | JHA - Job Hazard Analysis |  |  |  |  | Yes | JHA - Job Hazard Analysis | 9a3493e5-c97a-4747-a455-4992a656e300
checkpoint-group |  |  | section | Job details
checkpoint-no-status |  |  | checkpoint | Job details
date | 9228185a-89c1-5995-aba4-a07d5a11b1a5 |  | date | Date:
text | eacc1b8f-ab8c-54a2-b507-907595912fc3 |  | textbox | Permit No.
text | 7702ea5d-0e1a-5d6f-9e94-740cad51db93 |  | textbox | Job No.
text | 26d919e2-1edb-5173-8f4d-a7b5999c6185 |  | textbox | Site
text | b5fdcfd2-b7ea-55fe-b3e0-9056c50a7272 |  | textbox | Activity Location
text | 16394c92-0d3b-51c5-bedc-3da559ed035a |  | textbox | Asset:
text | 931da22e-27fb-5012-b91b-f9bbf65f2627 |  | textbox | Work Details:
checkpoint-group |  |  | section | Prompts for Hazards - Mark all that apply.
checkpoint-no-status |  |  | checkpoint | Prompts for Hazards - Mark all that apply.
button | b6f128e4-0f7c-5101-b56f-07452079e105 |  | button | Sparks/Open flame | YES,NO
button | 40e6f312-962f-5e05-b891-5ddd07f29f77 |  | button | Disabled safety device(s) | YES,NO
button | a6a02c8d-0b6a-5e3f-8eee-6dd28e30c492 |  | button | Uneven surfaces | YES,NO
button | 7a39ef1b-fe85-5b1d-805c-821a53f4ab8a |  | button | Fatigue, over-exertion | YES,NO
button | 811f69ce-54b2-5042-a9ea-950e1a1ffd35 |  | button | Crane movements | YES,NO
button | d52e8977-82a3-5fd2-9f3e-507e92607014 |  | button | Moving/Rotating parts | YES,NO
button | 9448b6f4-c49d-5343-8c55-433cf1257970 |  | button | Remote area, working alone | YES,NO
button | d81cc73a-fcbe-59f2-9f98-d0a2c58cec9c |  | button | Conflicting work/SIMOPS | YES,NO
button | 5022767d-f511-5d1f-886f-63fa73629f81 |  | button | Electrical arc flash | YES,NO
button | 5f26df29-b493-59fb-b59d-de0556ef9f59 |  | button | Sharp objects/materials | YES,NO
button | 43c8a7bf-f804-5f5d-b1d3-df157cfc86ba |  | button | Restricted/Difficult Entry/Exit | YES,NO
button | 032c7688-da8f-5ed8-bc7b-b5955b19f3b1 |  | button | Overhead obstacles | YES,NO
button | 00a0a7fc-3faf-5d60-a026-1f345f76d417 |  | button | Ignition sources (other) | YES,NO
button | 86e2901f-1142-594c-8570-3afba470a57b |  | button | Access/Egress | YES,NO
button | 6fc222d6-5b75-5fc7-9081-11c9bad4e7e4 |  | button | Water body | YES,NO
button | 30945f6a-d5c6-5841-a616-c91a4db4b622 |  | button | Live equipment | YES,NO
button | 8a702a5e-5e15-5e5e-9e3e-510b01793e5a |  | button | Slippery surfaces | YES,NO
button | aa9ee685-722e-5f7f-90e6-2ac21ef2f953 |  | button | Suspended loads | YES,NO
button | 7240cfc1-c230-5d6f-9773-e80c16686e94 |  | button | Hazardous substances (chemicals) | YES,NO
button | 08cdefea-d8d6-5fd2-8dff-0a4771d6ecdd |  | button | Use of non-intrinsically safe equipment | YES,NO
button | 042f2098-4003-58f7-819f-47e49a5cb287 |  | button | Weather extremes | YES,NO
button | 55dd10d8-df18-5fbf-ab3b-884e5209b101 |  | button | Moving vehicles | YES,NO
button | ea37c232-40ac-580c-809c-1fbbc0ff137f |  | button | Task related noise | YES,NO
button | 4f7c5b42-5242-5713-9aed-39f34714ba6e |  | button | Engulfment | YES,NO
button | b6aa45cd-210f-5b3e-92c7-014e572a8541 |  | button | General waste | YES,NO
button | ad86938d-6854-5c2a-ab92-ef4528e68f96 |  | button | Hazardous waste | YES,NO
button | 9da40ec0-edaf-58c5-a535-25d6da136ac3 |  | button | Hazardous/toxic substance, fumes, gas | YES,NO
button | dfa2c111-26f1-5bb1-9b38-68fafb81274b |  | button | Flammable materials - Gas, liquids, solids | YES,NO
button | 95e8906a-d45c-5387-b00a-34a045ebc288 |  | button | Reduced visibility, lighting | YES,NO
button | 6d115cb5-3f90-5807-b653-7fcb3256f499 |  | button | Electricity | YES,NO
button | bae20d28-1ae9-57f2-b82f-a5fb1b9bf22e |  | button | Static electricity | YES,NO
button | bb929ae5-8469-5e8c-9c15-90a221357ce0 |  | button | Work at height | YES,NO
button | 858c1f9c-1c9a-555b-9dbf-9c9cad55ffe5 |  | button | Underground services | YES,NO
button | 07f0bec1-d4fd-5003-9c5c-9a306b4bbf30 |  | button | O2 Deficiency/Excess | YES,NO
button | 52c87905-61e9-5993-95c5-ddadc0af16d6 |  | button | Temperature extremes | YES,NO
button | 41bd60a4-87b5-573d-959e-39a16af6696e |  | button | Heavy objects | YES,NO
button | 0c9f144d-d49e-51c0-8062-254666c31d26 |  | button | Radiation | YES,NO
button | c9746719-e611-5895-b846-0a131427ed8c |  | button | Potential energy - Tension/Compression | YES,NO
button | 5c68516c-bf28-51a1-a3e5-878049820f4b |  | button | Flying particles/Dust/Objects | YES,NO
button | 57578f59-cc9e-53de-8c6b-f2469d6287ec |  | button | Vehicle entry | YES,NO
button | 86d839b0-5056-5d81-a179-827bf1a4cf27 |  | button | Exposure to process temperatures. | YES,NO
checkpoint-group |  |  | section | Prompts for Initial Consequences - Mark all that apply
checkpoint-no-status |  |  | checkpoint | Prompts for Initial Consequences - Mark all that apply
button | 756faa05-c1da-5627-8fdd-c3d617c96c94 |  | button | Falling/Dropped objects | YES,NO
button | 9e577e94-776e-50c9-987f-3f20b8381d17 |  | button | Fall from height | YES,NO
button | 57fa9ba9-c21b-5116-bd18-aaf622ed1ddb |  | button | Trip/Slip/Fall | YES,NO
button | 481dc0e1-1e08-563f-933f-eda827eb7356 |  | button | Gas release | YES,NO
button | 0001850a-bfff-56ef-a368-afb1bdb7ba92 |  | button | Pressure release | YES,NO
button | ac045262-fe23-5321-b9f9-f74adbb006be |  | button | Struck by object | YES,NO
button | 1ea204c6-e8a0-5ff4-84bb-c3996c6adad6 |  | button | Exceeding tool limits | YES,NO
button | 1d6ad2ef-ddde-5858-9d36-23cbb658afc6 |  | button | Overloading people | YES,NO
button | d697977c-b84a-578f-a11e-e5c86eb49dae |  | button | Unplanned shutdown | YES,NO
button | 95e33453-419f-5334-9139-f8f3026e8496 |  | button | Exposure to O2 deficiency/excess | YES,NO
button | cdcb4652-c456-5544-9fdb-759750408622 |  | button | Exposure to hazardous substance | YES,NO
button | 1c02d50d-38a7-50ed-b57f-c9bcbc0b6399 |  | button | Entanglement | YES,NO
button | 6519c43c-1b44-5796-84c8-3abaa6622d71 |  | button | Flying objects | YES,NO
button | dbff42b2-3bfe-58a2-98cb-0d03b31a7536 |  | button | Loss of control | YES,NO
button | f628b834-1216-5fe5-ba08-8d65f7dee060 |  | button | Loss of containment | YES,NO
button | 1b97dcc0-9349-5c9b-af82-32956ad70690 |  | button | Excess exposure to Emissions, dust, fumes, noise, fibres, heat | YES,NO
button | 4b05786c-9985-5c5f-85b3-9fb371678567 |  | button | Loss of structural integrity | YES,NO
button | eddb7c35-cb39-5ac7-a794-7dbe84833010 |  | button | Equipment failure | YES,NO
button | 61fbcff5-d156-5f07-a859-1ced8fd766a9 |  | button | Uncontrolled ignition source | YES,NO
button | dc6c5b89-1130-5fc4-94dc-a2c058f36659 |  | button | Collision | YES,NO
button | f448059e-d8e6-592a-84a8-482f69e8583a |  | button | Ignition/Fire | YES,NO
button | 885f94b7-b377-5830-8e1b-a6d8bc27f254 |  | button | Back strain/Injury | YES,NO
button | 075b0ce2-9c4e-5cac-ba0e-3525dabe7816 |  | button | Burns | YES,NO
button | ef2aed22-58c0-52aa-a410-a64466d5e0cd |  | button | Heat exhaustion | YES,NO
checkpoint-group |  |  | section | Initial controls - Mark all that apply.
checkpoint-no-status |  |  | checkpoint | Initial controls - Mark all that apply.
label | e90b273b-7554-5511-991d-a43960328d82 |  | note | People controls | YES,NO
button | 3aa0dd32-dc76-5287-86ad-c134f5f3c5c5 |  | button | Safety/Fire watch person | YES,NO
button | beceb8ae-53ee-58b0-8bf6-97ff99b84e94 |  | button | Barriers/Flagging | YES,NO
button | ec6bbb4d-b62c-51a3-829c-fdf0325802be |  | button | Warning signs | YES,NO
label | 5596dfc5-d13f-58bc-82f6-bb903a129ec6 |  | note | Equipment controls | YES,NO
button | 55419019-6048-55b9-b26b-5e3c79fcd732 |  | button | Master tags and locks | YES,NO
button | d31e8785-d511-553d-a38f-8c768534f9e3 |  | button | Scaffolding for access | YES,NO
button | 140152cb-2781-5b2c-a6c8-fd8bf0a6fb03 |  | button | Radio communication | YES,NO
label | 0431fff5-6289-583d-876c-8c3125e6569e |  | note | Environmental controls | YES,NO
button | 78ec6283-da08-528e-b5db-9b8f2d13bded |  | button | Ventilation | YES,NO
button | 339f533d-55ab-58fa-8904-4a03828b5f5b |  | button | Lighting | YES,NO
button | 234c965a-4933-5d9a-a5f5-14880ac54331 |  | button | Gas Testing | YES,NO
label | 1f54ef9d-3cee-53cd-8712-134551a10328 |  | note | High risk controls | YES,NO
button | 25be095b-2b64-5d7e-ad31-c67d94b207f6 |  | button | WSCS Work permit | YES,NO
button | c382a687-740b-526b-b5fe-fbdcbe1b063e |  | button | WSCS Certificates | YES,NO
button | 3852be11-59e4-5ab6-a43c-fb29b2758ddc |  | button | Critical lift/Fall protection plan | YES,NO
button | a9809938-0ad6-5d84-b2e2-6b830c850414 |  | button | Specialised PPE | YES,NO
button | 3d9760c3-95f8-58db-8b96-4ad7b99062f6 |  | button | Spill kit | YES,NO
button | f7ca7e28-86e1-535f-a040-d18fa29c81c6 |  | button | Fire extinguisher | YES,NO
checkpoint-group |  |  | section | Signatures
checkpoint-no-status |  |  | checkpoint | Signatures
text | ba86b2fe-a84a-5847-b952-f3d2c2cb45e8 |  | textbox | Applicant name
holdpoint |  |  | signoff | Applicant signature
checklist-sectioned |  |  | checklist | ITR-I-13 Temperature Instrument Installation |  |  |  |  | Yes | ITR-I-13 Temperature Instrument Installation | 9e831e17-4f8f-41dc-8842-6e5e47c4171f
checkpoint-group |  |  | section | Temperature Instrument Installation
checkpoint-status |  |  | checkpoint | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint-status |  |  | checkpoint | Temperature instrument calibrated before installation (ITR-I-07 Instrument Calibration)
select | e760d504-4eeb-5c15-b765-6b6c1f79f83e |  | dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
checkpoint-status |  |  | checkpoint | Thermowell details including flange size are correct in accordance with the specifications
checkpoint-status |  |  | checkpoint | Internal depth of thermowell checked and recorded
text | 710c61eb-7c0e-5241-9370-fa8945563884 |  | textbox | Depth:
checkpoint-status |  |  | checkpoint | Bar material and tag number stamped on thermowell flange/exposed surface
button | 26e6b580-6d20-5a79-8eed-fe72dec465ed |  | button | Thermowell CE marked | YES,NO
checkpoint-status |  |  | checkpoint | EOL resistor fitted and correctly rated where applicable
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 79288316-5f7f-54e3-b6ba-cb0803f3b84e |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 6e2d14c6-624e-5a43-b160-60f9abd1cc67 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 942da81f-090c-546f-b498-0b5c868e3f27 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-flat |  |  | checklist | Record of Inspection (ROI) |  |  |  |  | Yes | Record of Inspection (ROI) | adba6f65-e3a3-4d59-8004-17345db23ba0
checkpoint-status |  |  | checkpoint | Please upload Record of Inspection here when complete (ROI)
checklist-sectioned |  |  | checklist | ITR-I-11 Cone and Thread Pressure Testing |  |  |  |  | Yes | ITR-I-11 Cone and Thread Pressure Testing | bd879bf2-dbf9-4ae5-9336-89c45cb4d770
checkpoint-group |  |  | section | General Data
checkpoint-no-status |  |  | checkpoint | General Data
text | ed179f9b-1f9a-5fc7-a35a-a90b0a23bde5 |  | textbox | Location:
text | 0026092e-2e64-52aa-adca-6d69c8a833b6 |  | textbox | Duty:
text | 822702ca-d1b2-5b46-b332-e42114442cb8 |  | textbox | Reference Drawings:
text | 76e0eedc-2756-55a2-b13d-5e097fb6778a |  | textbox | Hook-up drawing:
text | 92393313-80d2-5e0e-b4c4-a2330f90b1ce |  | textbox | Related instrument tag no:
text | 8e865aa7-4b85-5e8f-9d9b-9df005d662fc |  | textbox | Tube diameter and wall thickness:
text | 994fd601-e1d6-5674-958c-255a765e7130 |  | textbox | Instrument location drawing:
checkpoint-group |  |  | section | Checklist items
checkpoint-status |  |  | checkpoint | Tubing orientation as per hook up drawing.
checkpoint-status |  |  | checkpoint | Checked with a Torque Wrench and marked and tagged
checkpoint-status |  |  | checkpoint | Ensure Area is barricaded off to restrict unauthorized entry to personnel
checkpoint-status |  |  | checkpoint | Tube as per specification and hook up drawings.
text | eaff791b-76c2-50de-ae9f-d4edbfac645d |  | textbox | Max design pressure:
text | 3d395273-2578-51a7-afb3-4e9caa42ee19 |  | textbox | Test medium used:
text | 90b56ead-f8ed-551e-918e-12dde7419af9 |  | textbox | Record Testing pressure:
text | 7b52e4b7-61bf-526e-8151-5d7d69afcc96 |  | textbox | Test pressure duration: | Minutes
text | a2d03532-b398-5828-9df7-fa3423b30c60 |  | textbox | Test leak rate: | Litres/minute
checkpoint-status |  |  | checkpoint | Chart recorder used and attached (where applicable).
checkpoint-status |  |  | checkpoint | Confirm all Tubing lines have been pigged / cleaned.
checkpoint-status |  |  | checkpoint | Check all plugs are replaced (if removed), vents are closed, and isolation valves are in correct positions.
checkpoint-status |  |  | checkpoint | Ensure equipment is left clean and in a safe state for handover to operations to the standard of ITP-I-08 Cone and Thread cleaning procedure
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 4224808e-22c5-5f23-ba1f-c7034eefb2a7 |  | textbox | Make:
text | efaec329-939b-52ea-ace8-3717a9797226 |  | textbox | Model:
text | 28334279-c20b-57fd-b8a7-22fd88decfd5 |  | textbox | Serial No:
text | 9b7c7b59-5795-5969-82c1-d8a718246124 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 1b5560f9-ee82-5f12-b0ea-93b65cc056a0 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | bc781493-7cc9-5dff-9a0b-3b4627847843 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 964d6b5d-3866-522d-afe4-e0e365fdf115 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-01 General Electrical Equipment |  |  |  |  | Yes | ITR-E-01 General Electrical Equipment | bea4b48d-0be1-4a3d-b17c-82bcc42e682c
checkpoint-group |  |  | section | General Electrical Equipment
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | No mechanical damage and paintwork in good condition.
checkpoint-status |  |  | checkpoint | Installation is clean and tidy
checkpoint-status |  |  | checkpoint | Mounting arrangement correct
checkpoint-status |  |  | checkpoint | All internal cabling and wiring correctly installed and labelled.
checkpoint-status |  |  | checkpoint | External cabling is correctly installed and labelled.
checkpoint-status |  |  | checkpoint | Check that Equipment is correctly earthed.
checkpoint-status |  |  | checkpoint | Check gland, plate, frame & door earth continuity
checkpoint-status |  |  | checkpoint | All spare entries blanked off with correct plugs.
checkpoint-status |  |  | checkpoint | Check item is suitably rated for area (E.g. IP rating, Ex rating)
checkpoint-status |  |  | checkpoint | Conforms to Specifications and Drawings.
checkpoint-status |  |  | checkpoint | As-builts complete.
checkpoint-group |  |  | section | Electrical Checks
checkpoint-status |  |  | checkpoint | IR and Earth tests
text | f76fbe5a-8ad3-5ea9-bab2-294b7f4b6c24 |  | textbox | Insulation Resistance (P/N to E) |  |  | MegaOhms
text | fa6a30ac-c8a1-593c-97aa-914a2bddbe8a |  | textbox | Earth Continuity: |  |  | Ohms
text | 5ebe2ec7-8117-527d-9a32-6d1a0fe03be2 |  | textbox | Earth Bonding: |  |  | Ohms
text | 76c9be5e-65bf-545b-b712-63bfb549a7a2 |  | textbox | Other checks:
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 75df0a65-88ae-5935-a510-bb0b4aaf33d9 |  | textbox | Make:
text | ff971738-1cc3-503d-b8c5-5124de058e05 |  | textbox | Model:
text | 4afeba79-ef4c-5509-94f7-b1eace74eddc |  | textbox | Serial No:
text | 2d225650-8765-5325-b5ee-a7ff13cbaf0c |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | c5dbcf96-3c25-5f35-9c71-fea57cd0484e |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 5c5d8438-1034-5a6e-bbb7-92a5746f2441 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 2260db83-7b15-58a0-b932-7ff23b0e6fa9 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-11 Generator Package (LV) |  |  |  |  | Yes | ITR-E-11 Generator Package (LV) | cf08128c-93c1-4474-ba7d-c42837448cc0
checkpoint-group |  |  | section | Generator Package (LV)
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | No mechanical damage and paintwork in good condition.
checkpoint-status |  |  | checkpoint | Check terminal boxes and glanding correct.
checkpoint-status |  |  | checkpoint | Check earthing is correct.
text | 71fc251a-c4aa-59fc-9fdb-110b56af6be9 |  | textbox | Test and confirm the generator earth to local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status |  |  | checkpoint | Instruments correctly installed.
checkpoint-status |  |  | checkpoint | Heaters correctly installed.
text | 7299bb69-28a0-53d4-a03b-b7249d07922c |  | textbox | Heater circuit Insulation Resistance: |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Check unit for cleanliness.
checkpoint-status |  |  | checkpoint | Check manual operation of selector switches, MCB, push buttons etc.
checkpoint-status |  |  | checkpoint | External cabling correctly installed.
checkpoint-status |  |  | checkpoint | Protection of live parts adequate.
checkpoint-status |  |  | checkpoint | Main terminal box complete and terminations correct torque.
checkpoint-status |  |  | checkpoint | Ensure direction of rotation is clearly marked.
checkpoint-status |  |  | checkpoint | Check gasket and seals are not damaged.
checkpoint-status |  |  | checkpoint | Unused cable entries are correctly sealed.
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 2f03a7c8-0291-59eb-8165-b9f0214aad64 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 8d01a201-bec2-5adc-b3a0-bddbc925af45 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 91469ecc-b196-54c6-b2e8-1b35a653e637 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-12 Electrical Earthing |  |  |  |  | Yes | ITR-E-12 Electrical Earthing | d3e509b2-f5a9-4401-b282-cd8df013d96e
checkpoint-group |  |  | section | Earthing System
checkpoint-no-status |  |  | checkpoint | Earthing System
text | ca6df6b9-06cd-5e26-a348-b1690d6627fb |  | textbox | Electrode type
text | df24737b-47ed-5fcf-a9a8-4a7c9c4e6aee |  | textbox | Electrode length/size
text | a42db1e0-4fa7-5a97-b00f-f0275bb27d47 |  | textbox | Location of Electrodes
text | 63fce004-a79c-5f87-b48d-2018e25b4f8e |  | textbox | Method of installing electrode
text | f2980ac1-706e-5a81-a35c-78afe72d240d |  | textbox | Method of attaching to electrode (e.g Clamp, Cad Weld, Lug & Bolt)
text | 8b41752e-1664-50b9-819f-1bf07625aeca |  | textbox | Number of electrodes
checkpoint-group |  |  | section | General Items
checkpoint-status |  |  | checkpoint | Confirm earth grid layout
checkpoint-status |  |  | checkpoint | Ensure grid layout is in accordance with design drawings
checkpoint-status |  |  | checkpoint | Record number of grid interconnections
checkpoint-status |  |  | checkpoint | Ensure all metalwork is earthed as required
checkpoint-status |  |  | checkpoint | Check welding of earth bosses and associated surface finish
checkpoint-status |  |  | checkpoint | Ensure that earth cables/conductors have adequate mechanical protection i.e. conduits, kick-plates, PVC duct through concrete etc. at points of high exposure.
checkpoint-status |  |  | checkpoint | Ensure that brazing or welding of all joints has been completed correctly.
checkpoint-status |  |  | checkpoint | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, Cad (thermal) welds and earth bosses
checkpoint-status |  |  | checkpoint | Ensure that earth electrodes are located within a protected, covered and identified surround.
checkpoint-status |  |  | checkpoint | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating.
checkpoint-status |  |  | checkpoint | MEN Link Installed (If applicable)
checkpoint-group |  |  | section | Earthing Conductors
checkpoint-status |  |  | checkpoint | Ensure that earthing conductor size is correct in accordance with approved installation drawings.
checkpoint-status |  |  | checkpoint | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly.
checkpoint-status |  |  | checkpoint | Check terminations to ensure that all connections are correct, clean, greased and tight.
checkpoint-status |  |  | checkpoint | Check that all bi-metal connections have been performed correctly to manufacturer's requirements.
checkpoint-status |  |  | checkpoint | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar.
checkpoint-status |  |  | checkpoint | Ensure that earth cable identification markings are in place.
checkpoint-status |  |  | checkpoint | Ensure that earth connections are not multi-coiled or 'pig-tailed' but are terminated as straight as possible.
checkpoint-group |  |  | section | Earth Bar Installation
checkpoint-status |  |  | checkpoint | Check for correct assembly of equipment
checkpoint-status |  |  | checkpoint | Check fixings and mounting points conform to project specification and are secure
checkpoint-status |  |  | checkpoint | Check for equipment levels and alignment
checkpoint-group |  |  | section | Earth System Testing
checkpoint-status |  |  | checkpoint | Using an Earth Resistance tester, measure earth resistance between electrodes or main earth bars & the earth body.
text | a337325b-c0e1-559b-88c6-2c772545e16d |  | textbox | Record results:
checkpoint-status |  |  | checkpoint | Measure earth continuity from each earth point and/or equipment earth frame to the nearest electrode or main earth bar
label | 655f4a9d-a9ed-5330-b185-86c134776c05 |  | note | Note: Sketch a layout of earth electrodes showing electrode numbers and distances and attach below
checkpoint-status |  |  | checkpoint | Earth Grid Test Results (electrodes connected)
text | a44ef334-5454-5f42-9dae-201745fa1efe |  | textbox | HV Earth grid:
text | a90012b6-d687-5da7-9bf2-edffaf39e7fd |  | textbox | LV Earth grid:
text | 2c588b10-04cc-5539-aa4b-a8be61f3ef89 |  | textbox | Combined HV/LV Earth grids:
text | 681b7925-8549-5e62-9f87-12e3e047be64 |  | textbox | Instrument Earth:
checkpoint-status |  |  | checkpoint | Earth Resistivity Tests
text | 8960be3b-79f9-5d14-bece-c6ffde6a3bd9 |  | textbox | From (Main Earth Bar or Auxiliary Earth Point): |  |  | To Earth Body
text | 8c44d7bd-6834-5609-b61b-bb3f9d9c3534 |  | textbox | Result: |  |  | Ohms
text | 731f02d8-2611-5232-8c5f-63a49314653c |  | textbox | From (Main Earth Bar or Auxiliary Earth Point): |  |  | To Earth Body
text | 3e34d55d-e2b5-5312-a130-ed45b197c72f |  | textbox | Result: |  |  | Ohms
checkpoint-status |  |  | checkpoint | Earth Continuity Tests
text | a93bd2d5-5318-559e-b9ba-511f052bf50e |  | textbox | From: (Main Earth Bar Location)
text | 2cd100b0-08fe-5795-8beb-2015c7f85fa6 |  | textbox | To: (Earth Electrode number/description)
text | d959fa4b-df94-5093-991f-5791164ab45b |  | textbox | Record Resistance: |  |  | Ohms
text | b8588f97-dd69-5ffe-8fa7-45b0caf26404 |  | textbox | From: (Main Earth Bar Location)
text | b1a99a09-cef8-545a-889b-2e74900a0065 |  | textbox | To: (Earth Electrode number/description)
text | 687e9de1-d6f2-58d2-b5d0-e3f291b76d7b |  | textbox | Record Resistance: |  |  | Ohms
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 928767e8-f29c-5cca-8baa-0116694e5c97 |  | textbox | Make:
text | 0f26107b-921f-5ef7-81ee-e21e96fff150 |  | textbox | Model:
text | 242173e3-aba4-5c79-a3aa-dcecc59e3ebc |  | textbox | Serial No:
text | d2fbc42d-945d-5d20-8f76-1e63606a92d3 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | f86d08a9-a37a-5aa2-bb8d-cd5206866fc3 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 7d23845b-e0ea-5ba0-870b-516d1e2abe51 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 420e469c-bfb7-5961-a5c2-e172bc102950 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-09 Electrical Switch Rooms |  |  |  |  | Yes | ITR-E-09 Electrical Switch Rooms | d45e2201-35f0-495b-a964-dab17de094c4
checkpoint-group |  |  | section | Electrical Switch Rooms
checkpoint-status |  |  | checkpoint | Substation construction finished
checkpoint-status |  |  | checkpoint | All floor, wall & ceiling penetrations sealed.
checkpoint-status |  |  | checkpoint | Danger, warning & resuscitation signs installed
checkpoint-status |  |  | checkpoint | All equipment installed
checkpoint-status |  |  | checkpoint | Lighting & general power installation complete
checkpoint-status |  |  | checkpoint | All earth busbars installed satisfactorily & connections tight
checkpoint-status |  |  | checkpoint | All telecommunication equipment is installed & operational
checkpoint-status |  |  | checkpoint | Smoke / Heat detectors installed (Including Vesda / Alarm Panel)
checkpoint-status |  |  | checkpoint | Substation fire alarm panel installed
checkpoint-status |  |  | checkpoint | HVAC equipment installed & operational
checkpoint-status |  |  | checkpoint | Illuminated exit signs installed & operational
checkpoint-status |  |  | checkpoint | Hand-held fire extinguishers installed with correct type available
checkpoint-status |  |  | checkpoint | All doors and locks operational (including emergency)
checkpoint-status |  |  | checkpoint | All keys available and handed to Commissioning E&I Superintendent
checkpoint-status |  |  | checkpoint | All safety equipment supplied – rubber mats, voltage sticks etc
checkpoint-status |  |  | checkpoint | Single line diagram detailing main power is fitted to wall
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 108e790d-d3da-5a3e-8b25-8894e732d44b |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | d4c2b627-e59c-5d37-bdb7-c9329da78f68 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | bbb21d81-54b4-5066-8a98-a17b289c83f2 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-flat |  |  | checklist | ITR-E-04 Schedule of Test Results DB |  |  |  |  | Yes | ITR-E-04 Schedule of Test Results DB | d9155e08-634f-4b56-b5fe-9968d86f4e48
checkpoint-status |  |  | checkpoint | Upload completed ITR scans
checklist-sectioned |  |  | checklist | ITR-I-10 Cone and Thread Tubing Installation |  |  |  |  | Yes | ITR-I-10 Cone and Thread Tubing Installation | da656b82-d4bf-4cdc-bee8-46fe756c0f4f
checkpoint-group |  |  | section | General Data
checkpoint-no-status |  |  | checkpoint | General Data
text | a0ba7f1b-6ad5-5438-ade4-4418995d1e4b |  | textbox | Location:
text | 887a4963-0ffd-5ec0-8c5c-724534cd7c0a |  | textbox | Duty:
text | 329cce4e-66d3-5baa-b994-9d247cb7fa08 |  | textbox | Reference Drawings:
text | 7113fa5a-9e12-597d-9542-8c56e1541c41 |  | textbox | Hook-up drawing:
text | c6bbe1e7-cda9-57c3-adda-5ad7bc385eae |  | textbox | Related instrument tag no:
text | d6ed4943-fa77-5efb-9593-3d2b7b16af9a |  | textbox | Tube diameter and wall thickness:
text | b92d3639-fddf-566f-b149-7538d47d10e8 |  | textbox | Instrument location drawing:
checkpoint-group |  |  | section | Cone and Thread installation - Stainless fittings
checkpoint-status |  |  | checkpoint | Correct thread compatibility and engagement
checkpoint-status |  |  | checkpoint | Correct thread lubricant used on fittings
checkpoint-status |  |  | checkpoint | Check fitting collar prior to connection - 1 to 2 threads visible at cone
checkpoint-status |  |  | checkpoint | Tube installation follows the client specification.
label | 83fe0c4c-ee45-52ff-ab7b-9a0134e42cab |  | note | (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables)
checkpoint-status |  |  | checkpoint | Tube bent correctly, sufficient straight section into fitting
checkpoint-status |  |  | checkpoint | Tube cut clean and straight, de-burred, reamed, and blown through
checkpoint-status |  |  | checkpoint | Lubricate collar, cone and gland thread at assembly to prevent galling
checkpoint-status |  |  | checkpoint | Correct Tube nut used for the right sized tube
checkpoint-status |  |  | checkpoint | Ensure No thread tape or sealant are used on tube nuts
checkpoint-status |  |  | checkpoint | Tube fitting hex torqued to ensure correct tightness, marked with pen
checkpoint-status |  |  | checkpoint | Ensure Weep hole is unobstructed and clean
checkpoint-status |  |  | checkpoint | In service leak test performed and passed
checkpoint-status |  |  | checkpoint | Fitting completion tag completed and applied to each fitting
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | bd609d13-508f-50cc-aef0-9d2d8f29de0d |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | fde93e89-aa33-5cf2-86ff-4a7ac45c1b78 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 6993f118-da73-5828-84d5-8d3e1559fd6d |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-15 UPS Installation |  |  |  |  | Yes | ITR-E-15 UPS Installation | e000fc79-19be-40b4-9cde-98a608b0ea05
checkpoint-group |  |  | section | UPS Installation
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | Check for mechanical damage.
checkpoint-status |  |  | checkpoint | Panel IP rating is correct:
text | 2a141c7a-c8eb-5c5a-a7f5-2a6569885810 |  | textbox | IP Rating: |  | IP
checkpoint-status |  |  | checkpoint | Holding down arrangement and seat alignment correct.
checkpoint-status |  |  | checkpoint | Panels aligned correctly.
checkpoint-status |  |  | checkpoint | Earth alignment to vendor specification & connecting link bolts torqued to the manufacturers recommendations & marked.
checkpoint-status |  |  | checkpoint | External bonding correct
checkpoint-status |  |  | checkpoint | Bus bar alignment to vendor specifications & connecting link bolts torqued to the manufacturers recommendations & marked.
text | f9e83d5e-1367-5bf8-afbf-263d275ca034 |  | textbox | Nm.
checkpoint-status |  |  | checkpoint | Phase identification correct.
checkpoint-status |  |  | checkpoint | Instrument, indication lamps & interlocks correct.
checkpoint-status |  |  | checkpoint | Main switches, contactors, fuses etc. sized & identified correctly as per Single-
checkpoint-status |  |  | checkpoint | Line Drawings.
checkpoint-status |  |  | checkpoint | Check main isolator switch operation.
checkpoint-status |  |  | checkpoint | Check bypass isolator switch operation.
checkpoint-status |  |  | checkpoint | Check DC UPS battery isolator switch operation.
checkpoint-status |  |  | checkpoint | COM Interface & Mod Link.
checkpoint-status |  |  | checkpoint | Padlocking facilities correct.
checkpoint-status |  |  | checkpoint | Check internals for cleanliness.
checkpoint-status |  |  | checkpoint | Check manual operation of selector switch, MCB, push button, etc.
checkpoint-status |  |  | checkpoint | Incoming cable correctly installed, terminated & supported.
checkpoint-status |  |  | checkpoint | Unused cable entries sealed.
checkpoint-status |  |  | checkpoint | All internal cabling & wiring neat, correct & tight.
checkpoint-status |  |  | checkpoint | Heaters correctly installed.
checkpoint-status |  |  | checkpoint | Fans correctly installed.
checkpoint-status |  |  | checkpoint | Verify continuity of earth bar to frame
text | cf1a23af-88aa-555d-9537-7f2a655a00e2 |  | textbox | Earth continuity: |  |  | Ohms
checkpoint-status |  |  | checkpoint | Check Busbar Insulation resistance between Phases & Phases & Earth (690V-2500VDC, 400V -1000VDC)
text | 0219232e-50f3-5082-aa7a-3634251e3c98 |  | textbox | L3-L2 |  |  | MegaOhms
text | 276fdb2d-00c7-5044-9937-bf277a046391 |  | textbox | L3-L1 |  |  | MegaOhms
text | b298dc4f-3061-564b-9fd5-aa843953c639 |  | textbox | L3-N |  |  | MegaOhms
text | 97cd0bd8-b322-50f8-a61b-3f2e9e269777 |  | textbox | L2-L1 |  |  | MegaOhms
text | 3c6c86c3-54b6-5322-bcef-1d1291131f36 |  | textbox | L2-N |  |  | MegaOhms
text | 50eb375f-2010-5708-b3d6-6888ee11766b |  | textbox | L2-E |  |  | MegaOhms
text | 4ebd1b37-e82d-5c77-95c1-0e38df9de16a |  | textbox | L1-N |  |  | MegaOhms
text | 91eef8c5-e9dd-564d-908f-c71650a7610b |  | textbox | L1-E |  |  | MegaOhms
text | 6aa59f66-d4e9-54d6-b5f5-fd464e239f4b |  | textbox | N-E |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Drawings marked up with relevant changes
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | a5142dd1-9f1e-50dc-8a2b-735d44e8ae92 |  | textbox | Make:
text | fe9d2331-0c5b-50b1-aa9d-00b14c596bc4 |  | textbox | Model:
text | 1e6089be-960d-5216-a7c2-23615ac91a9d |  | textbox | Serial No:
text | cfeefb69-c022-5279-b011-cca5cbbe4fe3 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 1c98d9e2-a4ca-54d2-896b-2d663500be2c |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 9ebefe6c-80d1-5a9c-b7d0-c9a5eb51c489 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 54242d2b-0a19-5c70-a3ec-921509eff4ff |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-16 Lightning Protection |  |  |  |  | Yes | ITR-E-16 Lightning Protection | ea9bb401-86ae-40a8-a259-79d63b04a59e
checkpoint-group |  |  | section | Lightning protection checks
checkpoint-no-status |  |  | checkpoint | Lightning protection checks
label | 8a5ad587-73bb-5fa0-9cf5-3aefa4b730dd |  | note | These checks shall be conducted in accordance with the requirements of AS/NZS 1768:2007
checkpoint-status |  |  | checkpoint | Check lightning conductor is 2 metres or more above the entire protected area
checkpoint-status |  |  | checkpoint | Check the materials and equipment used for the down conductors are suitable
checkpoint-status |  |  | checkpoint | Check the down conductors are routed, located and electrically bonded as required
checkpoint-status |  |  | checkpoint | Check all installed components are firmly secured
checkpoint-status |  |  | checkpoint | Check the method of protection against electric shock, including the measurement of distances
checkpoint-status |  |  | checkpoint | Check the resistance of all connections at the location of the connection. The resistance of each connection shall not exceed 0.05 Ohm
checkpoint-status |  |  | checkpoint | Earth termination system resistance is correct
text | f1e2d80d-6892-5bb7-b905-cd8c84698afc |  | textbox | Resistance value: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Insulation resistance of the electrical installation
text | c54feb50-ebf1-537c-a202-bac8a24f5e12 |  | textbox | IR |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Continuity of main and supplementary bonding
text | 91d38429-fa3b-51df-9c77-fb63e4306b15 |  | textbox | Main bonding: |  |  | Ohm
text | ea933a29-1fa7-5586-9a39-4f9f3756199b |  | textbox | Supplementary bonding: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Check earth termination systems are interconnected
checkpoint-status |  |  | checkpoint | Check isolating and switching devices correctly located
checkpoint-status |  |  | checkpoint | Check warning signs and diagrams are installed
checkpoint-status |  |  | checkpoint | Check accessibility for operation and maintenance
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 32ee0bc6-77c9-533d-a30b-861f60abf09b |  | textbox | Make:
text | efd80735-7201-5f03-85cb-fcc852026ac4 |  | textbox | Model:
text | 9ed7dcfe-4f80-52cd-bdc5-6ead6e6dfc9a |  | textbox | Serial No:
text | 6c0e34f8-9d37-53a3-bf7b-9289f37ac2f2 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 443eacdd-ea82-549c-841a-10754b8983f1 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 5c7ce0b1-f85b-5ef4-bb13-3d65ce073986 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 39e0b6a8-c476-5799-90e9-b60ebb90dfc6 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-I-08 Instrument Pre-Commissioning |  |  |  |  | Yes | ITR-I-08 Instrument Pre-Commissioning | eaf4c1e4-a7c9-4e44-9129-bdf4bd7e18b1
checkpoint-group |  |  | section | Checklist items
checkpoint-status |  |  | checkpoint | Verify transmitter loop connection - Remove wre on transmitter and confirm at Control System interface
checkpoint-status |  |  | checkpoint | Relevant individual control system/ESD loops have been checked and test sheets completed
checkpoint-group |  |  | section | Analogue Input:
checkpoint-no-status |  |  | checkpoint | Analogue Input:
text | d000d487-5c71-5e58-83d4-b63fe91047db |  | textbox | Input range & units:
text | 3dc2d61a-67d1-5eb4-86f3-475770697b02 |  | textbox | Indication range & units:
checkpoint-status |  |  | checkpoint | 0% Rising
text | 7f07d84d-e405-52fe-9886-658acf3fa9f1 |  | textbox | Input Signal:
text | 9c76c1a7-ea1f-52ca-ac71-cffbf9573ae3 |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 25% Rising
text | 3e322911-4fcc-5c5c-ad98-9ef3366c5b4b |  | textbox | Input Signal:
text | 7bb8c592-3cc9-57fb-8b74-8ec35d3fe3ef |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 50% Rising
text | 0b7bb9e2-6cb5-57ff-8c6a-8ae125e9e4de |  | textbox | Input Signal:
text | 2eef6022-c5cd-548d-88bd-e9b2b615e429 |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 75% Rising
text | 0755e3f9-eca2-5dab-88bf-027e94cf9cd8 |  | textbox | Input Signal:
text | de91d6f5-1cce-5ef0-8dc4-0035134eea0e |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 100% Peak
text | dd4caa10-39b7-58e9-907b-56b1bddb5ba0 |  | textbox | Input Signal:
text | 0e4aa82d-65ae-5b71-a94b-eed8a76cde7b |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 75% Falling
text | cfa45924-214a-5c76-af6a-223aba5f1f76 |  | textbox | Input Signal:
text | b8bbf4ef-cd5b-52c0-8d40-3978a17ba79e |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 50% Falling
text | 0eb37ab6-5245-5f62-b9ff-1da94b154fcd |  | textbox | Input Signal:
text | 780b56f7-47c4-5a13-acb6-2543110b6f15 |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 25% Falling
text | 805e8d05-2b74-5f79-a537-6ce3c91165bd |  | textbox | Input Signal:
text | ffb5513f-01dc-52c0-a692-e53ce4893cab |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 0% Falling
text | e078b525-9ed2-56c4-859b-252f4507210a |  | textbox | Input Signal:
text | 3f0d05a9-8e32-5ca0-abe0-e91b14aae38d |  | textbox | Control Interface Indication:
checkpoint-group |  |  | section | Digital Input/Analogue Alarm Trip Points
checkpoint-status |  |  | checkpoint | Alarm Lo:
text | b1ac3ae1-a288-59db-8dde-d915c997f7ca |  | textbox | Alarm setting
text | babae84a-2a69-5802-9d45-b5c0f5f4744c |  | textbox | Measured Alarm Point
text | f77a1315-dc86-56aa-9c0b-3da66ae3ecd3 |  | textbox | Filter/Time Delay
text | e14a8cee-ee76-5b31-b3a7-d1f6fc9d5602 |  | textbox | Result
checkpoint-status |  |  | checkpoint | Alarm Lo-Lo:
text | fb4b2825-4b34-578e-8ea5-a5f5ef518cf4 |  | textbox | Alarm setting
text | d26bb926-4396-5821-b36e-5e5c66014b90 |  | textbox | Measured Alarm Point
text | 0226baf1-028a-57c8-a562-ed4630bf9356 |  | textbox | Filter/Time Delay
text | 82530f39-30c6-5fd8-a9c0-cdb7e6cc4c82 |  | textbox | Result
checkpoint-status |  |  | checkpoint | Alarm Hi:
text | 47f22604-676b-5e5a-892a-1260c5614280 |  | textbox | Alarm setting
text | 0c687e4a-289d-5947-b7d8-043cec865a08 |  | textbox | Measured Alarm Point
text | ad1a99c5-dd20-54d6-959b-21075f830f39 |  | textbox | Filter/Time Delay
text | 34aa4996-d509-5790-a76a-712b7a4e883c |  | textbox | Result
checkpoint-status |  |  | checkpoint | Alarm Hi-Hi:
text | 514f1ad9-e977-5557-9f65-381503f03fab |  | textbox | Alarm setting
text | 6a0917ac-4d1a-5f6e-937d-a54409ad66c8 |  | textbox | Measured Alarm Point
text | d96d63b8-85f8-591d-a4ed-5461eb8fa398 |  | textbox | Filter/Time Delay
text | 83cb22d6-d6ca-5cf3-9b8e-29048b1744a9 |  | textbox | Result
checkpoint-status |  |  | checkpoint | Control loop set points correct:
text | c6b4b4f7-b1bc-572a-8420-a008b7c9ef6c |  | textbox | Set Point 1:
text | 44bccb99-d5ee-508d-b596-1e844d839f4a |  | textbox | Set Point 2:
text | f9442303-6cd2-5619-b4cf-991d4768d266 |  | textbox | Set Point 3:
text | f332c07c-f369-51fb-ace6-aa2a6014f0a0 |  | textbox | Set Point 4:
checkpoint-group |  |  | section | Startup, Shutdown and Override functions
checkpoint-status |  |  | checkpoint | Control system graphic display
checkpoint-status |  |  | checkpoint | Control system point display
checkpoint-status |  |  | checkpoint | ESD graphic display
checkpoint-status |  |  | checkpoint | Alarm Recording and Text
checkpoint-group |  |  | section | Additional checks
checkpoint-status |  |  | checkpoint | Control system display and alarms are correct as per control functions
checkpoint-status |  |  | checkpoint | Transmitter fail direction and burnout are to spec (Upscale/Downscale)
checkpoint-status |  |  | checkpoint | Switch action verified, including power loss
checkpoint-status |  |  | checkpoint | Drawings, documents and As-Builts scanned and attached
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 2ca2128a-7ad0-564f-a22d-ddc21233d1eb |  | textbox | Make:
text | a697f61f-295d-5caf-8311-05548361916c |  | textbox | Model:
text | 74ca1807-d83c-5c70-9ac2-d39fedb6bc09 |  | textbox | Serial No:
text | 3029a937-3d36-5e23-9783-8daeee4b202b |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | b1e242b3-097b-5a44-a357-34e514390f3e |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 79a690cb-6b6c-5d8a-9461-761e490d1de4 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 403ad186-24c7-5c98-bf78-367bcc9448b5 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-E-08 Heat Tracing Circuit |  |  |  |  | Yes | ITR-E-08 Heat Tracing Circuit | ecfdcc07-544f-4065-8d9b-e4978cc71639
checkpoint-group |  |  | section | Heat Tracing Circuit
checkpoint-status |  |  | checkpoint | Circuit installed, connected & identified according to design drawings.
checkpoint-status |  |  | checkpoint | End caps and connection kits correctly installed.
checkpoint-status |  |  | checkpoint | All junction boxes properly supported, and all cables protected against sharp edges.
checkpoint-status |  |  | checkpoint | Cable termination and glanding at all junction boxes correct.
checkpoint-status |  |  | checkpoint | All spare entries blanked off correctly.
checkpoint-status |  |  | checkpoint | Insulation resistance to earth after installation:
text | 7e380da2-b744-53e9-9817-4ec794e2d468 |  | textbox | Insulation resistance: |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Phase to Neutral resistance
text | 2a56cf48-3daa-5144-a8ae-40ff453b1b67 |  | textbox | Insulation resistance: |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Equipment certification meets the area classification requirements.
checkpoint-status |  |  | checkpoint | Confirm warning labels are fixed on outside of pipe lagging
checkpoint-status |  |  | checkpoint | Check correct rating of protection device against design drawings.
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 2e0f6956-6283-59fc-956b-9ba1011e0efa |  | textbox | Make:
text | e61b7da6-a893-562c-85d0-212a4db9ed79 |  | textbox | Model:
text | 2cff21ac-1f7b-5d5a-a9c0-f7dccc139b06 |  | textbox | Serial No:
text | ba440310-2aca-540c-8c6a-53e68d85b7fc |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 6b3084eb-c37c-56dd-b916-7d6d8d0c7b06 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | ccc77095-e0a2-528c-a27a-93c82c093ddf |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 190de20e-a2c8-55ea-9e91-b88232c71e73 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-I-07 Instrument Calibration |  |  |  |  | Yes | ITR-I-07 Instrument Calibration | fb769912-7b7f-4367-bbf0-f513cdb86c8b
checkpoint-group |  |  | section | Required Data
checkpoint-no-status |  |  | checkpoint | Required Data
text | 2db3fb8e-f317-567a-8b01-01ef30bbb3e5 |  | textbox | Type and Size:
text | 47e6bb8f-3999-5737-a013-1c1b4c4d4455 |  | textbox | Make:
text | 512b2473-4bc7-5ede-a480-78965d8edcec |  | textbox | Serial No:
text | 5e8118d3-a441-5c76-b788-c7ed36cc0e5c |  | textbox | Instrument Type:
text | f41fda0c-bab7-5855-8559-9431ec48153a |  | textbox | Instrument designation/equipment no
text | 452174c6-490f-5ad9-9b1f-4aee2654d161 |  | textbox | Calibration interval
text | fd5f4803-4e2f-5528-9a40-8c26dca35ba6 |  | textbox | Calibration method
text | e03e8d48-b1ad-5966-8fba-0c44cc893138 |  | textbox | Calibrated at
checkpoint-group |  |  | section | Instrument Power Supply
checkpoint-no-status |  |  | checkpoint | Instrument Power Supply
select | 045f01e5-b856-5515-a656-fdf529d22445 |  | dropdown | Supply type | VAC, 2 Wire DC, Other, None
text | 974489de-4be4-5899-a0e4-eb10a8548010 |  | textbox | Supply value:
checkpoint-status |  |  | checkpoint | Calibration sheet completed and attached below
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | a7e53511-0adc-5322-bd13-99c9bbbca308 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 22ade89a-768d-5c85-b031-53ee099d310c |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | d6313009-9025-55c9-9d02-5a7ff1d82bba |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-I-05 Analogue Valve & Ancillaries (Pre-Installation) |  |  |  |  | Yes | ITR-I-05 Analogue Valve & Ancillaries (Pre-Installation) | fdceee66-ff5c-4f0f-9c0b-b94d16e01f47
checkpoint-group |  |  | section | Equipment
checkpoint-status |  |  | checkpoint | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No.
checkpoint-status |  |  | checkpoint | Equipment checked for additional items as applicable
checkpoint-status |  |  | checkpoint | Complete ITR-I-05A and attach
checkpoint-group |  |  | section | Valve
checkpoint-no-status |  |  | checkpoint | Valve
text | c3889bb5-85ef-543c-89bd-d4443f1737dd |  | textbox | Size:
text | 340cc3ca-df89-5124-833a-8efe2e67895c |  | textbox | Flange type:
checkpoint-status |  |  | checkpoint | Material certification correct
checkpoint-status |  |  | checkpoint | Trim material correct
text | 860b12bd-ef81-50fc-8807-5aa96f7b51a1 |  | textbox | Rating:
text | 782a7599-871b-539e-9949-a2a444bb2c66 |  | textbox | Service:
checkpoint-status |  |  | checkpoint | Body material correct
text | 3ae7f35d-bc2d-5c09-9e74-4f8468631bb7 |  | textbox | Leakage class:
checkpoint-group |  |  | section | Actuator
checkpoint-no-status |  |  | checkpoint | Actuator
text | bbe802a6-63c6-527f-82f2-004a795ea454 |  | textbox | Input range:
checkpoint-status |  |  | checkpoint | Failure action
checkpoint-status |  |  | checkpoint | Hand wheel operation correct
checkpoint-group |  |  | section | Positioner
checkpoint-no-status |  |  | checkpoint | Positioner
text | b47cb39b-c20a-54b9-b5b0-80fb527ca52f |  | textbox | Signal range
text | 1c3a9aef-a725-5cfd-909b-30e9138d68d0 |  | textbox | Output range
checkpoint-group |  |  | section | I/P Converter
checkpoint-no-status |  |  | checkpoint | I/P Converter
text | e4537463-dd53-5cda-bf90-b5080dce552b |  | textbox | Signal range
text | 000b9146-8345-5f72-b5a8-8d2ef328fbff |  | textbox | Output range
checkpoint-group |  |  | section | Filter/Regulator
checkpoint-no-status |  |  | checkpoint | Filter/Regulator
text | d35bf8df-939c-5be5-b535-7df08cc7109a |  | textbox | Range |  |  | kPa
text | 04e23a80-ccd6-5d36-ae36-9e0056595bfd |  | textbox | Pressure setting |  |  | kPa
checkpoint-group |  |  | section | Fail Action
checkpoint-no-status |  |  | checkpoint | Fail Action
select | 86fcf9f6-f7ad-5952-9666-1b26df3f4225 |  | dropdown | Electrical Fail Action | FO, FC, FL
select | fa3b619b-a4c2-54b5-acd1-6bba3834c65a |  | dropdown | Motive Force | FO, FC, FL
checkpoint-group |  |  | section | Proximity Detectors
checkpoint-status |  |  | checkpoint | Open switch set
checkpoint-status |  |  | checkpoint | Open switch mode setting correct
checkpoint-status |  |  | checkpoint | Closed switch set
checkpoint-status |  |  | checkpoint | Closed switch mode setting correct
checkpoint-status |  |  | checkpoint | Electrical connections correct
checkpoint-status |  |  | checkpoint | Electrical certification correct
checkpoint-group |  |  | section | Solenoid Valve
checkpoint-status |  |  | checkpoint | Operation correct
checkpoint-status |  |  | checkpoint | Electrical connections correct
checkpoint-status |  |  | checkpoint | Electrical certification correct
text | b5f0ce7d-6a94-50c0-bd7a-994ab8d38c42 |  | textbox | Voltage: |  |  | V
checkpoint-status |  |  | checkpoint | Pneumatic connections correct
text | 9cd6662b-e864-5d9d-bb50-d53f909ef75d |  | textbox | Pneumatic pressure |  |  | kPa
checkpoint-group |  |  | section | Pilot Valve
checkpoint-status |  |  | checkpoint | Pneumatic connections correct
checkpoint-status |  |  | checkpoint | Operation correct
checkpoint-status |  |  | checkpoint | Action/Lockup
checkpoint-group |  |  | section | Hydraulic Actuator
checkpoint-no-status |  |  | checkpoint | Hydraulic Actuator
text | 57a316ac-9d3d-59e7-9bae-c6d73ef1cbd4 |  | textbox | Working pressure
text | 83dad715-3818-5f52-8569-c9549fbd4802 |  | textbox | Manifold pressure
text | ec79f385-2948-531c-af7e-772f3494847c |  | textbox | Fluid type
checkpoint-status |  |  | checkpoint | Hydraulic connections correct
text | 7f047d12-66c4-528f-a0d0-476696f24bd1 |  | textbox | Regulator pressure setting
checkpoint-status |  |  | checkpoint | Pilot operation correct
checkpoint-group |  |  | section | Accumulator
checkpoint-status |  |  | checkpoint | N2 Charge required
text | c2a62d4c-bf5c-5f65-b282-c59950d7b0db |  | textbox | N2 Pre-charge pressure
text | e606600b-fdff-50c7-917b-2c8540f8015a |  | textbox | Pressure switch setting
text | abcdd7b5-b69f-50de-a4a4-6b9510d0d4e2 |  | textbox | Working pressure
text | 75d8b2ac-ea3a-563a-9ce8-29bb42b6d948 |  | textbox | Output range
checkpoint-status |  |  | checkpoint | Volume tank & check valve installed correctly
checkpoint-group |  |  | section | Electric Actuator
checkpoint-no-status |  |  | checkpoint | Electric Actuator
text | 71a76c58-998c-5c21-a12c-7cea29658e70 |  | textbox | Voltage:
text | 5ea76af7-d200-53b6-83b4-3baa2e7baec4 |  | textbox | Electrical certification correct
text | 3104e389-fc89-5b42-a201-10be19e537c0 |  | textbox | Electrical connections correct
text | 66c0eefa-7145-5962-8c95-201ec99c43bf |  | textbox | Remote operation correct
text | 89e1727c-e89a-591d-846c-ad6cae0d7ab2 |  | textbox | Local hand operation correct
text | 37a08cc8-1859-587c-a10d-6e37b65ae76f |  | textbox | Torque switches and travel stops set
checkpoint-group |  |  | section | Miscellaneous Equipment
checkpoint-no-status |  |  | checkpoint | Miscellaneous Equipment
text | 59a7247d-58fe-5905-84f1-3a643bca1fa4 |  | textbox | Description
text | 876b055b-2246-5272-8eeb-e72b563f4abf |  | textbox | Manufacturer
text | 9ac88f31-0d6b-5a90-a730-062a530a3077 |  | textbox | Model No:
text | e69207d8-c9f9-5634-a803-2078f22a864a |  | textbox | Serial No:
text | 0f880b3c-a955-5665-992c-8e7a48fff8a6 |  | textbox | Range:
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 9e9a6b24-82de-502e-8f56-4f360863e059 |  | textbox | Make:
text | b66b4cee-7a49-5332-adbe-12372be7efe1 |  | textbox | Model:
text | bf0bb173-acdb-5119-8b90-e980144ad778 |  | textbox | Serial No:
text | 3b7f68e6-ecc9-5203-9aad-fe365562c1f1 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | a9d17933-80a3-5e73-8049-1399fe7f699f |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 886e2906-bed9-5e27-bb58-82bbb9fd57e1 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 342cfb89-ef90-55a5-b749-f6152df73907 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-I-15 Pressure Instrument Installation |  |  |  |  | Yes | ITR-I-15 Pressure Instrument Installation | ffbd1b4e-bf81-41f1-9536-68d11958bf6b
checkpoint-group |  |  | section | Pressure Instrument Installation
checkpoint-status |  |  | checkpoint | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint-status |  |  | checkpoint | Pressure Instrument calibrated before installation (ITR-I-07 Instrument Calibration)
checkpoint-status |  |  | checkpoint | Instrument mounted as per hook-up drawings
checkpoint-status |  |  | checkpoint | Air line/Impulse line are correct material to site specifications
checkpoint-status |  |  | checkpoint | Air line/Impulse line are routed tidily and as per hook-up drawings
checkpoint-status |  |  | checkpoint | Correct bolt size and material/grade used
checkpoint-status |  |  | checkpoint | Local indicator is mounted and easy to read, easy access for technicians
checkpoint-status |  |  | checkpoint | Instrument and tubing are adequately supported as per drawings
checkpoint-status |  |  | checkpoint | Isolation valve installed
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 43c1dae5-2777-517d-b0fe-7e63535e856d |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 0dfae3c5-358c-5390-aba8-7a2f3ba3de8a |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 89306f66-5d20-5fc7-b650-efb68808d72c |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed