## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITR-CL-1-128 Temperature Instrument Installation |  |  |  |  | Yes | ITR-CL-1-128 Temperature Instrument Installation | 0d401b24-c752-4526-9676-c9908309e446
checkpoint-group |  |  | section | Temperature Instrument Installation
checkpoint-status |  |  | checkpoint | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint-status |  |  | checkpoint | Temperature instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration)
select | 00e8933f-6d81-505c-86d7-d49e742456dd |  | dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
checkpoint-status |  |  | checkpoint | Thermowell details including flange size are correct in accordance with the specifications
checkpoint-status |  |  | checkpoint | Internal depth of thermowell checked and recorded
text | ee99487e-1c59-56fc-a910-f93c97d1a602 |  | textbox | Depth:
checkpoint-status |  |  | checkpoint | Bar material and tag number stamped on thermowell flange/exposed surface
button | 45b7a9cb-a06c-5423-9ab7-f91af4981214 |  | button | Thermowell CE marked | YES,NO
checkpoint-status |  |  | checkpoint | EOL resistor fitted and correctly rated where applicable
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | bcc60cdf-a48a-53fa-8e40-00938e3d6f30 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 28d8f985-ab1e-5945-8c4e-25466fb0dcef |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 3ec5ac38-577c-5249-9141-33c6e0888136 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-flat |  |  | checklist | Cable Test Record |  |  |  |  | Yes | Cable Test Record | 1cfe973c-5085-4843-98b5-b4cfcd1cfe38
checkpoint-status |  |  | checkpoint | Upload completed ITR scans
checklist-sectioned |  |  | checklist | ITR-CL-1-118 Instrument Pressure/Leak Test |  |  |  |  | Yes | ITR-CL-1-118 Instrument Pressure/Leak Test | 2511439b-880b-4afe-bab8-8331926556d4
checkpoint-group |  |  | section | Checklist items
checkpoint-status |  |  | checkpoint | Tube identification correct
checkpoint-status |  |  | checkpoint | Check mechanical damage
checkpoint-status |  |  | checkpoint | Flow direction and instrument orientation correct
checkpoint-status |  |  | checkpoint | Tubing installed correctly
checkpoint-status |  |  | checkpoint | Tubing size
checkpoint-group |  |  | section | Testing
checkpoint-no-status |  |  | checkpoint | Testing
label | 74d5b7d5-c2b2-5257-a869-91cecdd7c7a1 |  | note | Verify test pressure and medium is correct per project and manufacture specification prior to test
select | 27a18388-74ee-5337-8e94-e82252d59d8e |  | dropdown | Test fluid: | Air, N2, Water, Hydro-oil, Other
text | 70f888fb-dd38-575a-ab51-1f845878e66c |  | textbox | Test pressure:
text | 41766925-f86f-55b8-8af1-699e0453c77c |  | textbox | Max design pressure:
select | a438d8c1-f34c-5933-a7a7-ad83c5ce61b0 |  | dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
text | 4165381b-6fdb-5d65-9f56-b373f2b4779c |  | textbox | Duration: |  |  | Minutes
checkpoint-status |  |  | checkpoint | Confirm all impulse lines have been drained and cleaned
checkpoint-status |  |  | checkpoint | Confirm any temporary test connections, valve etc. are rated for the intended test.
checkpoint-status |  |  | checkpoint | Confirm pneumatic, test gas and aspirator lines have been blown clear.
checkpoint-status |  |  | checkpoint | Check hydraulic lines flushed to project specification.
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 80ba3992-8a3b-56dd-be02-da429c879eab |  | textbox | Make:
text | 51b709df-57b1-5981-a804-57997ccaacc2 |  | textbox | Model:
text | 7a941e10-3965-5b9e-9f8c-f5565a516b57 |  | textbox | Serial No:
text | d6a5aa43-7637-55da-93eb-42ef7424c1d7 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 01b5c383-b942-5c4d-815a-279435f49fa2 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | ceaa235b-c4cf-52e7-b1c1-d7765829c9d6 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | b87845e9-bb30-5418-98ee-457cc6287a62 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | Toolbox Meeting |  |  |  |  | Yes | Toolbox Meeting | 3629266a-0c9d-4a39-9689-da1870b43b0d
checkpoint-group |  |  | section | Toolbox meeting
checkpoint-no-status |  |  | checkpoint | Toolbox meeting
date | ec7e1a6c-c58f-54f1-beee-804da452f1b1 |  | date | Date:
text | 0a9a483c-40f0-58d0-be51-e9e3cb2ab2e2 |  | textbox | Meeting location:
text | 480c03d7-d6fa-5e4f-a2f5-f4c76526f7f7 |  | textbox | Meeting conducted by:
text | 82060030-279b-5b75-9d45-21c3d1a43ff5 |  | textbox | Meeting attendees:
text | 02ed6488-5419-509e-960b-df5376e12f36 |  | textbox | Today's work scope/Hazards
text | 76518f74-fbd3-53a0-907f-77c7ff6ca33d |  | textbox | Hazard controls:
holdpoint |  |  | signoff | PICWS Signoff
checklist-sectioned |  |  | checklist | ITR-CL-1-124 Commissioning Instruments |  |  |  |  | Yes | ITR-CL-1-124 Commissioning Instruments | 390e53bc-feae-45e9-8597-75a89075ba44
checkpoint-group |  |  | section | Required Data
checkpoint-no-status |  |  | checkpoint | Required Data
text | 8d0a7ad4-0a3f-5633-a142-6d1934b721f7 |  | textbox | Instrument range:
checkpoint-status |  |  | checkpoint | Installation complete
checkpoint-status |  |  | checkpoint | Point-to-point
checkpoint-status |  |  | checkpoint | Haz. Inspected
checkpoint-status |  |  | checkpoint | Tag correct
checkpoint-status |  |  | checkpoint | Hook-up correct
checkpoint-group |  |  | section | Alarms & Set points
checkpoint-status |  |  | checkpoint | Alarm Lo
text | 87454f13-62ae-53c0-95f1-7f538721eed8 |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Alarm Lo-Lo
text | 238887fd-8408-5ad0-8ca7-1e0e32ada888 |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Alarm Hi
text | 06a3bd5b-73db-5baa-8615-433d048f8e9d |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Alarm Hi-Hi
text | 45867eec-3b24-5cdd-bd82-186be12f4ab5 |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Set Point 1
text | 5cbaba96-b87d-5bbd-9dff-38cfc2b017d5 |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Set Point 2
text | f5093763-ea6c-5add-ab7b-ee2e5c26a2ea |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Set Point 3
text | 906b61b0-b671-5232-8ed5-594d1bbe66eb |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Set Point 4
text | 4ae1a66f-6a86-533c-a016-dfb85344191f |  | textbox | Activated:
checkpoint-group |  |  | section | Calibration settings
checkpoint-no-status |  |  | checkpoint | Calibration settings
text | d32b5f75-9fc5-5f4d-8314-bc215d33de06 |  | textbox | Zero
text | e76fdf50-a424-5250-9efb-26da97b9eb0a |  | textbox | Range
text | 5a4398a1-2fa1-57b5-89f3-160152d06e95 |  | textbox | Other (Specify)
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 8d98d372-398b-56a1-bb0b-0850002811fb |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 10a38e73-f712-572b-8978-f30a64975931 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | dbb3ed09-5374-5f41-a15e-834270b577f6 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-113 Motor Control |  |  |  |  | Yes | ITR-CL-1-113 Motor Control | 3ab1b19f-567e-41ff-b995-2f3a04c179ff
checkpoint-group |  |  | section | General Motor Control
checkpoint-status |  |  | checkpoint | Check all labelling and warning signs are correctly installed and visible
checkpoint-status |  |  | checkpoint | Check control equipment is clean and free from dust, debris and tools
checkpoint-status |  |  | checkpoint | Check preservation and transit items are removed
checkpoint-status |  |  | checkpoint | Check there are no mechanical damage and no damage to paintwork
checkpoint-status |  |  | checkpoint | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor
checkpoint-status |  |  | checkpoint | Check all cabling to control gear and motor is undamaged, supported and tidy
checkpoint-status |  |  | checkpoint | Check earthing bar and connections are correct and tight
checkpoint-status |  |  | checkpoint | Check incoming and outgoing power cables are terminated and glanded correctly
checkpoint-status |  |  | checkpoint | Check phase identification on power cables is correct and visible
checkpoint-status |  |  | checkpoint | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque
checkpoint-status |  |  | checkpoint | Check all other nuts and bolts are tight
checkpoint-status |  |  | checkpoint | Check spare gland entries are plugged with correct rated plugs
checkpoint-status |  |  | checkpoint | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected
checkpoint-group |  |  | section | Variable Speed Drives (VSD)
checkpoint-status |  |  | checkpoint | Record VSD Nameplate Details
text | d40b7f3e-7774-576b-a857-898184294575 |  | textbox | Volts (Input) |  |  | V
text | 8ab65535-69f1-5b6b-970a-4a0794e4d42a |  | textbox | Amps (Input) |  |  | A
text | 188c91bc-7654-5116-ba1f-6ce5635cd2b0 |  | textbox | Amps (Output) |  |  | A
checkpoint-status |  |  | checkpoint | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input)
checkpoint-status |  |  | checkpoint | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used.
checkpoint-status |  |  | checkpoint | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged
checkpoint-status |  |  | checkpoint | Check control signal cables use twisted pairs
checkpoint-status |  |  | checkpoint | Check control signal and profibus cables shield is earthed at one end
checkpoint-status |  |  | checkpoint | Check analogue and digital signals are run in separate cables
checkpoint-group |  |  | section | Check that voltage segregation is applied along the length of cables:
checkpoint-status |  |  | checkpoint | Distance between input power and motor cable >300mm
checkpoint-status |  |  | checkpoint | Distance between input power and control signal cable >200mm
checkpoint-status |  |  | checkpoint | Distance between motor cable and control signal cable >500mm
checkpoint-status |  |  | checkpoint | Check there is no power factor compensation capacitors installed on the outgoing power cables
checkpoint-status |  |  | checkpoint | Check gland plates with single core power cables are non-magnetic at VSD and LIS
checkpoint-status |  |  | checkpoint | Check mains voltage cannot be applied to the VSD output by means of a bypass connection
checkpoint-status |  |  | checkpoint | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC
checkpoint-status |  |  | checkpoint | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position)
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | a0b017de-6db7-5738-81a2-145086fa4d8d |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | b086c7dc-a33b-5172-9d1c-9af40fa29969 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | dae48cf6-9fd8-55db-ad59-8d036c006718 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-117 Instrument Tubing Installation |  |  |  |  | Yes | ITR-CL-1-117 Instrument Tubing Installation | 41d3797c-3bf6-4074-a1fd-cfb8bf0b87f9
checkpoint-group |  |  | section | Information
checkpoint-no-status |  |  | checkpoint | Information
text | 8cd76939-9b8f-55a2-bf13-b360c33c136b |  | textbox | Equipment:
text | e17bc158-a1fe-5b73-bfb9-96fd41ebd224 |  | textbox | Location:
text | 0f581eb6-779e-50ab-8624-fd33cbb14514 |  | textbox | Tag Numbers:
text | b7fd6483-84a7-55c2-80c1-7dffcfdf733e |  | textbox | Process Fluid:
text | ec608963-59f2-5474-8d2b-81b56b97867c |  | textbox | Reference Drawings:
text | 99da2f93-bd47-5fdb-a6b0-cbbbb24e350a |  | textbox | Max Process Pressure:
text | ce20d033-ae6e-5ccd-82e0-f8ee8ed78624 |  | textbox | Max Supply Pressure:
text | 6e23baf6-09bd-5fe9-b755-a02c25bee71b |  | textbox | Max Signal Pressure:
text | 76c2ba8e-88c9-5dab-a38d-40f02582f346 |  | textbox | Process Temperature:
text | f581911d-63e1-5226-8f27-d92120f4d58d |  | textbox | Other:
button | ffde3aef-3256-5bc0-b800-f0c46fe454e5 |  | button | Inspection | Yes, No
text | 6237c6b1-662c-5865-ac2f-7bea1da30305 |  | textbox | Percentage of installed items to be checked:
checkpoint-group |  |  | section | Checks Pre-Installation
checkpoint-status |  |  | checkpoint | Tubing connection drawings and details available
checkpoint-status |  |  | checkpoint | Client site specific changes noted, agreed and sketched
checkpoint-status |  |  | checkpoint | Tube material type, size, gauge and standard confirmed and available
checkpoint-status |  |  | checkpoint | Tube fitting size and type confirmed and available
checkpoint-status |  |  | checkpoint | Torque wrench - Current calibration certificate
checkpoint-group |  |  | section | Checks During and Post-Installation
checkpoint-status |  |  | checkpoint | Correct thread compatibility and engagement
checkpoint-status |  |  | checkpoint | Correct thread tape and sealant used on fittings
checkpoint-status |  |  | checkpoint | Check fitting ferrule orientation and confirm prior to connection
checkpoint-status |  |  | checkpoint | Tube installation is in compliance with the client specification.
label | b8f33d21-54e5-5729-8102-1e5780be7f6f |  | note | (Supports, bracketry, slope, expansion, vibration, access, cables)
checkpoint-status |  |  | checkpoint | Tube bent correctly, sufficient straight section into fitting
checkpoint-status |  |  | checkpoint | Tube cut clean and straight, de-burred, reamed, and blown through
checkpoint-status |  |  | checkpoint | Depth insertion tool used; witness mark visible at all stages of process
checkpoint-status |  |  | checkpoint | Tube fitting hexes marked to ensure correct swage tightness
checkpoint-status |  |  | checkpoint | Random check with No-Go gap gauge
checkpoint-status |  |  | checkpoint | In service leak test performed and passed
checkpoint-status |  |  | checkpoint | Fitting completion tag completed and applied to each fitting
label | e76a2748-380e-5da8-9f0a-e207bd35690c |  | note | Refer to Swagelok book for tube/thread size pressure ratings
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 12e89ac5-388c-538a-9692-9f8e60393b31 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | b903e175-1c63-53ab-b7c3-660d4e506ee5 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 8593c987-2982-5904-a097-8478510eb9dc |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | As-Built Drawings |  |  |  |  | Yes | As-Built Drawings | 4c2bd76d-70c9-4c6d-a227-3a5ccafc2735
checkpoint-group |  |  | section | As-Built Drawings - attach scanned documents
checkpoint-no-status |  |  | checkpoint | As-Built Drawings - attach scanned documents
text | 61baba17-9a7a-59f3-8640-da513f593f1c |  | textbox | Drawing no.
checklist-flat |  |  | checklist | Record of Inspection (ROI) |  |  |  |  | Yes | Record of Inspection (ROI) | 541f17b2-51ff-486f-b30a-2a39f7af079a
checkpoint-status |  |  | checkpoint | Please upload Record of Inspection here when complete (ROI)
checklist-sectioned |  |  | checklist | ITR-CL-1-109 Electrical Equipment Package |  |  |  |  | Yes | ITR-CL-1-109 Electrical Equipment Package | 54b21698-40fc-4023-aa97-df70e7f16b56
checkpoint-group |  |  | section | Electrical Equipment Package
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | Check equipment is correctly rated for the area.
checkpoint-status |  |  | checkpoint | Check if package is complete with all accessories.
checkpoint-status |  |  | checkpoint | No mechanical damage and paintwork in good condition.
checkpoint-status |  |  | checkpoint | All transportation supports, stops and fastenings removed.
checkpoint-status |  |  | checkpoint | Package fixing down bolts/shims/washers installed and tensioned.
checkpoint-status |  |  | checkpoint | Check package location.
checkpoint-status |  |  | checkpoint | Check package is installed on a level plane.
checkpoint-status |  |  | checkpoint | External cabling (if required) correctly installed.
checkpoint-status |  |  | checkpoint | Internal equipment installed and all tests complete and accepted.
checkpoint-status |  |  | checkpoint | Verify package using vendor and/or project P&IDs.
checkpoint-status |  |  | checkpoint | Check that equipment is correctly earthed.
text | e4627933-2679-54eb-a217-238d72b60a86 |  | textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status |  |  | checkpoint | All spare entries blanked off with correct plugs.
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 6ed3c3c8-c753-5183-badc-1651ccaa6df6 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 2cf9d865-45d9-56f0-b303-b15e244df6f7 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 674b64cf-4ba6-5b45-a428-5e60219c0a34 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-121 Instrument Installation |  |  |  |  | Yes | ITR-CL-1-121 Instrument Installation | 590f78a2-e5e8-4d85-a530-b52b650412db
checkpoint-group |  |  | section | Checklist items
checkpoint-status |  |  | checkpoint | Check instrument nameplate details are correct in accordance with instrument index
text | ef8abe9f-2dbe-5146-9b80-0d25c34c2a18 |  | textbox | Make:
text | 418228aa-f935-570a-a61a-29951d893789 |  | textbox | Model:
text | f0dae677-64dc-5ca8-9169-afbec3fe402c |  | textbox | Serial No:
checkpoint-status |  |  | checkpoint | Ingress protection is suitable for area
text | 7ecf711a-5630-50c6-bd6e-e3289f0ee320 |  | textbox | IP rating:
checkpoint-status |  |  | checkpoint | Instrument rating is correct for hazardous area
text | d2ef17c6-4c05-59c8-a9b1-232d693e5a3a |  | textbox | Haz Rating:
checkpoint-status |  |  | checkpoint | Instrument mounted correctly, elevation correct and free from vibration
checkpoint-status |  |  | checkpoint | Instrument is accessible for maintenance and clear of obstruction
checkpoint-status |  |  | checkpoint | Vent lines are directed into a safe area
checkpoint-status |  |  | checkpoint | Cable glands rated and installed correctly. Spare entries plugged with correctly rated plug
checkpoint-status |  |  | checkpoint | Impulse, hydraulic, pneumatics, lines and air headers correctly installed and supported
checkpoint-status |  |  | checkpoint | Instrument earthed according to client specification
checkpoint-status |  |  | checkpoint | Relevant ITRs for type of instrument completed in conjunction with this (if applicable)
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 8228d0ee-d422-502a-9595-b74905687c6b |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | d0ca1565-fd41-5f67-bef1-860dfd0068ca |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 0e039bde-a7ec-5f17-8502-7a6003b346ee |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-105 Control Panel |  |  |  |  | Yes | ITR-CL-1-105 Control Panel | 59c6da08-f46f-49a3-9fa4-e77437e35d92
checkpoint-group |  |  | section | Control Panel
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | Check holding down/mounting arrangement is correct.
checkpoint-status |  |  | checkpoint | Check for mechanical damage.
checkpoint-status |  |  | checkpoint | Check that panel is correctly earthed.
text | 14939901-1d0e-5969-8601-3367678b85fa |  | textbox | Check earth continuity between panel and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status |  |  | checkpoint | Check tightness of circuit connections.
checkpoint-status |  |  | checkpoint | All internal cabling and wiring is correctly numbered, colour coded and terminated
checkpoint-status |  |  | checkpoint | Ammeter scale and current transformer correct.
checkpoint-status |  |  | checkpoint | Check internals for cleanliness.
checkpoint-status |  |  | checkpoint | Check manual operation of selector switches, MCB, push buttons, etc.
checkpoint-status |  |  | checkpoint | Incoming cables correctly glanded, terminated and labelled.
checkpoint-status |  |  | checkpoint | Unused holes are sealed.
checkpoint-status |  |  | checkpoint | Heaters correctly installed.
text | 7abaaf48-e517-5a75-a3be-3e11c2271216 |  | textbox | Heater circuit Insulation Resistance: |  |  | MegaOhm
checkpoint-status |  |  | checkpoint | Fuse rating correct.
checkpoint-status |  |  | checkpoint | Padlocking facilities correct (if applicable).
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | dc3d0a1c-4bc7-5ab0-a8d5-96119528c73c |  | textbox | Make:
text | e433651f-45a9-5c62-9e2a-57cfd8c91f1b |  | textbox | Model:
text | 5fb44586-0f8c-5aa3-ae73-f10a26103ed8 |  | textbox | Serial No:
text | d1391423-c842-53e4-ab5a-7da81337d923 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | b5198022-6fbe-597e-a990-b195f7d69ab7 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | aef80339-621d-5033-b84e-d113e734044d |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | b9d0d9c1-2797-5670-b949-8c85c7a02b65 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-114 UPS Installation |  |  |  |  | Yes | ITR-CL-1-114 UPS Installation | 60171299-5242-4c88-a170-b756f10d1635
checkpoint-group |  |  | section | UPS Installation
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | Check for mechanical damage.
checkpoint-status |  |  | checkpoint | Panel IP rating is correct:
text | 2b1abc46-ef1e-5af4-8ce9-30bab7642700 |  | textbox | IP Rating:
checkpoint-status |  |  | checkpoint | Holding down arrangement and seat alignment correct.
checkpoint-status |  |  | checkpoint | Panels aligned correctly.
checkpoint-status |  |  | checkpoint | Earth alignment to vendor specification & connecting link bolts torqued to the manufacturers recommendations & marked.
checkpoint-status |  |  | checkpoint | External bonding correct
checkpoint-status |  |  | checkpoint | Bus bar alignment to vendor specifications & connecting link bolts torqued to the manufacturers recommendations & marked.
text | 5b9da5f7-e3de-5b4f-ae52-82e94975035b |  | textbox | Nm.
checkpoint-status |  |  | checkpoint | Phase identification correct.
checkpoint-status |  |  | checkpoint | Instrument, indication lamps & interlocks correct.
checkpoint-status |  |  | checkpoint | Main switches, contactors, fuses etc. sized & identified correctly as per Single-
checkpoint-status |  |  | checkpoint | Line Drawings.
checkpoint-status |  |  | checkpoint | Check main isolator switch operation.
checkpoint-status |  |  | checkpoint | Check bypass isolator switch operation.
checkpoint-status |  |  | checkpoint | Check DC UPS battery isolator switch operation.
checkpoint-status |  |  | checkpoint | COM Interface & Mod Link.
checkpoint-status |  |  | checkpoint | Padlocking facilities correct.
checkpoint-status |  |  | checkpoint | Check internals for cleanliness.
checkpoint-status |  |  | checkpoint | Check manual operation of selector switch, MCB, push button, etc.
checkpoint-status |  |  | checkpoint | Incoming cable correctly installed, terminated & supported.
checkpoint-status |  |  | checkpoint | Unused cable entries sealed.
checkpoint-status |  |  | checkpoint | All internal cabling & wiring neat, correct & tight.
checkpoint-status |  |  | checkpoint | Heaters correctly installed.
checkpoint-status |  |  | checkpoint | Fans correctly installed.
checkpoint-status |  |  | checkpoint | Verify continuity of earth bar to frame
text | 8f8e5794-ec2d-512c-bdb0-777afdb705a5 |  | textbox | Earth continuity: |  |  | Ohms
checkpoint-status |  |  | checkpoint | Check Busbar Insulation resistance between Phases & Phases & Earth (690V-2500VDC, 400V -1000VDC)
text | 5c6499f8-1976-5914-acfb-ab5f9639a901 |  | textbox | L3-L2 |  |  | MegaOhms
text | b30834e9-fd83-56b8-a317-1834aefb8fca |  | textbox | L3-L1 |  |  | MegaOhms
text | 4b26812c-da21-54c9-85b0-f81c968d1f91 |  | textbox | L3-N |  |  | MegaOhms
text | 98cf800f-7469-5031-bac4-33ac607c0359 |  | textbox | L2-L1 |  |  | MegaOhms
text | 99daa204-971a-5e74-9310-2bc652382364 |  | textbox | L2-N |  |  | MegaOhms
text | 646952d4-c7a2-55fd-8674-d8ae5bbf85e0 |  | textbox | L2-E |  |  | MegaOhms
text | ee6e934c-d068-5a80-9358-59aac60b7729 |  | textbox | L1-N |  |  | MegaOhms
text | 5e5ee2e2-6123-5392-8669-190001f0db66 |  | textbox | L1-E |  |  | MegaOhms
text | 2efbbb56-46aa-5295-b720-b516458a7ba2 |  | textbox | N-E |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Drawings marked up with relevant changes
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | eb8becdf-f4b4-5cd4-81de-19ec72ed519b |  | textbox | Make:
text | 6cdba49d-6b62-5216-a1e6-70e790b80d6a |  | textbox | Model:
text | 9c770f61-3a60-5f6a-8ce9-d19ca5dadc5e |  | textbox | Serial No:
text | 8e0129d5-b8bf-5821-a161-7c0d1ae1abf8 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 6e90ae9b-2ba4-5310-949c-81c953a37517 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | aed1275f-ea0e-5166-891a-e091d1d47dcc |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 29ebf5d5-d15e-54a8-b203-b4eb056feebb |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-127 Telecommunications Equipment Panel |  |  |  |  | Yes | ITR-CL-1-127 Telecommunications Equipment Panel | 69660914-93cc-44a7-9173-4abda198292c
checkpoint-group |  |  | section | Telecommunications Equipment Panel
checkpoint-status |  |  | checkpoint | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings:
checkpoint-status |  |  | checkpoint | Check tag number is in accordance with Telecommunications Equipment List.
checkpoint-status |  |  | checkpoint | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order.
checkpoint-status |  |  | checkpoint | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation.
checkpoint-status |  |  | checkpoint | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified.
checkpoint-status |  |  | checkpoint | Check panel air vents are clean and free of dust and dirt.
checkpoint-status |  |  | checkpoint | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar.
checkpoint-status |  |  | checkpoint | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar.
checkpoint-status |  |  | checkpoint | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s).
checkpoint-status |  |  | checkpoint | Check sealing of all cable penetration (where applicable).
checkpoint-status |  |  | checkpoint | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel.
checkpoint-status |  |  | checkpoint | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable).
checkpoint-status |  |  | checkpoint | Confirm panel is readily accessible for inspection and maintenance.
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 7c8e4d45-1aa5-5107-a28c-d73ee5faf8b2 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 82f1aea5-75e0-516c-b775-052c6c7b9051 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 82a17978-ddc9-55b3-8872-4f64eff33ba4 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-100 General Electrical Equipment |  |  |  |  | Yes | ITR-CL-1-100 General Electrical Equipment | 6b1029da-0779-4299-b43c-25e9ee3014c2
checkpoint-group |  |  | section | General Electrical Equipment
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | No mechanical damage and paintwork in good condition.
checkpoint-status |  |  | checkpoint | Installation is clean and tidy
checkpoint-status |  |  | checkpoint | Mounting arrangement correct
checkpoint-status |  |  | checkpoint | All internal cabling and wiring correctly installed and labelled.
checkpoint-status |  |  | checkpoint | External cabling is correctly installed and labelled.
checkpoint-status |  |  | checkpoint | Check that Equipment is correctly earthed.
checkpoint-status |  |  | checkpoint | Check gland, plate, frame & door earth continuity
checkpoint-status |  |  | checkpoint | All spare entries blanked off with correct plugs.
checkpoint-status |  |  | checkpoint | Check item is suitably rated for area (E.g. IP rating, Ex rating)
checkpoint-status |  |  | checkpoint | Conforms to Specifications and Drawings.
checkpoint-status |  |  | checkpoint | As-builts complete.
checkpoint-group |  |  | section | Electrical Checks
checkpoint-status |  |  | checkpoint | IR and Earth tests
text | c8cbd303-9866-5959-a14c-de5c590950d5 |  | textbox | Insulation Resistance (P/N to E) |  |  | MegaOhms
text | 5e4a2dd1-123f-57d4-99c6-e187412f5ae4 |  | textbox | Earth Continuity: |  |  | Ohms
text | 42607220-5a48-5397-9515-61bd99717aa3 |  | textbox | Earth Bonding: |  |  | Ohms
text | da6f7299-b487-56a0-87e4-59f12e7ac1cc |  | textbox | Other checks:
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 63b2269f-b04c-5e3f-8ece-f1e10eb6566c |  | textbox | Make:
text | caedc6e9-84ad-5cff-b347-5b93344d3ca7 |  | textbox | Model:
text | 3408372c-666a-5886-9cda-89decf13b320 |  | textbox | Serial No:
text | 20157eb3-4c2d-57b5-ad60-1031071a17ed |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 39e38e39-e29b-53c7-ba43-dcb368ea9dfb |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | e5c704fa-7a5d-5dad-ae0f-6000ea9a9bfb |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 84dab5a2-533d-5022-8165-6a8bdd0998df |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-102 Distribution Board Installation |  |  |  |  | Yes | ITR-CL-1-102 Distribution Board Installation | 6b6f8d38-8312-4ffa-b277-86529a36854f
checkpoint-group |  |  | section | Distribution Board Installation
checkpoint-status |  |  | checkpoint | Inspect for mechanical damage from freight and handling
checkpoint-status |  |  | checkpoint | Check mounting arrangement is adequate.
checkpoint-status |  |  | checkpoint | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct.
checkpoint-status |  |  | checkpoint | Check IP rating is correct for location.
text | 6a8d7ba3-eb35-57d5-bce4-7464f8a73045 |  | textbox | IP Rating:
checkpoint-status |  |  | checkpoint | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order.
checkpoint-status |  |  | checkpoint | Confirm main isolator operates with associated switches and auxiliaries
checkpoint-status |  |  | checkpoint | Confirm main isolator operates all active conductors
checkpoint-status |  |  | checkpoint | Confirm main isolator and sub-circuit MCB’s can be padlocked open if required.
checkpoint-status |  |  | checkpoint | Check number and rating of sub-circuits as per design and specifications.
checkpoint-status |  |  | checkpoint | Ensure different Voltage segregation is correct.
checkpoint-status |  |  | checkpoint | Heaters installed and functioning.
text | e5817a0c-e970-525c-a4f0-37b8f8e0c70c |  | textbox | Record IR of heater circuit |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar.
checkpoint-status |  |  | checkpoint | Check internal cables properly terminated and labelled
checkpoint-status |  |  | checkpoint | DB properly labelled, sub circuit MCB correct rating and application
checkpoint-status |  |  | checkpoint | Check cable penetration is correct. (E.g. sealed correctly, correct size/type of glands)
checkpoint-status |  |  | checkpoint | Active, Neutral and Earth bar properly identified and labelled
checkpoint-status |  |  | checkpoint | DB legend card correct and updated, As-built
checkpoint-status |  |  | checkpoint | Confirm panel is readily accessible for inspection and maintenance.
checkpoint-status |  |  | checkpoint | Confirm panel is clean and tidy
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | f7559f9b-1f97-5b6e-8de6-cc808fecef74 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 8db8cb91-88ba-50f2-a26d-68e2e01a4724 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 242e09cc-29cc-5508-a61a-a7ad3ce8b7c9 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-122 Instrument Calibration |  |  |  |  | Yes | ITR-CL-1-122 Instrument Calibration | 70e3e410-deab-4830-ae1b-bb4a2223461a
checkpoint-group |  |  | section | Required Data
checkpoint-no-status |  |  | checkpoint | Required Data
text | 8841a35d-a2fc-5aee-be9b-8c1b41b182d6 |  | textbox | Type and Size:
text | 62c56dd7-62a8-5bf2-9d82-8641799cd788 |  | textbox | Make:
text | 0169e260-2c35-53ea-9227-dc65966b46e2 |  | textbox | Serial No:
text | 80d6abd3-2c1f-587c-92d7-5917a5cc805e |  | textbox | Instrument Type:
text | 8e41afdb-a2a9-5306-8627-790d563be0c5 |  | textbox | Instrument designation/equipment no
text | ef11030e-f939-5773-96ed-0ec9b48c27cb |  | textbox | Calibration interval
text | 0f45e2b5-9478-5768-80c7-e41bdb806503 |  | textbox | Calibration method
text | aea150b1-851f-56ae-985c-c210670b063d |  | textbox | Calibrated at
checkpoint-group |  |  | section | Instrument Power Supply
checkpoint-no-status |  |  | checkpoint | Instrument Power Supply
select | 58182335-d473-5388-b0aa-7aa7e53dc9a9 |  | dropdown | Supply type | VAC, 2 Wire DC, Other, None
text | dba22179-3412-5625-b1ae-2f4474b62e86 |  | textbox | Supply value:
checkpoint-status |  |  | checkpoint | Calibration sheet completed and attached below
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | d3a1ccd2-8610-53cd-8f52-12e056b089ca |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 1f513879-9294-5309-89d6-871ce787474d |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 9705c5a1-3fd3-5445-b47b-a5292b10b5bc |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-126 Cone and Thread Pressure Testing |  |  |  |  | Yes | ITR-CL-1-126 Cone and Thread Pressure Testing | 763d93eb-dea5-4ca7-8fdb-10d43cc42a7a
checkpoint-group |  |  | section | General Data
checkpoint-no-status |  |  | checkpoint | General Data
text | 0c122bd0-817b-56a0-b6b6-273e2f05d57f |  | textbox | Location:
text | 022e2c00-5518-58c9-9948-0f31eadebb3d |  | textbox | Duty:
text | f4a7ef80-9447-523d-9d98-c079a7bcec34 |  | textbox | Reference Drawings:
text | f4954c42-8ff8-5955-aa52-462a41955495 |  | textbox | Hook-up drawing:
text | fad14a14-096f-5fe9-9a45-149f7d4229eb |  | textbox | Related instrument tag no:
text | 63f16818-9eea-5b37-811c-1a45314c23e1 |  | textbox | Tube diameter and wall thickness:
text | 669f8c2b-6d20-5111-94ea-78e0a358dc05 |  | textbox | Instrument location drawing:
checkpoint-group |  |  | section | Checklist items
checkpoint-status |  |  | checkpoint | Tubing orientation as per hook up drawing.
checkpoint-status |  |  | checkpoint | Checked with a Torque Wrench and marked and tagged
checkpoint-status |  |  | checkpoint | Ensure Area is barricaded off to restrict unauthorized entry to personnel
checkpoint-status |  |  | checkpoint | Tube as per specification and hook up drawings.
text | d2148108-d7f9-57ea-aa93-2149527e6cfb |  | textbox | Max design pressure:
text | 0c2c1d38-d1b1-58e5-9cbc-14efc99fc77b |  | textbox | Test medium used:
text | 7fc82341-5dcd-552f-8170-08b32dc689bb |  | textbox | Record Testing pressure:
text | 72f90f97-77ab-569c-a63a-c5e26cd70293 |  | textbox | Test pressure duration: | Minutes
text | 4a09176c-a9e2-57fb-8ebb-8cbfa15bea37 |  | textbox | Test leak rate: | Litres/minute
checkpoint-status |  |  | checkpoint | Chart recorder used and attached (where applicable).
checkpoint-status |  |  | checkpoint | Confirm all Tubing lines have been pigged / cleaned.
checkpoint-status |  |  | checkpoint | Check all plugs are replaced (if removed), vents are closed, and isolation valves are in correct positions.
checkpoint-status |  |  | checkpoint | Ensure equipment is left clean and in a safe state for handover to operations to the standard of ITP-I-08 Cone and Thread cleaning procedure
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 0db71783-d6bc-5a4c-9f5d-6bd2ea0f97b9 |  | textbox | Make:
text | a6d86fc3-9f42-5b2d-885a-323201b6aa36 |  | textbox | Model:
text | 2b03bc7e-d4c3-5dd6-81f7-3ce45dcd7322 |  | textbox | Serial No:
text | 3393cc66-e5a0-5bac-911c-3283f13cac43 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 5bececa9-110c-5011-9a9c-7500e1461cbb |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 792e63ab-9d9d-5334-ab4d-57e8edc343d9 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 24b7e114-8a6b-578c-aa87-bef0c58c8d70 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-111 Electrical Earthing |  |  |  |  | Yes | ITR-CL-1-111 Electrical Earthing | 7723a393-f5f8-4781-b651-2065c9685414
checkpoint-group |  |  | section | Earthing System
checkpoint-no-status |  |  | checkpoint | Earthing System
text | 5bd1f02f-7a7d-5b4b-8ac5-405b14cbdcfc |  | textbox | Electrode type
text | 1545794b-021d-5c6d-a826-01a939c7bdb7 |  | textbox | Electrode length/size
text | c10858a8-27af-5bfc-8bce-af48d9231dfa |  | textbox | Location of Electrodes
text | e0687a12-ee05-5968-825f-ecb24c0ce91d |  | textbox | Method of installing electrode
text | 6198850e-72e9-58d1-a5fb-bd594b21849a |  | textbox | Method of attaching to electrode (e.g Clamp, Cad Weld, Lug & Bolt)
text | 40ac4553-b6e9-56b5-8f24-dcab42c7e66a |  | textbox | Number of electrodes
checkpoint-group |  |  | section | General Items
checkpoint-status |  |  | checkpoint | Confirm earth grid layout
checkpoint-status |  |  | checkpoint | Ensure grid layout is in accordance with design drawings
checkpoint-status |  |  | checkpoint | Record number of grid interconnections
checkpoint-status |  |  | checkpoint | Ensure all metalwork is earthed as required
checkpoint-status |  |  | checkpoint | Check welding of earth bosses and associated surface finish
checkpoint-status |  |  | checkpoint | Ensure that earth cables/conductors have adequate mechanical protection i.e. conduits, kick-plates, PVC duct through concrete etc. at points of high exposure.
checkpoint-status |  |  | checkpoint | Ensure that brazing or welding of all joints has been completed correctly.
checkpoint-status |  |  | checkpoint | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, Cad (thermal) welds and earth bosses
checkpoint-status |  |  | checkpoint | Ensure that earth electrodes are located within a protected, covered and identified surround.
checkpoint-status |  |  | checkpoint | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating.
checkpoint-status |  |  | checkpoint | MEN Link Installed (If applicable)
checkpoint-group |  |  | section | Earthing Conductors
checkpoint-status |  |  | checkpoint | Ensure that earthing conductor size is correct in accordance with approved installation drawings.
checkpoint-status |  |  | checkpoint | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly.
checkpoint-status |  |  | checkpoint | Check terminations to ensure that all connections are correct, clean, greased and tight.
checkpoint-status |  |  | checkpoint | Check that all bi-metal connections have been performed correctly to manufacturer's requirements.
checkpoint-status |  |  | checkpoint | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar.
checkpoint-status |  |  | checkpoint | Ensure that earth cable identification markings are in place.
checkpoint-status |  |  | checkpoint | Ensure that earth connections are not multi-coiled or 'pig-tailed' but are terminated as straight as possible.
checkpoint-group |  |  | section | Earth Bar Installation
checkpoint-status |  |  | checkpoint | Check for correct assembly of equipment
checkpoint-status |  |  | checkpoint | Check fixings and mounting points conform to project specification and are secure
checkpoint-status |  |  | checkpoint | Check for equipment levels and alignment
checkpoint-group |  |  | section | Earth System Testing
checkpoint-status |  |  | checkpoint | Using an Earth Resistance tester, measure earth resistance between electrodes or main earth bars & the earth body.
text | 0f299223-f63d-51dd-820d-b0ab0bfed052 |  | textbox | Record results:
checkpoint-status |  |  | checkpoint | Measure earth continuity from each earth point and/or equipment earth frame to the nearest electrode or main earth bar
label | 266f04ad-a28a-52c8-ad67-e10155da5d28 |  | note | Note: Sketch a layout of earth electrodes showing electrode numbers and distances and attach below
checkpoint-status |  |  | checkpoint | Earth Grid Test Results (electrodes connected)
text | 36527e4d-146b-53f1-9b3b-aeaf3a530be0 |  | textbox | HV Earth grid:
text | 89cf3a81-4fd9-5bb0-87a2-5def15c98ebe |  | textbox | LV Earth grid:
text | 9e3bb7b6-deec-54ac-9d52-39bd29fe6916 |  | textbox | Combined HV/LV Earth grids:
text | 25ec0ec8-8b64-57de-b998-bf8b9a202e3c |  | textbox | Instrument Earth:
checkpoint-status |  |  | checkpoint | Earth Resistivity Tests
text | dab82569-1ca3-59f8-ab4c-ff58dd7581be |  | textbox | From (Main Earth Bar or Auxiliary Earth Point): |  |  | To Earth Body
text | 3b4b084c-ae3b-522e-83ce-569dca7f3a73 |  | textbox | Result: |  |  | Ohms
text | 0cd17715-711d-55b8-b2ff-cc0cdc041d63 |  | textbox | From (Main Earth Bar or Auxiliary Earth Point): |  |  | To Earth Body
text | d0bbd9a8-9d5a-5d1c-a0bf-043518adaf12 |  | textbox | Result: |  |  | Ohms
checkpoint-status |  |  | checkpoint | Earth Continuity Tests
text | 0f7adf46-f0ae-5585-8a6a-cd4a05164921 |  | textbox | From: (Main Earth Bar Location)
text | e12a147b-ca4e-52fd-b27e-4845a755d317 |  | textbox | To: (Earth Electrode number/description)
text | 6fe0d16c-48d0-5ec9-86cd-6076857d16df |  | textbox | Record Resistance: |  |  | Ohms
text | c61c866b-01ad-5d79-af81-17051f7f04d4 |  | textbox | From: (Main Earth Bar Location)
text | 20a8248c-4e89-51f4-94de-468109a49db1 |  | textbox | To: (Earth Electrode number/description)
text | 58e0079f-1368-553c-94f6-57271d2de12e |  | textbox | Record Resistance: |  |  | Ohms
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | b7393455-429f-5767-94d0-63a435d8c006 |  | textbox | Make:
text | ae402341-1308-585c-8450-4242db7c3ed8 |  | textbox | Model:
text | bec946d5-e98d-585b-9037-2aeea720050b |  | textbox | Serial No:
text | 82051c98-4322-5f51-bb5a-5fa869a0a7eb |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | f04ebb98-1606-548f-976a-1372c9e3d322 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 554ae2b0-2566-59b9-8572-83e1a6bdc01a |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 395b50bc-3cd5-546a-9a38-bd4689259c1a |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-106 Junction Box |  |  |  |  | Yes | ITR-CL-1-106 Junction Box | 7c1f0edc-a093-44ac-9527-b759115ad25a
checkpoint-group |  |  | section | Junction Box
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | Check holding down/mounting arrangement and accessibility for maintenance.
checkpoint-status |  |  | checkpoint | Check for mechanical damage
checkpoint-status |  |  | checkpoint | Check that Junction box is correctly earthed.
text | 67214de3-d670-553d-be33-1107bd07bcac |  | textbox | Test and confirm the earth resistance between junction box and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status |  |  | checkpoint | Check all internal cabling and wiring is correct and tight, including segregation (e.g. IS to NON IS circuits).
checkpoint-status |  |  | checkpoint | Check cables for Voltage segregation. Ensure clearance, labelling, colour coding is to standard
checkpoint-status |  |  | checkpoint | Incoming/Outgoing cables are glanded and terminated correctly
checkpoint-status |  |  | checkpoint | Spare entries plugged correctly.
checkpoint-status |  |  | checkpoint | Check internals for cleanliness
checkpoint-status |  |  | checkpoint | All cover bolts and gasket undamaged
checkpoint-status |  |  | checkpoint | Verify ingress protection is suitable for area (IP rating)
text | 1270bced-762c-5303-b7b0-eecb28ad031b |  | textbox | IP Rating:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 7d7abd7f-8400-5f4b-b2ca-237f9febab64 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 38d3baca-65c5-52de-92f6-f70f81edf975 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 13761674-a18f-5502-8732-fe08e13f45d7 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-125 Cone and Thread Tubing Installation |  |  |  |  | Yes | ITR-CL-1-125 Cone and Thread Tubing Installation | 7df205a6-434e-41e8-8310-30c0b39c3dfd
checkpoint-group |  |  | section | General Data
checkpoint-no-status |  |  | checkpoint | General Data
text | 423a4181-a2a9-5af8-bc88-8e3ccf4c9181 |  | textbox | Location:
text | a97a49b7-8fa4-5b75-809b-48584022141c |  | textbox | Duty:
text | 87354745-edc3-51b5-8247-16268defcf26 |  | textbox | Reference Drawings:
text | cc2595bb-40f5-5893-9cc7-8315d4354432 |  | textbox | Hook-up drawing:
text | aeff6b90-c463-5c34-8b20-3a993f0e7502 |  | textbox | Related instrument tag no:
text | 6c60a637-8f65-5ab7-bd70-2c5ea95a036d |  | textbox | Tube diameter and wall thickness:
text | 013f0958-108d-5735-ba77-9d2074dded7f |  | textbox | Instrument location drawing:
checkpoint-group |  |  | section | Cone and Thread installation - Stainless fittings
checkpoint-status |  |  | checkpoint | Correct thread compatibility and engagement
checkpoint-status |  |  | checkpoint | Correct thread lubricant used on fittings
checkpoint-status |  |  | checkpoint | Check fitting collar prior to connection - 1 to 2 threads visible at cone
checkpoint-status |  |  | checkpoint | Tube installation follows the client specification.
label | 5c8ceecb-850e-50ad-b751-3bace6c730e9 |  | note | (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables)
checkpoint-status |  |  | checkpoint | Tube bent correctly, sufficient straight section into fitting
checkpoint-status |  |  | checkpoint | Tube cut clean and straight, de-burred, reamed, and blown through
checkpoint-status |  |  | checkpoint | Lubricate collar, cone and gland thread at assembly to prevent galling
checkpoint-status |  |  | checkpoint | Correct Tube nut used for the right sized tube
checkpoint-status |  |  | checkpoint | Ensure No thread tape or sealant are used on tube nuts
checkpoint-status |  |  | checkpoint | Tube fitting hex torqued to ensure correct tightness, marked with pen
checkpoint-status |  |  | checkpoint | Ensure Weep hole is unobstructed and clean
checkpoint-status |  |  | checkpoint | In service leak test performed and passed
checkpoint-status |  |  | checkpoint | Fitting completion tag completed and applied to each fitting
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | ef4b16cc-89ef-5bc9-8c63-15aee2422870 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 22eb61b4-95f3-514d-8d04-468bb5033154 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | cf58615c-a4b9-58ab-b6b2-a96af281ea79 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation) |  |  |  |  | Yes | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation) | 81681e32-7c0b-4c7a-be64-d905f1ea903a
checkpoint-group |  |  | section | Equipment
checkpoint-status |  |  | checkpoint | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No.
checkpoint-status |  |  | checkpoint | Equipment checked for additional items as applicable
checkpoint-group |  |  | section | Valve
checkpoint-no-status |  |  | checkpoint | Valve
text | d68ea1e8-af4d-553a-a138-b0f8c0712a53 |  | textbox | Size:
text | 909b8818-e48d-5bf0-a030-75bd2e93035d |  | textbox | Flange type:
checkpoint-status |  |  | checkpoint | Material certification correct
checkpoint-status |  |  | checkpoint | Trim material correct
text | c3cd62fa-477e-554b-a923-d708532b6306 |  | textbox | Rating:
text | df0544e3-2a86-55e9-a149-5fe7841719c3 |  | textbox | Service:
checkpoint-status |  |  | checkpoint | Body material correct
text | ae1e58ee-f71b-5299-829c-cbace44ea7d0 |  | textbox | Leakage class:
checkpoint-group |  |  | section | Actuator
checkpoint-no-status |  |  | checkpoint | Actuator
text | 22cdca66-95cf-56ca-8379-e550c1264188 |  | textbox | Input range: |  |  | kPa
checkpoint-status |  |  | checkpoint | Failure action
checkpoint-status |  |  | checkpoint | Hand wheel operation correct
checkpoint-group |  |  | section | Positioner
checkpoint-no-status |  |  | checkpoint | Positioner
text | 320656c7-d1b8-5c70-9f63-43aa22a5cff3 |  | textbox | Signal range
text | c8bff268-ef7e-505d-b44d-070305a9d727 |  | textbox | Output range
checkpoint-group |  |  | section | I/P Converter
checkpoint-no-status |  |  | checkpoint | I/P Converter
text | 36f7008a-d788-5250-b9e6-31b5938b9e2b |  | textbox | Signal range
text | 5582a706-9dbb-519f-ac52-5c752f8ef77d |  | textbox | Output range
checkpoint-group |  |  | section | Filter/Regulator/On-Off Valve
checkpoint-no-status |  |  | checkpoint | Filter/Regulator/On-Off Valve
text | 1a567e7a-8291-5569-9623-ca5904a20951 |  | textbox | Range |  |  | kPa
text | 09e356a8-a2ee-5d03-8406-1b981b831b08 |  | textbox | Pressure setting |  |  | kPa
checkpoint-status |  |  | checkpoint | Stroke Time
text | 27097e10-6d12-5e1a-a0a2-9d04226c6b73 |  | textbox | Open |  |  | sec
text | 20aaa7e1-aeab-5d57-b6d7-46ff3b62f993 |  | textbox | Close |  |  | sec
checkpoint-status |  |  | checkpoint | Open/Close times conform to commissioning specifications
checkpoint-group |  |  | section | Fail Action
checkpoint-no-status |  |  | checkpoint | Fail Action
select | c1801311-b13d-510b-8cdf-2f8022097b00 |  | dropdown | Electrical Fail Action | FO, FC, FL
select | 4662cab7-d477-5cb7-871c-6e2004c528ec |  | dropdown | Motive Force | FO, FC, FL
checkpoint-group |  |  | section | Valve Field Calibration and Hysteresis Check
checkpoint-status |  |  | checkpoint | Confirm test equipment is within calibration period prior to testing
label | f6320ee7-75ba-508e-93ac-4c9f88a5fa23 |  | note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
label | c8a115f2-e93f-5bd2-a58d-df5386bb673c |  | note | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100%
checkpoint-group |  |  | section | Proximity Detectors
checkpoint-status |  |  | checkpoint | Open switch set
checkpoint-status |  |  | checkpoint | Open switch mode setting correct
checkpoint-status |  |  | checkpoint | Closed switch set
checkpoint-status |  |  | checkpoint | Closed switch mode setting correct
checkpoint-status |  |  | checkpoint | Electrical connections correct
checkpoint-status |  |  | checkpoint | Electrical certification correct
checkpoint-group |  |  | section | Solenoid Valve
checkpoint-status |  |  | checkpoint | Operation correct
checkpoint-status |  |  | checkpoint | Electrical connections correct
checkpoint-status |  |  | checkpoint | Electrical certification correct
text | 2ef1b34a-952e-5f2d-87c9-b442da71d659 |  | textbox | Voltage: |  |  | V
checkpoint-status |  |  | checkpoint | Pneumatic connections correct
text | 622e1473-bbfc-5bd3-a71a-4edb733e07d3 |  | textbox | Pneumatic pressure |  |  | kPa
checkpoint-group |  |  | section | Pilot Valve
checkpoint-status |  |  | checkpoint | Pneumatic connections correct
checkpoint-status |  |  | checkpoint | Operation correct
checkpoint-status |  |  | checkpoint | Action/Lockup
checkpoint-group |  |  | section | Hydraulic Actuator
checkpoint-no-status |  |  | checkpoint | Hydraulic Actuator
text | 4d41e321-c233-5c4f-8507-c001d1bf843a |  | textbox | Working pressure
text | 75e1ece3-9c74-504e-bb04-795c12154718 |  | textbox | Manifold pressure
text | 4830d90b-02cd-551f-90cd-fdb4c67b40a3 |  | textbox | Fluid type
checkpoint-status |  |  | checkpoint | Hydraulic connections correct
text | c1918cf0-6deb-5b4b-982f-11ae8e02c4ec |  | textbox | Regulator pressure setting
checkpoint-status |  |  | checkpoint | Pilot operation correct
checkpoint-group |  |  | section | Accumulator
checkpoint-status |  |  | checkpoint | N2 Charge required
text | af1d45da-4c32-5d27-9e96-3ea8bcab652d |  | textbox | N2 Pre-charge pressure
text | 34366f56-ebcd-5bf0-a445-9cedd32f91b1 |  | textbox | Pressure switch setting
text | cd35e3ca-14ab-50d4-9683-c7b6b7cf6dfd |  | textbox | Working pressure
text | 75d76b3e-f0b9-5d6b-b833-564c0555050d |  | textbox | Output range
checkpoint-status |  |  | checkpoint | Volume tank & check valve installed correctly
checkpoint-group |  |  | section | Electric Actuator
checkpoint-no-status |  |  | checkpoint | Electric Actuator
text | 9f134de9-68bc-557b-aff0-e35e3713ea1c |  | textbox | Voltage:
text | c6171ac4-d8e1-56a1-9c64-5e068e5b3078 |  | textbox | Electrical certification correct
text | 79353afa-60a3-5716-8fa4-a2e2890219ad |  | textbox | Electrical connections correct
text | fa08adf5-1fb6-59e8-970e-9df0f1554c19 |  | textbox | Remote operation correct
text | 70d6e8ac-f108-56c8-92a8-0c044180a3b4 |  | textbox | Local hand operation correct
text | 084ff936-71e6-51b0-9ecf-a94ac4b10179 |  | textbox | Torque switches and travel stops set
checkpoint-group |  |  | section | Miscellaneous Equipment
checkpoint-no-status |  |  | checkpoint | Miscellaneous Equipment
text | e88f8b21-4c8e-54f9-a5b8-d1debc105230 |  | textbox | Description
text | 24439868-e16a-592d-a544-d90fe3dbc58f |  | textbox | Manufacturer
text | 7f8da1ea-1416-5028-92b2-3697ea76b519 |  | textbox | Model No:
text | 06d199a1-b77e-51bc-a820-33922ce62084 |  | textbox | Serial No:
text | d8572a47-0ea1-5892-b464-61af804186ac |  | textbox | Range:
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 991e8aeb-2b42-53fd-83b9-000389a5d1f0 |  | textbox | Make:
text | f1e8d01d-4425-5a55-81a6-0c7da82ac5c1 |  | textbox | Model:
text | 24500f2b-1d63-5dc3-9bfa-8b186f39124d |  | textbox | Serial No:
text | 0d4885ba-090f-5108-8a37-4a14201e9084 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | edb29987-c638-545b-ba3c-586bb7f5d0a4 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 03751cac-959f-5fb3-bf0e-6e0f71ff4abf |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 0ed595b0-519c-52a7-a1d0-4b6b0eaee027 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-131 Level Instrument Installation |  |  |  |  | Yes | ITR-CL-1-131 Level Instrument Installation | 83abc647-b290-4185-82af-825754c47107
checkpoint-group |  |  | section | Level Instrument Installation
checkpoint-status |  |  | checkpoint | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint-status |  |  | checkpoint | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration)
checkpoint-status |  |  | checkpoint | Level instrument mounting equipment is adequately sturdy and correct materials used
checkpoint-status |  |  | checkpoint | Bolts and studs are to site specification
checkpoint-status |  |  | checkpoint | Ensure location and tapping point is verified per relevant drawings
checkpoint-status |  |  | checkpoint | Ensure gasket and studs are used as per specifications
checkpoint-status |  |  | checkpoint | Verify contact type sensor probes are installed without any resistance
checkpoint-status |  |  | checkpoint | Verify antenna/source are installed correctly
checkpoint-status |  |  | checkpoint | Ensure display is easily readable by operations and access is easy for technicians
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 50a74c02-f62b-589a-bb5b-1a47c266c0b0 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | eb4bd8e1-2340-5f94-9b9d-be7ecbf719b9 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 8bd5c30a-0c6e-55c1-af9f-09ad23eb5287 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-107 Heat Tracing Circuit |  |  |  |  | Yes | ITR-CL-1-107 Heat Tracing Circuit | 8a06c44f-5fc9-4dfe-87b0-06d1e9d9ba16
checkpoint-group |  |  | section | Heat Tracing Circuit
checkpoint-status |  |  | checkpoint | Circuit installed, connected & identified according to design drawings.
checkpoint-status |  |  | checkpoint | End caps and connection kits correctly installed.
checkpoint-status |  |  | checkpoint | All junction boxes properly supported, and all cables protected against sharp edges.
checkpoint-status |  |  | checkpoint | Cable termination and glanding at all junction boxes correct.
checkpoint-status |  |  | checkpoint | All spare entries blanked off correctly.
checkpoint-status |  |  | checkpoint | Insulation resistance to earth after installation:
text | c09445fc-320c-52a7-bf83-7211d59d3609 |  | textbox | Insulation resistance: |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Phase to Neutral resistance
text | d3776cb6-c8c7-599a-80ce-d6b58d5f8707 |  | textbox | Insulation resistance: |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Equipment certification meets the area classification requirements.
checkpoint-status |  |  | checkpoint | Confirm warning labels are fixed on outside of pipe lagging
checkpoint-status |  |  | checkpoint | Check correct rating of protection device against design drawings.
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | a70ead30-0c74-5ac3-a2a2-28806f5402b9 |  | textbox | Make:
text | f6ba3ea6-6f01-5ee2-89ad-22e2d8bceaa6 |  | textbox | Model:
text | 47bc0784-a64e-538f-b01c-64808ca7bf2f |  | textbox | Serial No:
text | 32faaeaf-1323-5e10-8883-2d58b25f2b40 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 199b5701-f2a0-5907-b6c6-03add342241d |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 1538cfcc-d7a6-5d4e-9fa4-990ddcc69ada |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 32615f19-5b13-5ec5-bcce-66ceb9a548bd |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-flat |  |  | checklist | Certificate of compliance (COC) |  |  |  |  | Yes | Certificate of compliance (COC) | 9bd20be8-9bc8-4ea5-8c1b-23bb2299c6bb
checkpoint-status |  |  | checkpoint | Please upload Certificate of Compliance here when complete (COC)
checklist-sectioned |  |  | checklist | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation) |  |  |  |  | Yes | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation) | a06bc53b-3dc3-4caf-9a09-9996f14139a4
checkpoint-group |  |  | section | Equipment
checkpoint-status |  |  | checkpoint | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No.
checkpoint-status |  |  | checkpoint | Equipment checked for additional items as applicable
checkpoint-status |  |  | checkpoint | Complete ITR-CL-1-121A and attach
checkpoint-group |  |  | section | Valve
checkpoint-no-status |  |  | checkpoint | Valve
text | 956fba32-cd07-5e6b-8476-b5521de50dc2 |  | textbox | Size:
text | b47d73e2-0eb0-5140-8820-8d2020c31c15 |  | textbox | Flange type:
checkpoint-status |  |  | checkpoint | Material certification correct
checkpoint-status |  |  | checkpoint | Trim material correct
text | 580058e3-1d27-5d51-a5f2-cead7eb5c195 |  | textbox | Rating:
text | 2fd07260-adde-5490-8415-0cf69c194ccd |  | textbox | Service:
checkpoint-status |  |  | checkpoint | Body material correct
text | 9f603954-fc39-5578-b3a3-69de9fbc9434 |  | textbox | Leakage class:
checkpoint-group |  |  | section | Actuator
checkpoint-no-status |  |  | checkpoint | Actuator
text | 26e96c4f-18eb-52c9-b402-8ac226747245 |  | textbox | Input range:
checkpoint-status |  |  | checkpoint | Failure action
checkpoint-status |  |  | checkpoint | Hand wheel operation correct
checkpoint-group |  |  | section | Positioner
checkpoint-no-status |  |  | checkpoint | Positioner
text | 7b0acc06-480f-5b96-a029-375066ee8b13 |  | textbox | Signal range
text | dfbdb3f1-3697-5a74-8334-639700b5c7a7 |  | textbox | Output range
checkpoint-group |  |  | section | I/P Converter
checkpoint-no-status |  |  | checkpoint | I/P Converter
text | 7a5e2db6-ed0e-5c5b-9b4a-75f2d1e68254 |  | textbox | Signal range
text | aa6fa260-5e0b-5bed-b162-c11066ccd6c2 |  | textbox | Output range
checkpoint-group |  |  | section | Filter/Regulator
checkpoint-no-status |  |  | checkpoint | Filter/Regulator
text | 221ac46f-18a0-544c-8ebe-df36da02d7c0 |  | textbox | Range |  |  | kPa
text | edef4f3b-49a3-5f51-8a6a-1d23850a55a2 |  | textbox | Pressure setting |  |  | kPa
checkpoint-group |  |  | section | Fail Action
checkpoint-no-status |  |  | checkpoint | Fail Action
select | 40c751bb-a23d-5c16-b3b9-f63d66c2952e |  | dropdown | Electrical Fail Action | FO, FC, FL
select | a4013177-c71e-51ec-aee8-b3223005d2ee |  | dropdown | Motive Force | FO, FC, FL
checkpoint-group |  |  | section | Proximity Detectors
checkpoint-status |  |  | checkpoint | Open switch set
checkpoint-status |  |  | checkpoint | Open switch mode setting correct
checkpoint-status |  |  | checkpoint | Closed switch set
checkpoint-status |  |  | checkpoint | Closed switch mode setting correct
checkpoint-status |  |  | checkpoint | Electrical connections correct
checkpoint-status |  |  | checkpoint | Electrical certification correct
checkpoint-group |  |  | section | Solenoid Valve
checkpoint-status |  |  | checkpoint | Operation correct
checkpoint-status |  |  | checkpoint | Electrical connections correct
checkpoint-status |  |  | checkpoint | Electrical certification correct
text | c93a7d00-1ce1-57bb-9feb-8a9ee30ceafd |  | textbox | Voltage: |  |  | V
checkpoint-status |  |  | checkpoint | Pneumatic connections correct
text | aee21bfe-387b-50b6-9b0e-97a0cf7d55ec |  | textbox | Pneumatic pressure |  |  | kPa
checkpoint-group |  |  | section | Pilot Valve
checkpoint-status |  |  | checkpoint | Pneumatic connections correct
checkpoint-status |  |  | checkpoint | Operation correct
checkpoint-status |  |  | checkpoint | Action/Lockup
checkpoint-group |  |  | section | Hydraulic Actuator
checkpoint-no-status |  |  | checkpoint | Hydraulic Actuator
text | 50ab6aec-d971-5823-8948-58099b348c22 |  | textbox | Working pressure
text | 05762a41-47a1-5396-a7e2-da5eb5e15313 |  | textbox | Manifold pressure
text | 11800bd5-41f8-5d1a-b549-f6b9a2f75559 |  | textbox | Fluid type
checkpoint-status |  |  | checkpoint | Hydraulic connections correct
text | c54aea5b-ce91-56e1-85a8-17f76da097a9 |  | textbox | Regulator pressure setting
checkpoint-status |  |  | checkpoint | Pilot operation correct
checkpoint-group |  |  | section | Accumulator
checkpoint-status |  |  | checkpoint | N2 Charge required
text | e925041f-f1e4-5308-8092-259af6247d25 |  | textbox | N2 Pre-charge pressure
text | d1c3e58c-8fea-5ac0-8501-9994f0f3b2f6 |  | textbox | Pressure switch setting
text | 9ec7081b-9499-5595-93b9-be0205e8beca |  | textbox | Working pressure
text | 149cf975-110e-53fd-96a3-c4cc57b03655 |  | textbox | Output range
checkpoint-status |  |  | checkpoint | Volume tank & check valve installed correctly
checkpoint-group |  |  | section | Electric Actuator
checkpoint-no-status |  |  | checkpoint | Electric Actuator
text | db0ddb55-2e3e-5cb0-b280-1a3dc487b4fb |  | textbox | Voltage:
text | dd1f432a-1f12-5b9d-9aad-e14cc59e5d8a |  | textbox | Electrical certification correct
text | a396421b-70d7-534c-adc2-4fcd9232e02a |  | textbox | Electrical connections correct
text | 803e3d7b-ed4c-5026-8703-1e97dd242a2f |  | textbox | Remote operation correct
text | b5b07e97-01d6-50d0-b447-cb8ca83dd066 |  | textbox | Local hand operation correct
text | cdc5fc20-1772-5d12-b5d8-794b51691d81 |  | textbox | Torque switches and travel stops set
checkpoint-group |  |  | section | Miscellaneous Equipment
checkpoint-no-status |  |  | checkpoint | Miscellaneous Equipment
text | aa465e14-1b4f-5921-bb1b-3f282a8eaf5e |  | textbox | Description
text | 8d43bfb4-73a3-5d7a-b1c4-f886ff3c1774 |  | textbox | Manufacturer
text | 1cc38c32-041e-5abf-a3a2-4a3174751291 |  | textbox | Model No:
text | 68178d54-8ece-5a43-b8fd-e3904d76edce |  | textbox | Serial No:
text | 66d3f560-bbc5-5f18-b6f5-0fc1c6631864 |  | textbox | Range:
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 8618de3a-01e8-5e34-bf06-a6b708e2cd18 |  | textbox | Make:
text | a744819c-f291-59e2-9944-1f375556543e |  | textbox | Model:
text | 8c3f338e-cd5e-5d66-8e85-85713b532746 |  | textbox | Serial No:
text | df0eb806-7c2a-5569-8408-22867cad2260 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 9f83c1d9-9f3c-56d0-b2b2-f3c270329952 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 74c7ab23-7028-589b-8540-ddcdde9245c8 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 65e2c0a3-095c-507e-a375-4be1549d4943 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-115 Lightning Protection |  |  |  |  | Yes | ITR-CL-1-115 Lightning Protection | a0bbc43d-9ab8-4173-b931-ba29b6f962ef
checkpoint-group |  |  | section | Lightning protection checks
checkpoint-no-status |  |  | checkpoint | Lightning protection checks
label | 34cfae9b-fc0b-54f1-979c-fea74227cf83 |  | note | These checks shall be conducted in accordance with the requirements of AS/NZS 1768:2007
checkpoint-status |  |  | checkpoint | Check lightning conductor is 2 metres or more above the entire protected area
checkpoint-status |  |  | checkpoint | Check the materials and equipment used for the down conductors are suitable
checkpoint-status |  |  | checkpoint | Check the down conductors are routed, located and electrically bonded as required
checkpoint-status |  |  | checkpoint | Check all installed components are firmly secured
checkpoint-status |  |  | checkpoint | Check the method of protection against electric shock, including the measurement of distances
checkpoint-status |  |  | checkpoint | Check the resistance of all connections at the location of the connection. The resistance of each connection shall not exceed 0.05 Ohm
checkpoint-status |  |  | checkpoint | Earth termination system resistance is correct
text | 77ed97c3-8ac6-5fd9-8cae-0b9fa6d20a38 |  | textbox | Resistance value: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Insulation resistance of the electrical installation
text | b7a5cfb8-e556-5fd2-a846-2a3214ef8da2 |  | textbox | IR |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Continuity of main and supplementary bonding
text | 67a085c2-895c-56d5-b11e-6c5bf50e1fdf |  | textbox | Main bonding: |  |  | Ohm
text | a2fa0ea6-ccda-5e8c-be9c-690ac731fedf |  | textbox | Supplementary bonding: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Check earth termination systems are interconnected
checkpoint-status |  |  | checkpoint | Check isolating and switching devices correctly located
checkpoint-status |  |  | checkpoint | Check warning signs and diagrams are installed
checkpoint-status |  |  | checkpoint | Check accessibility for operation and maintenance
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | d722ac38-8ce9-58d2-a19b-518fa2a1ea5c |  | textbox | Make:
text | f84bde51-0c23-5c7b-8c72-e5568a5bcd8e |  | textbox | Model:
text | 6011c3cb-a7c4-5e15-a8fa-aa5504015d9e |  | textbox | Serial No:
text | 614e60b8-300f-5f35-8ccb-6e0cde30152d |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 8fb33ecd-9f67-5841-9a63-a5e30c461415 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | c7688f92-da9d-5298-818a-a0fe77f75fa0 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 07d72dfd-4ed2-5aa2-b171-3f019152f114 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-112 Motors |  |  |  |  | Yes | ITR-CL-1-112 Motors | be3fc2f8-3a35-4e15-acdf-a44df28b0d3d
checkpoint-group |  |  | section | Inspection
checkpoint-status |  |  | checkpoint | Tag number correct
checkpoint-status |  |  | checkpoint | Area Classification correct
text | 36e7f781-af58-5a48-9bdc-833b4b2ea657 |  | textbox | IP Rating:
text | c39c0333-85cb-5b96-a90d-48bb37a46ec5 |  | textbox | Hazardous area cert:
checkpoint-status |  |  | checkpoint | Electrical Connections correct
button | a45f01e2-a36c-5049-ad03-5414d38eb60c |  | button | Space heater | YES,NO
text | 231882b6-9c37-5b2a-ba46-6d87a925ea02 |  | textbox | Space heater Volts:
text | 97c12508-e4b4-5197-bb39-694d90d4401a |  | textbox | Space heater Power (Watts) |  |  | W
checkpoint-status |  |  | checkpoint | General condition
checkpoint-group |  |  | section | Nameplate Details
checkpoint-no-status |  |  | checkpoint | Nameplate Details
text | 457ab0d8-92b2-5909-a391-3e2384ce5a22 |  | textbox | Tag No:
text | 14d94795-ae07-5485-8466-4ff4aa453dbd |  | textbox | Manufacturer:
text | ce759b73-0ef2-5aad-bc5d-c53fdc8ca853 |  | textbox | Motor Serial Number:
select | 146fecb6-e02b-50f0-a8ba-0139232ff9c6 |  | dropdown | Phases: | Single-Phase, Three-Phase
text | 9fc9c987-c9a9-5ab9-9cd0-1dadf7c064a2 |  | textbox | Frame:
text | 72c6303c-1dba-5d55-b9a5-808fda08ef7e |  | textbox | Enclosure:
text | b8583d30-73a4-5254-9ac1-bff56b0f0a2b |  | textbox | Voltage: |  |  | V
text | 6c26bf4c-77ff-5cd3-9406-61a05a893cf7 |  | textbox | Current: |  |  | A
text | 27abb364-c1c3-5100-a716-20c5842fcace |  | textbox | kW: |  |  | kW
text | 0c4dfe25-e16f-5f11-a463-425d4add8cbf |  | textbox | Speed:
text | 8da343a0-0cb3-508f-8374-142ea4faf2ff |  | textbox | PF:
text | 9d5aec02-dce6-5c59-a044-48b85d8ea51f |  | textbox | No. of Poles:
text | cd6ea616-1a8b-54ea-98c7-334af559a546 |  | textbox | Insulation Class:
select | dd694193-538a-57f7-a54a-6bcb8f550e9e |  | dropdown | Rotation direction (looking down shaft) | Clockwise, Counter-Clockwise
checkpoint-status |  |  | checkpoint | Bearing Specs
text | a67d63df-3f64-54d1-99c0-fe058c639d1d |  | textbox | Drive end
text | 69accf3e-6ada-5ad5-be13-3579bcf4e096 |  | textbox | Non Drive end
checkpoint-group |  |  | section | Checklist items
checkpoint-status |  |  | checkpoint | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets
checkpoint-status |  |  | checkpoint | Check Equipment and Nameplate details are correct in accordance with the data sheet.
checkpoint-status |  |  | checkpoint | Identification Tag and Rotation Plate correctly fitted
checkpoint-status |  |  | checkpoint | Motor electrical coupling (Delta /Star) as per voltage is correct.
checkpoint-status |  |  | checkpoint | Check for mechanical condition, air ducts and fan free of debris
checkpoint-status |  |  | checkpoint | Correct glanding for area classification.
checkpoint-status |  |  | checkpoint | Holding down bolts fitted correctly.
checkpoint-status |  |  | checkpoint | Check bearing lubrication.
checkpoint-status |  |  | checkpoint | Check free rotation with driven equipment uncoupled
checkpoint-status |  |  | checkpoint | Cable(s) correctly terminated, labelled and colour identification
checkpoint-status |  |  | checkpoint | Terminations/ connections torqued correctly to data sheets.
checkpoint-group |  |  | section | Motor Installation Testing
checkpoint-status |  |  | checkpoint | LV Motor winding insulation resistance with cables disconnected
checkpoint-status |  |  | checkpoint | 1 Minute
text | 3149a583-c6ac-5f73-89d1-eec97e16738f |  | textbox | Winding "U" |  |  | MegaOhms
text | c9417ea5-5a97-580c-af67-551257a5c314 |  | textbox | Winding "V" |  |  | MegaOhms
text | 56832416-63be-53ae-b1d5-7f3ddbd3fdc9 |  | textbox | Winding "W" |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | 10 Minutes
text | 8cd22815-e8fd-5ea2-a3bd-0d81b78a570e |  | textbox | Winding "U" |  |  | MegaOhms
text | 1f964fbb-bf86-514b-bb89-cf13688833be |  | textbox | Winding "V" |  |  | MegaOhms
text | 9f5cf67f-ba43-534e-a367-5a44b0d338e3 |  | textbox | Winding "W" |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Motor continuity between windings
text | e14ac467-cb9d-53ec-aed7-6ee8e64540ea |  | textbox | U1 - U2 |  |  | Ohms
text | 09f963df-3eea-5905-83fa-ee23ac13eafe |  | textbox | V1 - V2 |  |  | Ohms
text | 27347b14-3f4f-58ff-abd9-d0f22b92f359 |  | textbox | W1 - W2 |  |  | Ohms
checkpoint-status |  |  | checkpoint | Space heater continuity & resistance check
text | 49468bfb-1827-5640-ad6e-81e55e776494 |  | textbox | Continuity: |  |  | Ohms
text | 1770d377-6abc-5868-b0bc-c2803cee586e |  | textbox | Insulation Resistance: |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Thermostat or RTD wiring resistance check
text | 6a455f78-5cf4-532a-92ea-8adb33dfd38e |  | textbox | Resistance: |  |  | Ohms
checkpoint-status |  |  | checkpoint | Check motor is earthed correctly and record motor earth bond:
text | bb8f5c02-1729-5135-82d0-92ef659fca18 |  | textbox | External bond continuity: |  |  | Ohms
checkpoint-group |  |  | section | Additional checks
checkpoint-status |  |  | checkpoint | Visual Inspections
checkpoint-status |  |  | checkpoint | Winding temperature detector
checkpoint-status |  |  | checkpoint | Air temp detectors
checkpoint-status |  |  | checkpoint | Bearing temp indicators
checkpoint-status |  |  | checkpoint | Vibration Monitors
checkpoint-status |  |  | checkpoint | Condensation detector
checkpoint-status |  |  | checkpoint | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable)
checkpoint-status |  |  | checkpoint | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable)
checkpoint-status |  |  | checkpoint | Installation conforms to specification and drawings
checkpoint-status |  |  | checkpoint | As-Builts complete
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 5201dca0-4420-50d1-bd00-95e88efa92c4 |  | textbox | Make:
text | fe7a6eb9-9df7-5598-8436-81d87d02b7e4 |  | textbox | Model:
text | b908b99e-b5e5-5d3f-9e15-68984009101b |  | textbox | Serial No:
text | d22171dc-1f9b-5d7b-85bc-bf4b3aae14dc |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 870fe42a-c158-5be1-b11e-a59d7b4f2831 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 49eaf4c5-49d5-5bd9-adc7-72d0fc8a4b0b |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | a4425503-bcb7-5be5-931c-5ddd066529d2 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-104 Cable Installation |  |  |  |  | Yes | ITR-CL-1-104 Cable Installation | be798428-dd61-4074-af18-c7c3a6018eae
checkpoint-group |  |  | section | Cable Installation
checkpoint-status |  |  | checkpoint | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule.
checkpoint-status |  |  | checkpoint | Check dressing/cleating.
checkpoint-status |  |  | checkpoint | Check cable for damage.
checkpoint-status |  |  | checkpoint | Check cable cores correctly identified and labelled.
checkpoint-status |  |  | checkpoint | Cable terminated with correct lugs and crimped with the correct die.
checkpoint-status |  |  | checkpoint | Check that cable phasing is correct and point-to-point each core for continuity.
checkpoint-status |  |  | checkpoint | Check Armour/Screen correctly made off.
checkpoint-status |  |  | checkpoint | Check armour continuity /earthing is maintained by the correct use of serrated washers and/or earth tags.
checkpoint-status |  |  | checkpoint | Glanding/Locknuts correctly installed.
checkpoint-group |  |  | section | Gland type - from:
checkpoint-no-status |  |  | checkpoint | Gland type - from:
text | b7acb3ae-e1df-5ced-b494-28e94f9f2152 |  | textbox | Haz. Area Rating:
text | 2691fd49-4240-5fa4-be5c-d2e475b350e8 |  | textbox | Haz. Area Cert Details:
checkpoint-group |  |  | section | Gland type - to:
checkpoint-no-status |  |  | checkpoint | Gland type - to:
text | 7d30a21f-32a5-5760-821f-93d55ad53b6a |  | textbox | Haz. Area Rating:
text | af9742be-d02d-5774-9777-b5e8b9ba202f |  | textbox | Haz. Area Cert Details.
checkpoint-group |  |  | section | Electrical Testing
checkpoint-status |  |  | checkpoint | IR Testing - LV Cables
label | cb4d5f0d-7f49-5824-a216-dd8fb6a6d277 |  | note | (Test voltage 1,000 VDC for LV cables and 5KVDC for HV cables)
text | 9aed7745-14e9-52f3-8001-bb12d02b2e99 |  | textbox | L1 – Earth |  |  | MegaOhms
text | 61c4e66e-f1d2-5938-b006-051143d8a2c8 |  | textbox | L2 – Earth |  |  | MegaOhms
text | 80e3ccae-606a-5adc-bf6e-694822ea45b0 |  | textbox | L3 – Earth |  |  | MegaOhms
text | 0c9f0d63-8976-5b60-8839-49818ea1c7f4 |  | textbox | L1 – L2 |  |  | MegaOhms
text | 0c9eeb38-d3c0-5e70-9ff7-b717a0ce9b19 |  | textbox | L1 – L3 |  |  | MegaOhms
text | 0b292c68-cce1-5eb8-8bc9-b831ec0a6d40 |  | textbox | L2 – L3 |  |  | MegaOhms
text | 29dc63a8-22e8-5ad9-82ad-7044a80caae4 |  | textbox | N – Earth |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | IR Testing - Multiple conductor cables (Record lowest readings)
text | 7452c9d0-22ba-5307-8cc0-3cd4237d77d0 |  | textbox | Between Conductors |  |  | MegaOhms
text | 76e245a7-db1b-5bba-9eb4-c3faf8c30fb2 |  | textbox | Conductors to GND |  |  | MegaOhms
text | 3b0541b7-a199-5f32-abfe-b5f87843448b |  | textbox | Measure gland body continuity to earth. (Max 0.1 Ohm) |  |  | Ohm
checkpoint-status |  |  | checkpoint | Confirm cable routing and segregation is correct.
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 6a92f594-3d5e-595f-b086-82198b146b0f |  | textbox | Make:
text | 7f2d3c0e-af57-5415-addb-caff5d0882ff |  | textbox | Model:
text | cefaddb4-52bd-52aa-b631-649d1ccb2898 |  | textbox | Serial No:
text | 9e1d0243-20ba-5783-ac3f-24d3e6a32484 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | a2adbbf6-f81a-5ef1-95fd-0a89f39e92a8 |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 532ced6f-ce9b-5b01-b2da-3ea11d11a784 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 57e6ade9-062b-5220-af30-08da1a156a1a |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-110 Generator Package (LV) |  |  |  |  | Yes | ITR-CL-1-110 Generator Package (LV) | c05e844b-ea04-4511-8b7c-07d5c88c5633
checkpoint-group |  |  | section | Generator Package (LV)
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | No mechanical damage and paintwork in good condition.
checkpoint-status |  |  | checkpoint | Check terminal boxes and glanding correct.
checkpoint-status |  |  | checkpoint | Check earthing is correct.
text | df2bb6bb-6f82-5fe1-9adc-bf04c7753fa6 |  | textbox | Test and confirm the generator earth to local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status |  |  | checkpoint | Instruments correctly installed.
checkpoint-status |  |  | checkpoint | Heaters correctly installed.
text | 0a5cdab1-8ec5-5330-9d3a-8ad85915fde8 |  | textbox | Heater circuit Insulation Resistance: |  |  | MegaOhms
checkpoint-status |  |  | checkpoint | Check unit for cleanliness.
checkpoint-status |  |  | checkpoint | Check manual operation of selector switches, MCB, push buttons etc.
checkpoint-status |  |  | checkpoint | External cabling correctly installed.
checkpoint-status |  |  | checkpoint | Protection of live parts adequate.
checkpoint-status |  |  | checkpoint | Main terminal box complete and terminations correct torque.
checkpoint-status |  |  | checkpoint | Ensure direction of rotation is clearly marked.
checkpoint-status |  |  | checkpoint | Check gasket and seals are not damaged.
checkpoint-status |  |  | checkpoint | Unused cable entries are correctly sealed.
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 64151d05-fb93-56f2-9d19-cf969d544ecd |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 5e2b6573-ea76-5a38-970f-7e0f9883de11 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | d6569301-d36b-544e-8afd-b010e0ff4a3b |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | JHA - Job Step |  |  |  |  | Yes | JHA - Job Step | c482ae65-4b47-488e-8a5b-01d9c2bf9e38
checkpoint-group |  |  | section | Task Step - add task step for each individual task
checkpoint-no-status |  |  | checkpoint | Task Step - add task step for each individual task
date | 1b7d4881-c01a-551f-83a1-3c4096c02052 |  | date | Date:
text | 68fb161a-541b-5cfc-a3a4-bc0a0ed14530 |  | textbox | Task step number (eg. Step 1, Step 2 etc):
text | c04cb7f5-9ca4-591e-b67a-e8ef61208422 |  | textbox | Task details:
text | 027a875a-1c66-5441-9d0d-ba90bedda0d8 |  | textbox | Hazards:
select | 872706be-9417-5f3f-9fb3-8a4391787c82 |  | dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
text | 608f90b3-b68c-50db-bd96-863af69c75dc |  | textbox | Potential consequence:
text | 9c46ced1-c79e-516c-bbb0-126f867ab08c |  | textbox | Controls:
text | 916ed1c9-c91c-5339-841d-fa7458e4f021 |  | textbox | Recovery steps:
select | f180a276-20de-5246-be81-3c44588e6d91 |  | dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
checklist-sectioned |  |  | checklist | ITR-CL-1-108 Electrical Switch Rooms |  |  |  |  | Yes | ITR-CL-1-108 Electrical Switch Rooms | c7775046-9570-4798-9498-892e35e330de
checkpoint-group |  |  | section | Electrical Switch Rooms
checkpoint-status |  |  | checkpoint | Substation construction finished
checkpoint-status |  |  | checkpoint | All floor, wall & ceiling penetrations sealed.
checkpoint-status |  |  | checkpoint | Danger, warning & resuscitation signs installed
checkpoint-status |  |  | checkpoint | All equipment installed
checkpoint-status |  |  | checkpoint | Lighting & general power installation complete
checkpoint-status |  |  | checkpoint | All earth busbars installed satisfactorily & connections tight
checkpoint-status |  |  | checkpoint | All telecommunication equipment is installed & operational
checkpoint-status |  |  | checkpoint | Smoke / Heat detectors installed (Including Vesda / Alarm Panel)
checkpoint-status |  |  | checkpoint | Substation fire alarm panel installed
checkpoint-status |  |  | checkpoint | HVAC equipment installed & operational
checkpoint-status |  |  | checkpoint | Illuminated exit signs installed & operational
checkpoint-status |  |  | checkpoint | Hand-held fire extinguishers installed with correct type available
checkpoint-status |  |  | checkpoint | All doors and locks operational (including emergency)
checkpoint-status |  |  | checkpoint | All keys available and handed to Commissioning E&I Superintendent
checkpoint-status |  |  | checkpoint | All safety equipment supplied – rubber mats, voltage sticks etc
checkpoint-status |  |  | checkpoint | Single line diagram detailing main power is fitted to wall
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | fe65a33e-5726-50ec-b421-4e205c089d4c |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | e95a3a46-6d4b-5409-8fb7-472a44ec5d8f |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | ea060598-b670-5251-8008-26d77d3edc87 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-flat |  |  | checklist | ITR-CL-1-103 Schedule of Test Results DB |  |  |  |  | Yes | ITR-CL-1-103 Schedule of Test Results DB | dcd4930d-da2b-4750-9fb0-3f9e2e738805
checkpoint-status |  |  | checkpoint | Upload completed ITR scans
checklist-sectioned |  |  | checklist | ITR-CL-1-123 Instrument Pre-Commissioning |  |  |  |  | Yes | ITR-CL-1-123 Instrument Pre-Commissioning | e06ad27c-0f9a-478e-9dea-0efcb09e0a25
checkpoint-group |  |  | section | Checklist items
checkpoint-status |  |  | checkpoint | Verify transmitter loop connection - Remove wre on transmitter and confirm at Control System interface
checkpoint-status |  |  | checkpoint | Relevant individual control system/ESD loops have been checked and test sheets completed
checkpoint-group |  |  | section | Analogue Input:
checkpoint-no-status |  |  | checkpoint | Analogue Input:
text | 32af0557-c17f-5a7b-b227-2342fe5bb32e |  | textbox | Input range & units:
text | c9856afd-c129-5e54-8491-456847d30adc |  | textbox | Indication range & units:
checkpoint-status |  |  | checkpoint | 0% Rising
text | ccd800be-a518-55e2-94f0-f2848c99d79e |  | textbox | Input Signal:
text | 1a6f7156-6515-5a53-941d-64018bf898ba |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 25% Rising
text | 2dd6da3e-1cd5-5652-a0b1-840a91958b7c |  | textbox | Input Signal:
text | 12d6370f-6773-5235-811b-3d82a83c6333 |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 50% Rising
text | 16a0e494-faff-53fb-b40c-c10ddb3e67e3 |  | textbox | Input Signal:
text | e98ad077-5f7b-51f2-92f5-cea63e6d0f6c |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 75% Rising
text | a9661a6d-09a5-5222-a165-71dd46923991 |  | textbox | Input Signal:
text | ee76ca88-f427-5695-bd52-111e59a525d2 |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 100% Peak
text | 1ca474fd-9fbd-5528-9b42-1a3e8cb87935 |  | textbox | Input Signal:
text | d62e4e0a-c9ad-5068-b203-bcd83cd39276 |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 75% Falling
text | d4fcae29-f874-57b4-9d62-000d4571c268 |  | textbox | Input Signal:
text | 57bee066-9814-523e-ad53-66d808dfe569 |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 50% Falling
text | f75ff69e-afce-5681-b03c-d4cd3ff45cec |  | textbox | Input Signal:
text | 21006a64-3ef5-58dc-9798-3a87abf30854 |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 25% Falling
text | 6ce8e5fd-dea0-52bb-a7af-f12e57726300 |  | textbox | Input Signal:
text | 5de298c2-fd97-5c8b-8728-2663f74d85f1 |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | 0% Falling
text | cc9693e0-36eb-5697-a53d-65e5508851fa |  | textbox | Input Signal:
text | 878efe6a-4c11-52eb-9e50-a63b6f3e8b54 |  | textbox | Control Interface Indication:
checkpoint-group |  |  | section | Digital Input/Analogue Alarm Trip Points
checkpoint-status |  |  | checkpoint | Alarm Lo:
text | 7bda09b6-6999-55fd-b271-bdfdca915b3c |  | textbox | Alarm setting
text | fbb90c00-bfd9-558b-b34f-e8dc26e1df98 |  | textbox | Measured Alarm Point
text | 4d2f1aad-fb8d-5ab9-9e1c-655c21125cbb |  | textbox | Filter/Time Delay
text | 79ced695-5fe3-59b0-ae34-d03762181f77 |  | textbox | Result
checkpoint-status |  |  | checkpoint | Alarm Lo-Lo:
text | 7c561bd2-6b06-5b93-b5ba-8940bb939eb7 |  | textbox | Alarm setting
text | cd91aeda-9b4f-5132-b2b0-fdd4215236fb |  | textbox | Measured Alarm Point
text | 64d9d2d3-29f8-5ee6-b240-4ca9b97712f1 |  | textbox | Filter/Time Delay
text | c10e5016-de4b-5b10-aa39-d3043b5f6e9e |  | textbox | Result
checkpoint-status |  |  | checkpoint | Alarm Hi:
text | 1ff45bf2-284b-59d8-bdc1-d1b063d0cc59 |  | textbox | Alarm setting
text | fc198fd7-07ee-511a-82e3-f53d8bcb71a7 |  | textbox | Measured Alarm Point
text | 116093ed-feef-5594-a123-8c4a3cd7790a |  | textbox | Filter/Time Delay
text | 3c35d845-87a5-544f-ab75-472dfed71267 |  | textbox | Result
checkpoint-status |  |  | checkpoint | Alarm Hi-Hi:
text | 8af7e2c3-6ff3-5d67-8676-c9f0e0fd624b |  | textbox | Alarm setting
text | 39ac170c-733f-50cc-a168-769148e050e9 |  | textbox | Measured Alarm Point
text | 85ad08f0-064c-55b5-a652-a1226ca6e185 |  | textbox | Filter/Time Delay
text | 1bcd0965-6db1-576d-a7e4-6753ddf21bba |  | textbox | Result
checkpoint-status |  |  | checkpoint | Control loop set points correct:
text | 69a00ea7-08d4-549d-a5a8-f7c472c817fc |  | textbox | Set Point 1:
text | 8df41374-f8db-5d4b-96da-531142b4388c |  | textbox | Set Point 2:
text | ecaa00de-918e-5f3d-a950-8966dcbc2cfa |  | textbox | Set Point 3:
text | ca2ab42e-57c4-54cc-83a8-8a1af7433d37 |  | textbox | Set Point 4:
checkpoint-group |  |  | section | Startup, Shutdown and Override functions
checkpoint-status |  |  | checkpoint | Control system graphic display
checkpoint-status |  |  | checkpoint | Control system point display
checkpoint-status |  |  | checkpoint | ESD graphic display
checkpoint-status |  |  | checkpoint | Alarm Recording and Text
checkpoint-group |  |  | section | Additional checks
checkpoint-status |  |  | checkpoint | Control system display and alarms are correct as per control functions
checkpoint-status |  |  | checkpoint | Transmitter fail direction and burnout are to spec (Upscale/Downscale)
checkpoint-status |  |  | checkpoint | Switch action verified, including power loss
checkpoint-status |  |  | checkpoint | Drawings, documents and As-Builts scanned and attached
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 4686280e-a578-510d-890d-bbfadc42dc17 |  | textbox | Make:
text | 4fe9f2e7-27af-5e59-961c-a391ebe1fc57 |  | textbox | Model:
text | 9610057a-b90b-53ca-9309-9e3695dbf124 |  | textbox | Serial No:
text | ba0d9e96-491e-533c-92cd-e33e86db0c7b |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | db3ebe68-7995-5ef2-a704-526028c82afc |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | b2fdf54a-5cc4-5dae-9ff1-474f08a02968 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 5eef584c-48b4-56e4-9f96-ed97a92c6851 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-129 Flow Meter Installation |  |  |  |  | Yes | ITR-CL-1-129 Flow Meter Installation | e1c7beda-b30a-4611-a348-4c2876249b4e
checkpoint-group |  |  | section | Flow Meter Installation
checkpoint-status |  |  | checkpoint | Check instrument nameplate details are correct in accordance with the instrument index
checkpoint-status |  |  | checkpoint | Flow meter calibrated before installation (ITR-CL-1-123 Instrument Calibration)
checkpoint-status |  |  | checkpoint | Ensure location and tapping point is verified as per P&ID & location drawings
checkpoint-status |  |  | checkpoint | Ensure direction of flow is correct with respect to flow meter
checkpoint-status |  |  | checkpoint | Check mechanical clearance is adequate for installation of flow meter
checkpoint-status |  |  | checkpoint | Verify type and size of gasket is correct between process line and measuring unit flange
checkpoint-status |  |  | checkpoint | Ensure correct nut and bolt grade and material for connecting unit to process line
checkpoint-status |  |  | checkpoint | Verify display/cover is oriented for ease of use for operators and access for technicians
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 4a94d6a9-bfc9-5ce9-a840-24ae3543e88e |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 7fc347fb-bc1a-5839-aabf-2a5c56ae3451 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 875bb191-1eaa-515c-b1b0-093f70eb656e |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-130 Pressure Instrument Installation |  |  |  |  | Yes | ITR-CL-1-130 Pressure Instrument Installation | e72653eb-7c07-443d-84d4-1d11b5fa0633
checkpoint-group |  |  | section | Pressure Instrument Installation
checkpoint-status |  |  | checkpoint | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint-status |  |  | checkpoint | Pressure Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration)
checkpoint-status |  |  | checkpoint | Instrument mounted as per hook-up drawings
checkpoint-status |  |  | checkpoint | Air line/Impulse line are correct material to site specifications
checkpoint-status |  |  | checkpoint | Air line/Impulse line are routed tidily and as per hook-up drawings
checkpoint-status |  |  | checkpoint | Correct bolt size and material/grade used
checkpoint-status |  |  | checkpoint | Local indicator is mounted and easy to read, easy access for technicians
checkpoint-status |  |  | checkpoint | Instrument and tubing are adequately supported as per drawings
checkpoint-status |  |  | checkpoint | Isolation valve installed
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | a76cc5e1-6efd-5ab0-aa92-b732995400ea |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 8a0bfbe0-57e2-5f2e-af2e-d74354befa37 |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | b65b9302-5c42-5957-92cb-192e2a95fa71 |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | ITR-CL-1-116 Fire and Gas Detection Alarms |  |  |  |  | Yes | ITR-CL-1-116 Fire and Gas Detection Alarms | e84c7c85-8201-49ff-9373-2a47e9b1a47a
checkpoint-group |  |  | section | Checklist items
checkpoint-no-status |  |  | checkpoint | Checklist items
text | 129e6e26-b694-5b22-abc8-18c763bd3f92 |  | textbox | Manufacturer
text | 5d580cd7-2439-5e82-a1fd-adf48d351437 |  | textbox | Make and Model
text | 47dd8ae2-dcb4-5cf7-9b54-6f2709e62baf |  | textbox | Type
checkpoint-status |  |  | checkpoint | Labelling/Number correct
checkpoint-status |  |  | checkpoint | Component & Type / Model correct
checkpoint-status |  |  | checkpoint | Cable connection & termination correct
checkpoint-status |  |  | checkpoint | Mechanical damage
checkpoint-status |  |  | checkpoint | Glanding condition
checkpoint-status |  |  | checkpoint | E.O.L Installation
checkpoint-status |  |  | checkpoint | Installation of Test tubing
checkpoint-status |  |  | checkpoint | Location correct
checkpoint-status |  |  | checkpoint | Detection Path Clear
checkpoint-group |  |  | section | Inspection
checkpoint-status |  |  | checkpoint | Tag No. Correct
text | f5909554-0829-55be-8501-16dcff85c511 |  | textbox | Tag No:
text | 23246d62-ac79-5074-b614-f5a53c66f8c8 |  | textbox | RX Tag No:
checkpoint-status |  |  | checkpoint | Area Classification correct
text | 2843d97e-2ee5-50ed-b3ab-4913bbfba422 |  | textbox | Hazardous Area Certificate:
text | dd836385-b58a-5e6b-bb24-a98984b15f22 |  | textbox | Detector Type:
text | 360f5d53-f852-5864-ad76-08bbea0c7abc |  | textbox | Gas Type:
checkpoint-status |  |  | checkpoint | Body Material Correct:
checkpoint-status |  |  | checkpoint | General Condition Satisfactory
text | 4f82c966-6799-57ec-b965-6721e7f3e8b4 |  | textbox | Supply Voltage:
text | 1721f8e8-7e2c-55f9-8a4c-6c349177db12 |  | textbox | Output Signal:
checkpoint-group |  |  | section | Functional Check
checkpoint-status |  |  | checkpoint | Self Test
checkpoint-status |  |  | checkpoint | Alarm Operation
checkpoint-status |  |  | checkpoint | Fault Relay Operation
text | 41db7ca0-27bd-5259-aca4-a639944d632f |  | textbox | Measured output (clear path)
text | 56c9629e-a2ea-5769-8f4b-fef2ae430804 |  | textbox | Measured output (blocked path)
text | 16e90bc2-a991-57d9-b6ff-9f3faa21113b |  | textbox | Measured output (filter in place)
checkpoint-group |  |  | section | Test Equipment
checkpoint-no-status |  |  | checkpoint | Test Equipment
text | 0e0b40aa-a1f1-58cf-9985-a0cf42ff436c |  | textbox | Make:
text | 396cf58c-1951-5e36-bb88-37cb9650739d |  | textbox | Model:
text | 7743aa38-2f72-5392-bf22-60217ce6b211 |  | textbox | Serial No:
text | 227ef094-b263-5852-aaec-75de62c2fb18 |  | textbox | Calibration Expiry:
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | 42a9ba4c-6bb0-5dde-a772-9b294d1c026f |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | aed95085-6755-58ed-b1c9-78b8cec8104d |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 928a7520-6c58-583f-9822-3f815282f1ce |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed
checklist-sectioned |  |  | checklist | JHA - Job Hazard Analysis |  |  |  |  | Yes | JHA - Job Hazard Analysis | ea541219-0fcf-4ae0-9c9f-55a150c1ead4
checkpoint-group |  |  | section | Job details
checkpoint-no-status |  |  | checkpoint | Job details
date | f6494b70-76e8-5ee0-86a7-5b8f94386108 |  | date | Date:
text | b7fd2905-d6f7-5f70-beec-fc56657d7dbf |  | textbox | Permit No.
text | 2786faa1-a237-5764-bbff-a0476df3af48 |  | textbox | Job No.
text | ba583da4-ff42-57c3-b4e1-9c7045a1ef45 |  | textbox | Site
text | cffce99c-f616-5da3-ab54-2b51d0f55484 |  | textbox | Activity Location
text | 96a35454-4991-5e65-8770-bf6439debbce |  | textbox | Asset:
text | 1bc43788-635b-5433-b329-d0dcdea170b6 |  | textbox | Work Details:
checkpoint-group |  |  | section | Prompts for Hazards - Mark all that apply.
checkpoint-no-status |  |  | checkpoint | Prompts for Hazards - Mark all that apply.
button | 5dff6889-1f01-5b30-9e1a-8347bdb2eefe |  | button | Sparks/Open flame | YES,NO
button | 3facdf13-bab3-5d10-8656-99cc2b9a5e20 |  | button | Disabled safety device(s) | YES,NO
button | f45995a7-6bc9-5973-94ec-319129af753c |  | button | Uneven surfaces | YES,NO
button | 6b08445b-7a7a-5f4e-b5dc-0dc5022b607a |  | button | Fatigue, over-exertion | YES,NO
button | 095dcd85-e3bd-5d16-9005-f961790574da |  | button | Crane movements | YES,NO
button | a24fb356-e8a4-5c7b-9ed1-563dab2a64e6 |  | button | Moving/Rotating parts | YES,NO
button | 44955bbc-01ae-5128-82ae-8e7a78e83e87 |  | button | Remote area, working alone | YES,NO
button | c4eb7c0c-ec14-50b8-9d05-f97e728fed64 |  | button | Conflicting work/SIMOPS | YES,NO
button | 1ca6b032-89ef-5820-8fbe-9aaf571f1592 |  | button | Electrical arc flash | YES,NO
button | 73405348-8206-5e46-82d1-0dedb6795490 |  | button | Sharp objects/materials | YES,NO
button | 8645a661-81e9-5c4e-8434-e39b5bd1b460 |  | button | Restricted/Difficult Entry/Exit | YES,NO
button | e8cbe405-8f9e-5fcf-96fa-d50b5109dffc |  | button | Overhead obstacles | YES,NO
button | a16dfe32-6027-5a7f-a761-dd9cc84da263 |  | button | Ignition sources (other) | YES,NO
button | 29468071-52bd-558f-ac63-58e4fea20f39 |  | button | Access/Egress | YES,NO
button | 07ee8713-6d4d-575c-b58d-3a8a27ab0e64 |  | button | Water body | YES,NO
button | 8c6c1cfa-31ef-5dd1-b2d9-997eb4b6c601 |  | button | Live equipment | YES,NO
button | c8636cec-6c33-517d-8438-a2bebb7f05ed |  | button | Slippery surfaces | YES,NO
button | f900ef1d-b01c-5ed2-89d7-3ae2f7374c58 |  | button | Suspended loads | YES,NO
button | 378bb096-5bca-50b1-b7e1-05838ae53ebf |  | button | Hazardous substances (chemicals) | YES,NO
button | 34671895-0a0e-5f6b-8421-aa0a1f787dda |  | button | Use of non-intrinsically safe equipment | YES,NO
button | 7386f823-259f-5f3a-acab-dd154f599766 |  | button | Weather extremes | YES,NO
button | 657b05ac-7c23-5d80-bcfa-3d3ca327293d |  | button | Moving vehicles | YES,NO
button | 99f80d40-6294-56f1-b46d-ca928e13777a |  | button | Task related noise | YES,NO
button | b45b0828-9f8e-53a9-9e46-096294ae2680 |  | button | Engulfment | YES,NO
button | 276a7bf2-528c-554b-a9ca-4fa7cdf6570c |  | button | General waste | YES,NO
button | 9a413d61-5793-5147-a073-a15fb6b3906b |  | button | Hazardous waste | YES,NO
button | 39558aca-8e35-562a-82ef-842d05ac2d14 |  | button | Hazardous/toxic substance, fumes, gas | YES,NO
button | 91ac9e10-5b45-5f5f-958b-db2cb0381bd2 |  | button | Flammable materials - Gas, liquids, solids | YES,NO
button | f8448d64-0e47-515b-8291-eca9ec29dae7 |  | button | Reduced visibility, lighting | YES,NO
button | c50eeb0d-643b-5f13-bf60-10952f581c98 |  | button | Electricity | YES,NO
button | b81ab024-7371-5dab-a53a-ed5076ba4dfe |  | button | Static electricity | YES,NO
button | 650d56e5-3c46-537f-b61b-bb499989e2b3 |  | button | Work at height | YES,NO
button | bb0b0921-3d82-5eaa-aec2-8a6ff5c0f2d3 |  | button | Underground services | YES,NO
button | 117b3a73-8bed-519d-aca0-3f54932b2085 |  | button | O2 Deficiency/Excess | YES,NO
button | 8021c1a5-9fe4-5da8-8389-225b3e1f3153 |  | button | Temperature extremes | YES,NO
button | ba654f9e-fe71-51eb-8c1f-f8f70742bd92 |  | button | Heavy objects | YES,NO
button | 98fd46ad-25c4-5ba4-a580-a42f4283519c |  | button | Radiation | YES,NO
button | b62f2b4a-3629-5d99-93d3-9cbd6267321f |  | button | Potential energy - Tension/Compression | YES,NO
button | e3c449c6-73a0-5b81-842a-aa9f2ae53d33 |  | button | Flying particles/Dust/Objects | YES,NO
button | 8822c500-ec7b-535e-af3a-3ae01d775b79 |  | button | Vehicle entry | YES,NO
button | f1eb4d91-e796-5b83-9914-cd6cf3617be0 |  | button | Exposure to process temperatures. | YES,NO
checkpoint-group |  |  | section | Prompts for Initial Consequences - Mark all that apply
checkpoint-no-status |  |  | checkpoint | Prompts for Initial Consequences - Mark all that apply
button | 4a3ee57e-5b51-5dea-8472-fa0a28cdeca5 |  | button | Falling/Dropped objects | YES,NO
button | 17648675-4760-5019-8fd6-41922df9f7f5 |  | button | Fall from height | YES,NO
button | 6663853e-27ea-5eec-b7da-dad774493e05 |  | button | Trip/Slip/Fall | YES,NO
button | e09a92fb-c9d4-52b4-b940-ffdff419fb7b |  | button | Gas release | YES,NO
button | 6a813336-340f-5269-8e22-57a7b555b7d6 |  | button | Pressure release | YES,NO
button | f3a27b37-ddc3-56dc-8f33-5d030aedf743 |  | button | Struck by object | YES,NO
button | cf4acf9a-ff77-5639-b8ad-1ba384158997 |  | button | Exceeding tool limits | YES,NO
button | d6553ea5-5d2c-58b4-b527-1a47a14b86d1 |  | button | Overloading people | YES,NO
button | 108b84dd-2610-582b-be21-031e246f1fee |  | button | Unplanned shutdown | YES,NO
button | 84cd74ce-5dae-5bcb-9f97-7c2bf8f7cb4e |  | button | Exposure to O2 deficiency/excess | YES,NO
button | 45e3c21c-9a4c-5f07-8efb-e601a1a54df2 |  | button | Exposure to hazardous substance | YES,NO
button | d834a25d-cb3e-54b4-be81-06f355240ef6 |  | button | Entanglement | YES,NO
button | 9a5fbc86-7714-55ab-8b59-df7e90d64745 |  | button | Flying objects | YES,NO
button | 4f5406fd-55bf-5506-b76f-f1162380e430 |  | button | Loss of control | YES,NO
button | 76e5b2ce-42cc-5a0a-8c0b-c233217c8ee3 |  | button | Loss of containment | YES,NO
button | 586c63b4-1e23-5f73-88aa-b3532cc4dd30 |  | button | Excess exposure to Emissions, dust, fumes, noise, fibres, heat | YES,NO
button | 8371dd30-f8e7-54ae-873b-cc740d391465 |  | button | Loss of structural integrity | YES,NO
button | 37c04eab-5746-53f5-8266-f6842115e317 |  | button | Equipment failure | YES,NO
button | da106719-7baf-5cee-a892-e308b6c1c5f2 |  | button | Uncontrolled ignition source | YES,NO
button | fe2a1100-a133-50e6-b098-07812473c13d |  | button | Collision | YES,NO
button | 31f4f25a-1730-51ec-8fc7-26e714f6a55f |  | button | Ignition/Fire | YES,NO
button | 0da4dc9b-ba1f-5cf8-bfcf-a2a483ceb647 |  | button | Back strain/Injury | YES,NO
button | 237ae504-6999-5f83-ad0b-b1d76d05e1b1 |  | button | Burns | YES,NO
button | 28272524-14ff-5d91-a9d5-179107a4d61c |  | button | Heat exhaustion | YES,NO
checkpoint-group |  |  | section | Initial controls - Mark all that apply.
checkpoint-no-status |  |  | checkpoint | Initial controls - Mark all that apply.
label | 3ec12a19-aef2-55e4-a529-d6552dbd2511 |  | note | People controls | YES,NO
button | d0b64235-39b6-5e56-88fd-69113232243b |  | button | Safety/Fire watch person | YES,NO
button | dcb9b935-3094-5cd6-95ac-5a09e0b05cb0 |  | button | Barriers/Flagging | YES,NO
button | 098ee376-8745-5e54-8b10-03ea8e507a31 |  | button | Warning signs | YES,NO
label | 8dd429db-8aab-5a94-b306-35fdad039cf6 |  | note | Equipment controls | YES,NO
button | 9f14da9e-44c2-5b93-af22-ba4c7851270d |  | button | Master tags and locks | YES,NO
button | e8ae5e49-0775-5e80-8b00-6e27749d4d71 |  | button | Scaffolding for access | YES,NO
button | af98a860-4987-53fc-8e38-22b892be9a6e |  | button | Radio communication | YES,NO
label | 86126f7a-4e6e-579f-9fd8-09b184dd43ef |  | note | Environmental controls | YES,NO
button | 771b7034-a475-5056-b35f-fb8045a297e5 |  | button | Ventilation | YES,NO
button | a7a970a3-45f4-5614-aa5e-08e7816ab91d |  | button | Lighting | YES,NO
button | 7803545c-d27f-521d-a0c4-ab1c778e34fb |  | button | Gas Testing | YES,NO
label | dd4b2ce4-cdfc-531e-90ea-53929df94acf |  | note | High risk controls | YES,NO
button | 4e3fc27a-9c10-5876-b521-1ed3e651733e |  | button | WSCS Work permit | YES,NO
button | 05aba4d4-a317-56ff-9227-9195dda05a86 |  | button | WSCS Certificates | YES,NO
button | afb288b5-6564-5948-b596-9ecf40abf08e |  | button | Critical lift/Fall protection plan | YES,NO
button | 14e839e5-a141-57f4-aca8-aa23cf14cb22 |  | button | Specialised PPE | YES,NO
button | da1a1a07-da5e-5e54-b511-5f9f192b93f0 |  | button | Spill kit | YES,NO
button | 5445d09d-54f8-50e1-9638-1c2b0e7f3ee7 |  | button | Fire extinguisher | YES,NO
checkpoint-group |  |  | section | Signatures
checkpoint-no-status |  |  | checkpoint | Signatures
text | c2dfa9d7-bc33-5323-9120-e295700b5715 |  | textbox | Applicant name
holdpoint |  |  | signoff | Applicant signature
checklist-sectioned |  |  | checklist | ITR-CL-1-101 Conduit, Ducting, Unistrut, Cable Tray & Ladder Installation |  |  |  |  | Yes | ITR-CL-1-101 Conduit, Ducting, Unistrut, Cable Tray & Ladder Installation | ecd2cdc3-7f02-48eb-a148-2b882ea5c9cd
checkpoint-group |  |  | section | Conduit/Ducting Installation Below Ground
checkpoint-status |  |  | checkpoint | Check equipment details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status |  |  | checkpoint | Check conduit cable enclosure installation is as-per design, layout drawings and specifications.
checkpoint-status |  |  | checkpoint | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed.
checkpoint-status |  |  | checkpoint | Confirm that there are no obstructions, and that the installation will be accessible for maintenance.
checkpoint-status |  |  | checkpoint | Check all fixings are tight and secure.
checkpoint-status |  |  | checkpoint | Check bends do not exceed the maximum cable bend radius.
checkpoint-group |  |  | section | Cable Supports Above Ground
checkpoint-status |  |  | checkpoint | Verify cable support has been installed as per relevant drawings.
checkpoint-status |  |  | checkpoint | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection.
checkpoint-status |  |  | checkpoint | All covers fitted if applicable.
checkpoint-status |  |  | checkpoint | Check cable support structures are adequately fixed and present no hazard to personnel.
checkpoint-status |  |  | checkpoint | Correct cable support size and type used.
checkpoint-status |  |  | checkpoint | Welded support brackets have been wire-brushed and painted to completion.
checkpoint-status |  |  | checkpoint | Splice plates, barriers, earthing system secure.
checkpoint-status |  |  | checkpoint | Trays / ladders, supports, brackets not interfering with other disciplines.
checkpoint-status |  |  | checkpoint | Check bends do not exceed the maximum cable bending radius.
checkpoint-status |  |  | checkpoint | Cables have adequate mechanical protection as and where required.
checkpoint-status |  |  | checkpoint | Inspect for system rigidity, and check levels to correct plane.
checkpoint-status |  |  | checkpoint | Earth bonding straps have been fitted to any sections that are split, hinged or flexible.
checkpoint-status |  |  | checkpoint | Tray bonded to structure at correct locations.
text | ce39e6ec-226c-5829-a316-f7a3c96ad8e7 |  | textbox | Earth bonding continuity tested – record result: |  |  | Ohms
checkpoint-group |  |  | section | Cable Transits
checkpoint-status |  |  | checkpoint | Transit frame installed as per drawings.
checkpoint-status |  |  | checkpoint | Transit frame identification marked correctly and visible.
checkpoint-status |  |  | checkpoint | Frame correctly packed with correct sized blocks and infills.
checkpoint-status |  |  | checkpoint | Correct stay plates fitted (non-ferrous for single core power cables.)
checkpoint-status |  |  | checkpoint | Rated insulation installed to transit (where required.)
checkpoint-status |  |  | checkpoint | Cables entering and leaving transits adequately supported and protected.
checkpoint-status |  |  | checkpoint | Cables pass through frames without strain on blocks.
checkpoint-status |  |  | checkpoint | All cables identified on both sides of transit and visible.
checkpoint-group |  |  | section | Acceptance Signatures
checkpoint-status |  |  | checkpoint | Test/Inspection carried out by:
text | e8370c42-dfc6-5898-86d1-751ce951712f |  | textbox | Test/Inspection carried out by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Test/Inspection approved by:
text | 13eb8ede-6fe2-5752-b5a7-f4d931f4403d |  | textbox | Test/Inspection approved by:
holdpoint |  |  | signoff | Signed
checkpoint-status |  |  | checkpoint | Client Representative
text | 8cea19d6-58c3-5fbb-918e-0d2d9612482c |  | textbox | Client Representative
holdpoint |  |  | signoff | Signed