## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Ex p (Detailed) - Date: |  |  |  |  | Yes | Ex p (Detailed) - Date: | 018c081f-515e-4ef0-8f89-ede32a61e536
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL /zone requirements of the location
checkpoint-status |  |  | checkpoint | Equipment group is correct
checkpoint-status |  |  | checkpoint | Equipment temperature class or surface temperature is correct
checkpoint-status |  |  | checkpoint | Equipment circuit identification is correct
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glasses and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no evident damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Lamp type, rating, and position are correct
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Type of cable is appropriate, is adequately supported , and undamaged
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | There is no evident damage or degradation that indicates that the fault loop impedance (TN systems) or earthing resistance (IT systems) is not satisfactory
checkpoint-status |  |  | checkpoint | Automatic electrical protective devices are set correctly and operate within permitted limits
checkpoint-status |  |  | checkpoint | Protective gas inlet temperature is below maximum specified
checkpoint-status |  |  | checkpoint | Ducts, pipes, and enclosures are in good condition
checkpoint-status |  |  | checkpoint | Protective gas is substantially free from contaminants
checkpoint-status |  |  | checkpoint | Protective gas pressure and/or flow is adequate
checkpoint-status |  |  | checkpoint | Pressure and/or flow indicators, alarms and interlocks function correctly
checkpoint-status |  |  | checkpoint | Conditions of spark and particle barriers of ducts for exhausting the gas in hazardous area are satisfactory
checkpoint-status |  |  | checkpoint | Specific conditions of use (if applicable) are complied with
checkpoint-group |  |  | section | Environment
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-group |  |  | section | Inspector Details
checkpoint-status |  |  | checkpoint | Inspection Complete
text | 0cd3cdaa-3b3f-5c29-b9c2-8ef3ea489a70 |  | textbox | Registration #
checklist-sectioned |  |  | checklist | Ex d (Close) - Date: |  |  |  |  | Yes | Ex d (Close) - Date: | 3204286d-f77c-4c4f-b79b-c996b3d63f2a
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL/ Zone requirements of the location
checkpoint-status |  |  | checkpoint | Equipment group is correct
checkpoint-status |  |  | checkpoint | Equipment temperature class is correct
checkpoint-status |  |  | checkpoint | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight
checkpoint-status |  |  | checkpoint | Threaded covers on enclosures are of the correct type, are tight and secured
checkpoint-status |  |  | checkpoint | Breathing and draining devices are satisfactory, and operating effectively
checkpoint-status |  |  | checkpoint | Type of cable is appropriate is adequately supported and undamaged
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | Obstructions adjacent to flameproof flanged joints are in accordance with IEC 60079-14
checkpoint-status |  |  | checkpoint | Variable voltage/frequency installation complies with documentation
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-group |  |  | section | Lighting, Motors & Heating Systems
checkpoint-status |  |  | checkpoint | Lighting
boolean | c303fc20-efcd-56f4-a502-70c4826d662c |  | tickbox | HID Lamps are not indicating EOL effects
checkpoint-status |  |  | checkpoint | Motors
boolean | 4c6d543e-5cd2-55ef-a793-33be85930990 |  | tickbox | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks
boolean | 4cce3e50-3e85-5375-b284-ebfd1b933a6f |  | tickbox | The ventilation airflow is not impeded
checkpoint-status |  |  | checkpoint | Heating Systems
boolean | 9a00380f-e9d6-5999-9c78-b3c9241bebed |  | tickbox | The setting of the safety cut off is sealed
boolean | 2a7528be-bc8b-5d50-ac4a-59d8e556d292 |  | tickbox | Reset of a heating system safety cut off possible with tool only
boolean | 401d0040-bc1a-5c03-a4bb-513a4757c679 |  | tickbox | Auto-reset is not possible
checklist-sectioned |  |  | checklist | Ex n (Visual) - Date: |  |  |  |  | Yes | Ex n (Visual) - Date: | 40d9b3a6-1366-4df5-973c-f0ecd2b2b704
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL/ Zone requirements of the location
checkpoint-status |  |  | checkpoint | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight (physical check)
checkpoint-status |  |  | checkpoint | Type of cable is appropriate is adequately supported and undamaged
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-group |  |  | section | Lighting & Motors
checkpoint-status |  |  | checkpoint | Lighting
boolean | 75f16046-6d04-5e82-9e04-984a2b63f9ee |  | tickbox | Fluorescent lamps are not indicating EOL effects
boolean | a0932105-a329-5017-affd-67d32df0eb97 |  | tickbox | HID Lamps are not indicating EOL effects
checkpoint-status |  |  | checkpoint | Motors
boolean | 86cc6809-2c35-51b9-a010-c8d41d1afd3e |  | tickbox | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks
boolean | 5ba8969b-c90a-5c1c-a99c-7c1bebb18ffb |  | tickbox | The ventilation airflow is not impeded
checklist-sectioned |  |  | checklist | Ex n (Detailed) - Date: |  |  |  |  | Yes | Ex n (Detailed) - Date: | 4384c4ea-8568-4794-bc93-0cfb0607dcb0
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL/ Zone requirements of the location
checkpoint-status |  |  | checkpoint | Equipment group is correct
checkpoint-status |  |  | checkpoint | Equipment temperature class is correct
checkpoint-status |  |  | checkpoint | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity
checkpoint-status |  |  | checkpoint | Equipment circuit identification is correct
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight (physical check)
checkpoint-status |  |  | checkpoint | Condition of enclosure gaskets is satisfactory
checkpoint-status |  |  | checkpoint | There is no evidence of ingress of water or dust in the enclosure in accordance with the IP rating
checkpoint-status |  |  | checkpoint | Electrical connections and unused terminals are tight
checkpoint-status |  |  | checkpoint | Enclosed break, Hermetically sealed, Encapsulated and/or flameproof components are undamaged
checkpoint-status |  |  | checkpoint | Restricted breathing enclosure is satisfactory and test port, if fitted, is functional (Type nR only)
checkpoint-status |  |  | checkpoint | Test port, if fitted, is functional - (type "nR"only)
checkpoint-status |  |  | checkpoint | Breathing operation is satisfactory (Type nR only)
checkpoint-status |  |  | checkpoint | Breathing and draining devices are satisfactory, and operating effectively
checkpoint-status |  |  | checkpoint | Type of cable is appropriate is adequately supported and undamaged
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-status |  |  | checkpoint | Integrity of conduit system and interface with mixed system maintained
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | There is no evident damage or degradation that indicates that the fault loop impedance (TN system) or earthing resistance (IT system) is not satisfactory
checkpoint-status |  |  | checkpoint | Automatic electrical protective devices are set correctly (auto reset not possible) and operate within permitted limits
checkpoint-status |  |  | checkpoint | Specific conditions of use (if applicable) are complied with
checkpoint-status |  |  | checkpoint | Cables not in use are correctly terminated
checkpoint-status |  |  | checkpoint | Variable voltage/frequency installation complies with documentation
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-status |  |  | checkpoint | All equipment housings are clean and dry
checkpoint-group |  |  | section | Lighting & Motors
checkpoint-status |  |  | checkpoint | Lighting
boolean | 15a8065c-ccaf-5414-a5aa-5bae7e854ce9 |  | tickbox | Fluorescent lamps are not indicating EOL effects
boolean | ca3e5aa8-fd84-5339-b829-5ef1442cd97d |  | tickbox | HID Lamps are not indicating EOL effects
boolean | 1cf01e0c-f909-5085-ae74-0d1260d719e2 |  | tickbox | Lamp type, rating, pin configuration and position are correct
checkpoint-status |  |  | checkpoint | Motors
boolean | 5d892c86-29e3-5ffd-bbae-3f0739334b3f |  | tickbox | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks
boolean | e62a29e9-eb86-51cd-ae5b-734a2e3eedeb |  | tickbox | The ventilation airflow is not impeded
boolean | 7667b5db-370d-560c-ba21-dce742284d24 |  | tickbox | Insulation resistance (IR) of the motor windings is satisfactory
checkpoint-group |  |  | section | Inspector Details
checkpoint-status |  |  | checkpoint | Inspection Complete
text | b94649cf-c17d-5121-81da-837aee92b7b8 |  | textbox | Registration #
checklist-sectioned |  |  | checklist | Ex i (Close) - Date: |  |  |  |  | Yes | Ex i (Close) - Date: | 460d9bf3-b138-48df-a3d4-53b8c3c42310
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Circuit and/or equipment documentation is appropriate to the EPL/ Zone
checkpoint-status |  |  | checkpoint | Equipment installed is that specified in the documentation
checkpoint-status |  |  | checkpoint | Circuit and/or equipment category and group correct
checkpoint-status |  |  | checkpoint | Equipment temperature class is correct
checkpoint-status |  |  | checkpoint | Ambient temperature range of the apparatus is correct for the installation
checkpoint-status |  |  | checkpoint | Service temperature range of the apparatus is correct for the installation
checkpoint-status |  |  | checkpoint | Installation is clearly labelled
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and/or compounds are satisfactory
checkpoint-status |  |  | checkpoint | Cable glands and blanking elements are the correct type, complete and tight
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Diode safety barriers, galvanic isolators, relays and other energy limiting devices are of the approved type, installed in accordance with the certification requirements and securely earthed where required
checkpoint-status |  |  | checkpoint | Printed circuit boards are clean and undamaged
checkpoint-status |  |  | checkpoint | The maximum voltage Um of the associated apparatus is not exceeded
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | The cables are adequately supported and there is no obvious damage to cables
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-group |  |  | section | Environment
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checklist-flat |  |  | checklist | Record of Inspection |  |  |  |  | Yes | Record of Inspection | 4db2002e-2d07-4d4b-99cf-f6a4b9ccf724
checkpoint-status |  |  | checkpoint | Please upload record of inspection here when complete
checklist-flat |  |  | checklist | Item Details |  |  |  |  | Yes | Item Details | 50e5fde0-69ec-44ef-8462-c5c36e17b122
checkpoint-status |  |  | checkpoint | Details complete (input/uploaded/scanned)
text | c9aa6bc0-bc23-58f9-91ca-3429a1960f05 |  | textbox | Tag #
text | d1c4ee1b-804b-5385-a086-607dbf892a6c |  | textbox | Manufacturer
text | ae53d460-1bad-50e6-9879-1bd6d38976ab |  | textbox | Model
text | 1dd4c60d-d380-5bf8-a351-6732b92b4ebe |  | textbox | Serial #
text | 82445369-6ca8-594c-a97d-8e131d1c74ac |  | textbox | Device Type
text | 9558f0b4-a66c-5a30-ab8e-53c95feaf06e |  | textbox | Location
text | 791adcf2-be11-51c8-a10b-bb781254f616 |  | textbox | Location details (Zone, Gas Group, Temp Class)
text | d9ebb509-5a68-5fe8-ac40-83e275552423 |  | textbox | Access Req
text | c1729adf-fd5f-59fc-9def-6f931c82e9e7 |  | textbox | Protection type (nameplate)
text | 9fbb55ef-cc12-5446-9cb6-679ae0c3512b |  | textbox | Protection type (installed as)
text | 37cf6762-7177-57e9-b382-b14d0be48c85 |  | textbox | Equipment Group
text | e2fc4cb5-ed22-5f82-a02e-5cb8f476cdd3 |  | textbox | Temperature class
text | cb27d688-6e89-5afd-9302-a74f4dbbe793 |  | textbox | IP rating
text | 3fec6826-1871-50a8-a581-fcdc6276d4b8 |  | textbox | Cable #
checkpoint-status |  |  | checkpoint | Cause & Effects
checkpoint-status |  |  | checkpoint | Cert #
checkpoint-status |  |  | checkpoint | Loop Drwg
checkpoint-status |  |  | checkpoint | P&ID Drwg
checkpoint-status |  |  | checkpoint | HAC Drwg
checklist-flat |  |  | checklist | Accessory: |  |  |  |  | Yes | Accessory: | 6b41c588-f32c-4628-a3a3-b7057fabc901
checkpoint-status |  |  | checkpoint | Accessory information complete
select | 8293c15a-e627-50c7-a59d-784a093fbf2e |  | dropdown | Type | Glands, Stopping Plug, Adaptor, Breather, Terminal, Associated Equipment
text | f8cf9e89-d874-5f92-9d22-7af6925ebdc7 |  | textbox | Quantity
text | a5deb09f-13ff-57a2-9930-59e1e0f9e480 |  | textbox | Make
text | a8973a7b-4ce1-5228-a04d-5b808dafe7ee |  | textbox | Model
text | 6151f4f9-4e83-5d89-9956-ea5f379ecbb8 |  | textbox | Protection type
text | b27a4a45-53a8-5fcd-8ee0-d4db863734df |  | textbox | Certificate
checklist-sectioned |  |  | checklist | Ex n (Close) - Date: |  |  |  |  | Yes | Ex n (Close) - Date: | 6fb34923-0f62-49cd-88f2-102c769cf4b1
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL/ Zone requirements of the location
checkpoint-status |  |  | checkpoint | Equipment group is correct
checkpoint-status |  |  | checkpoint | Equipment temperature class is correct
checkpoint-status |  |  | checkpoint | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight (physical check)
checkpoint-status |  |  | checkpoint | Restricted breathing enclosure is satisfactory and test port, if fitted, is functional (Type nR only)
checkpoint-status |  |  | checkpoint | Breathing and draining devices are satisfactory, and operating effectively
checkpoint-status |  |  | checkpoint | Type of cable is appropriate is adequately supported and undamaged
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | Variable voltage/frequency installation complies with documentation
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-group |  |  | section | Lighting & Motors
checkpoint-status |  |  | checkpoint | Lighting
boolean | 994646d6-36d7-59e2-9d3b-196a71cb8d87 |  | tickbox | Fluorescent lamps are not indicating EOL effects
boolean | a64f53b1-b9c7-54fb-9342-38fa6032e0b8 |  | tickbox | HID Lamps are not indicating EOL effects
checkpoint-status |  |  | checkpoint | Motors
boolean | cfa8b225-bf0b-5bc9-a3ff-81fc7eedebea |  | tickbox | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks
boolean | 8a155e9a-d073-52a6-8c85-d4058949bbd0 |  | tickbox | The ventilation airflow is not impeded
checklist-sectioned |  |  | checklist | Ex e (Visual) - Date: |  |  |  |  | Yes | Ex e (Visual) - Date: | 96ff1f0b-d092-4b4e-a1fe-ef19fbfa1cee
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL/ Zone requirements of the location
checkpoint-status |  |  | checkpoint | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity
checkpoint-status |  |  | checkpoint | Equipment circuit identification is correct
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight (physical check)
checkpoint-status |  |  | checkpoint | Type of cable is appropriate is adequately supported and undamaged
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-group |  |  | section | Lighting & Motors
checkpoint-status |  |  | checkpoint | Lighting
boolean | 45b403b0-ab95-5ff3-8f27-2be7a6101d88 |  | tickbox | Fluorescent lamps are not indicating EOL effects
boolean | c30be8a0-2ea7-585d-8433-bcd557330648 |  | tickbox | HID Lamps are not indicating EOL effects
checkpoint-status |  |  | checkpoint | Motors
boolean | 63375b82-d40b-5520-bad0-6e39867baf0f |  | tickbox | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks
boolean | 060826d5-198e-5f5f-abcb-96180536d444 |  | tickbox | The ventilation airflow is not impeded
checklist-sectioned |  |  | checklist | Ex e (Detailed) - Date: |  |  |  |  | Yes | Ex e (Detailed) - Date: | a33e663f-d44a-4295-ba3f-74ba45b2a3a8
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL/ Zone requirements of the location
checkpoint-status |  |  | checkpoint | Equipment group is correct
checkpoint-status |  |  | checkpoint | Equipment temperature class is correct
checkpoint-status |  |  | checkpoint | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity
checkpoint-status |  |  | checkpoint | Equipment circuit identification is correct
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight (physical check)
checkpoint-status |  |  | checkpoint | Condition of enclosure gaskets is satisfactory
checkpoint-status |  |  | checkpoint | There is no evidence of ingress of water or dust in the enclosure in accordance with the IP rating
checkpoint-status |  |  | checkpoint | Electrical connections and unused terminals are tight
checkpoint-status |  |  | checkpoint | Encapsulated and/or flameproof components are undamaged
checkpoint-status |  |  | checkpoint | Breathing and draining devices are satisfactory, and operating effectively
checkpoint-status |  |  | checkpoint | Type of cable is appropriate is adequately supported and undamaged
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-status |  |  | checkpoint | Integrity of conduit system and interface with mixed system maintained
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | There is no evident damage or degradation that indicates that the fault loop impedance (TN system) or earthing resistance (IT system) is not satisfactory
checkpoint-status |  |  | checkpoint | There is no evident damage or degradation that indicates the insulation resistance is not satisfactory.
checkpoint-status |  |  | checkpoint | Automatic electrical protective devices are set correctly (auto reset not possible) and operate within permitted limits
checkpoint-status |  |  | checkpoint | Specific conditions of use (if applicable) are complied with
checkpoint-status |  |  | checkpoint | Cables not in use are correctly terminated
checkpoint-status |  |  | checkpoint | Variable voltage/frequency installation complies with documentation
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-status |  |  | checkpoint | All equipment housings are clean and dry
checkpoint-group |  |  | section | Lighting, Motors & Heating Systems
checkpoint-status |  |  | checkpoint | Lighting
boolean | a19388e6-0b9d-5e2d-8d52-038aaf85bd67 |  | tickbox | Fluorescent lamps are not indicating EOL effects
boolean | e8a10e15-3219-573d-a483-6b80cfb6851d |  | tickbox | HID Lamps are not indicating EOL effects
boolean | 64385237-8fe5-53cc-9233-33186c1b209f |  | tickbox | Lamp type, rating, pin configuration and position are correct
checkpoint-status |  |  | checkpoint | Motors
boolean | 00535778-e835-5837-8c4f-72ae1644ba52 |  | tickbox | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks
boolean | 78c71988-3c6b-5aca-9d59-46d9f653b747 |  | tickbox | The ventilation airflow is not impeded
boolean | 72a9d115-2ae2-530b-987f-816eaf8bab39 |  | tickbox | Insulation resistance (IR) of the motor windings is satisfactory
boolean | f7800bf8-b377-579c-8a52-865e84b6a6b5 |  | tickbox | Motor protection devices operate within the permitted Te or Ta time limits
checkpoint-status |  |  | checkpoint | Heating Systems
boolean | 4f3ca202-00a9-59a2-b8f6-981d61560e82 |  | tickbox | Temperature sensors function according to manufacturer's documents
boolean | 5bf396bd-9ba4-5a43-94ce-1b0c1c13203a |  | tickbox | Safety cut off devices function according to manufacturer's documents
boolean | 16cc2206-bba0-555d-bdb6-542548f4007f |  | tickbox | The setting of the safety cut off is sealed
boolean | 137bc3a8-5aff-5fcf-bbb4-734046a6deb4 |  | tickbox | Reset of a heating system safety cut off possible with tool only
boolean | 28e870d1-b132-5c67-9a9d-7789478c0203 |  | tickbox | Auto-reset is not possible
boolean | 5f04ea99-94b3-533b-8481-9027a6eaa4a4 |  | tickbox | Reset of a safety cut off under under fault conditions is prevented
boolean | 0366391e-a5b5-50d4-8ea1-262c91c781fc |  | tickbox | Safety cut off independent from control system
boolean | 04e5f213-3d5b-592c-9cdd-d5089a415c63 |  | tickbox | Level/Flow switch is installed and correctly set if required
checkpoint-group |  |  | section | Inspector Details
checkpoint-status |  |  | checkpoint | Inspection Complete
text | 63491ee5-40dd-5d38-aabe-d8dd611a2c11 |  | textbox | Registration #
checklist-sectioned |  |  | checklist | Ex p (Close) - Date: |  |  |  |  | Yes | Ex p (Close) - Date: | a36982af-1cad-487e-b26c-289af4cf72a1
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL /zone requirements of the location
checkpoint-status |  |  | checkpoint | Equipment group is correct
checkpoint-status |  |  | checkpoint | Equipment temperature class or surface temperature is correct
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glasses and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no evident damage or unauthorised modifications
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Type of cable is appropriate, is adequately supported , and undamaged
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | Ducts, pipes, and enclosures are in good condition
checkpoint-status |  |  | checkpoint | Protective gas is substantially free from contaminants
checkpoint-status |  |  | checkpoint | Protective gas pressure and/or flow is adequate
checkpoint-group |  |  | section | Environment
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checklist-sectioned |  |  | checklist | Ex e (Close) - Date: |  |  |  |  | Yes | Ex e (Close) - Date: | a478fcd5-72fc-4fd7-8913-fb297436df36
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL/ Zone requirements of the location
checkpoint-status |  |  | checkpoint | Equipment group is correct
checkpoint-status |  |  | checkpoint | Equipment temperature class is correct
checkpoint-status |  |  | checkpoint | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight (physical check)
checkpoint-status |  |  | checkpoint | Breathing and draining devices are satisfactory, and operating effectively
checkpoint-status |  |  | checkpoint | Type of cable is appropriate is adequately supported and undamaged
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | Variable voltage/frequency installation complies with documentation
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-group |  |  | section | Lighting, Motors & Heating Systems
checkpoint-status |  |  | checkpoint | Lighting
boolean | d73a50eb-267e-5b64-b949-52f1709acf83 |  | tickbox | Fluorescent lamps are not indicating EOL effects
boolean | 33f8454f-c323-5beb-b516-838f211f4b91 |  | tickbox | HID Lamps are not indicating EOL effects
checkpoint-status |  |  | checkpoint | Motors
boolean | 6fbd8af7-eee8-5233-89e2-f411bfd786fd |  | tickbox | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks
boolean | ea3f5993-67f5-5331-ac1b-d97d41852b45 |  | tickbox | The ventilation airflow is not impeded
checkpoint-status |  |  | checkpoint | Heating Systems
boolean | af2d10b6-bc39-590d-8b8c-d33701228f17 |  | tickbox | The setting of the safety cut off is sealed
boolean | bfc24370-842f-5cc6-a84a-65bada791bc0 |  | tickbox | Reset of a heating system safety cut off possible with tool only
boolean | 455a9798-d3a8-5ccd-8c5a-553d20557293 |  | tickbox | Auto-reset is not possible
checklist-sectioned |  |  | checklist | Ex d (Detailed) - Date: |  |  |  |  | Yes | Ex d (Detailed) - Date: | b599c669-1b83-4c98-a771-ef5283d8cbeb
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL/ Zone requirements of the location
checkpoint-status |  |  | checkpoint | Equipment group is correct
checkpoint-status |  |  | checkpoint | Equipment temperature class is correct
checkpoint-status |  |  | checkpoint | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity
checkpoint-status |  |  | checkpoint | Equipment circuit identification is correct
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight
checkpoint-status |  |  | checkpoint | Threaded covers on enclosures are of the correct type, are tight and secured
checkpoint-status |  |  | checkpoint | Joint surfaces are clean and undamaged and gaskets, if any, are satisfactory and positioned correctly
checkpoint-status |  |  | checkpoint | There is no evidence of ingress of water or dust in the enclosure in accordance with the IP rating
checkpoint-status |  |  | checkpoint | Dimensions of flanged joint gaps are within the limits permitted by manufacturer's documentation or relevant construction standard at time of installation
checkpoint-status |  |  | checkpoint | Breathing and draining devices are satisfactory, and operating effectively
checkpoint-status |  |  | checkpoint | Type of cable is appropriate is adequately supported and undamaged
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-status |  |  | checkpoint | Stopping boxes and cable boxes are correctly filled
checkpoint-status |  |  | checkpoint | Integrity of conduit system and interface with mixed system maintained
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | There is no evident damage or degradation that indicates that the fault loop impedance (TN system) or earthing resistance (IT system) is not satisfactory
checkpoint-status |  |  | checkpoint | There is no evident damage or degradation that indicates that the insulation resistance is not satisfactory.
checkpoint-status |  |  | checkpoint | Automatic electrical protective devices are set correctly (auto reset not possible) and operate within permitted limits
checkpoint-status |  |  | checkpoint | Specific conditions of use (if applicable) are complied with
checkpoint-status |  |  | checkpoint | Cables not in use are correctly terminated
checkpoint-status |  |  | checkpoint | Obstructions adjacent to flameproof flanged joints are in accordance with IEC 60079-14
checkpoint-status |  |  | checkpoint | Variable voltage/frequency installation complies with documentation
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-group |  |  | section | Lighting, Motors & Heating Systems
checkpoint-status |  |  | checkpoint | Lighting
boolean | c520352a-34fa-5c82-931d-d560adc8f770 |  | tickbox | HID Lamps are not indicating EOL effects
boolean | df1d8b3b-771c-51b9-b717-b3d25f5dc06e |  | tickbox | Lamp type, rating, pin configuration and position are correct
checkpoint-status |  |  | checkpoint | Motors
boolean | 16dbdfaf-7da4-59e6-a2e1-49a1022e6ce2 |  | tickbox | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks
boolean | 01ea2322-b728-5bbd-86f0-c47ad593a45b |  | tickbox | The ventilation airflow is not impeded
boolean | bdb008b5-f99c-5be3-8914-2af1ff7f7975 |  | tickbox | Insulation resistance (IR) of the motor windings is satisfactory
checkpoint-status |  |  | checkpoint | Heating Systems
boolean | 19d1711e-db8e-50d8-9a7e-a206254d374c |  | tickbox | Temperature sensors function according to manufacturer's documents
boolean | ef920177-6b25-5f07-9f4b-f592c099bfff |  | tickbox | Safety cut off devices function according to manufacturer's documents
boolean | dd9b93a9-251d-5dad-a997-ca4c458818aa |  | tickbox | The setting of the safety cut off is sealed
boolean | 5064ad16-0d44-5b95-ae90-552cbe8a31ae |  | tickbox | Reset of a heating system safety cut off possible with tool only
boolean | 82e55de7-771c-54f3-9286-88766c0d29a3 |  | tickbox | Auto-reset is not possible
boolean | 1f0771df-da8f-5f92-b5c8-c33840c0fdca |  | tickbox | Reset of a safety cut off under under fault conditions is prevented
boolean | 9fe0539d-f2d4-5f9a-96ca-4915fb5e5ba1 |  | tickbox | Safety cut off independent from control system
boolean | 0e753935-c5d5-5213-b715-c18ab1171c88 |  | tickbox | Level/Flow switch is installed and correctly set if required
checkpoint-group |  |  | section | Inspector Details
checkpoint-status |  |  | checkpoint | Inspection Complete
text | 4f0a4e3f-4e99-5b18-8b3d-59e48e2dcb6a |  | textbox | Registration #
checklist-sectioned |  |  | checklist | Ex d (Visual) - Date: |  |  |  |  | Yes | Ex d (Visual) - Date: | c3557587-aeac-489c-bc8f-941040ba8a03
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL/ Zone requirements of the location
checkpoint-status |  |  | checkpoint | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight
checkpoint-status |  |  | checkpoint | Threaded covers on enclosures are of the correct type, are tight and secured
checkpoint-status |  |  | checkpoint | Type of cable is appropriate is adequately supported and undamaged
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | Obstructions adjacent to flameproof flanged joints are in accordance with IEC 60079-14
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-group |  |  | section | Lighting & Motors
checkpoint-status |  |  | checkpoint | Lighting
boolean | 6b187dc1-545b-524a-9291-2e5980208efd |  | tickbox | HID Lamps are not indicating EOL effects
checkpoint-status |  |  | checkpoint | Motors
boolean | ce6a57f3-ecb8-5889-90fd-ec1b545ac13f |  | tickbox | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks
boolean | 80b4f0ef-1191-5603-9a04-9720b0824241 |  | tickbox | The ventilation airflow is not impeded
checklist-sectioned |  |  | checklist | Ex i (Detailed) - Date: |  |  |  |  | Yes | Ex i (Detailed) - Date: | cf1c41b6-88c5-4d59-9e69-d5fc473cc6fa
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Circuit and/or equipment documentation is appropriate to the EPL/ Zone
checkpoint-status |  |  | checkpoint | Equipment installed is that specified in the documentation
checkpoint-status |  |  | checkpoint | Circuit and/or equipment category and group correct
checkpoint-status |  |  | checkpoint | Equipment temperature class is correct
checkpoint-status |  |  | checkpoint | Ambient temperature range of the apparatus is correct for the installation
checkpoint-status |  |  | checkpoint | Service temperature range of the apparatus is correct for the installation
checkpoint-status |  |  | checkpoint | Installation is clearly labelled
checkpoint-status |  |  | checkpoint | Enclosure, glass parts, and glass to metal sealing gaskets and/or compounds are satisfactory
checkpoint-status |  |  | checkpoint | Cable glands and blanking elements are the correct type, complete and tight
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Diode safety barriers, galvanic isolators, relays and other energy limiting devices are of the approved type, installed in accordance with the certification requirements and securely earthed where required
checkpoint-status |  |  | checkpoint | Condition of enclosure gaskets is satisfactory
checkpoint-status |  |  | checkpoint | Electrical connections are tight
checkpoint-status |  |  | checkpoint | Printed circuit boards are clean and undamaged
checkpoint-status |  |  | checkpoint | The maximum voltage Um of the associated apparatus is not exceeded
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Cables are installed in accordance with the documentation
checkpoint-status |  |  | checkpoint | Cable screens are earthed in accordance with the documentation
checkpoint-status |  |  | checkpoint | The cables are adequately supported and there is no obvious damage to cables
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-status |  |  | checkpoint | Point to point connections are all correct (Initial Inspection Only)
checkpoint-status |  |  | checkpoint | Earth continuity is satisfactory for non galvanically isolated circuits
checkpoint-status |  |  | checkpoint | Earth connections maintain the the integrity of the type of protection
checkpoint-status |  |  | checkpoint | There is no evident damage or degradation that indicates that the intrinsically safe earthing is not satisfactory
checkpoint-status |  |  | checkpoint | Insulation resistance is satisfactory
checkpoint-status |  |  | checkpoint | Separation is maintained between intrinsically safe and non intrinsically safe circuits in common distribution boxes or relay cubicles
checkpoint-status |  |  | checkpoint | Short circuit protection of the power supply is in accordance with the documentation
checkpoint-status |  |  | checkpoint | Specific conditions of use (if applicable) are complied with
checkpoint-status |  |  | checkpoint | Cables not in use are correctly terminated
checkpoint-group |  |  | section | Environment
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checkpoint-group |  |  | section | Inspector Details
checkpoint-status |  |  | checkpoint | Inspection Complete
text | 8149c5f7-53de-51ca-9991-cdbd4205cc49 |  | textbox | Registration #
checklist-sectioned |  |  | checklist | Ex i (Visual) - Date: |  |  |  |  | Yes | Ex i (Visual) - Date: | d76751b7-78fa-422c-9a45-a6201d10fa3e
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Circuit and/or equipment documentation is appropriate to the EPL/ Zone
checkpoint-status |  |  | checkpoint | Cable glands and blanking elements are the correct type, complete and tight
checkpoint-status |  |  | checkpoint | There is no damage or unauthorised modifications
checkpoint-status |  |  | checkpoint | Diode safety barriers, galvanic isolators, relays and other energy limiting devices are of the approved type, installed in accordance with the certification requirements and securely earthed where required
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | The cables are adequately supported and there is no obvious damage to cables
checkpoint-status |  |  | checkpoint | Sealing of trunking, ducts, pipes and/or conduits is satisfactory
checkpoint-group |  |  | section | Environment
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt
checklist-sectioned |  |  | checklist | Ex p (Visual) - Date: |  |  |  |  | Yes | Ex p (Visual) - Date: | e47e35f4-6277-404e-a883-494da8846ffb
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Equipment is appropriate to the EPL /zone requirements of the location
checkpoint-status |  |  | checkpoint | Equipment circuit identification is available
checkpoint-status |  |  | checkpoint | Enclosure, glasses and glass to metal sealing gaskets and or compounds are satisfactory
checkpoint-status |  |  | checkpoint | There is no evident damage or unauthorised modifications
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Type of cable is appropriate, is adequately supported , and undamaged
checkpoint-status |  |  | checkpoint | Earthing connections, including any supplementary earthing bonding connections are satisfactory
checkpoint-status |  |  | checkpoint | Ducts, pipes, and enclosures are in good condition
checkpoint-status |  |  | checkpoint | Protective gas is substantially free from contaminants
checkpoint-status |  |  | checkpoint | Protective gas pressure and/or flow is adequate
checkpoint-group |  |  | section | Environment
checkpoint-status |  |  | checkpoint | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors
checkpoint-status |  |  | checkpoint | No undue accumulation of dust and dirt