## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-sectioned | ITR-CL-1-118 Instrument Pressure/Leak Test |  |  |  |  | Yes | ITR-CL-1-118 Instrument Pressure/Leak Test | 0a505eac-9036-4ef6-9fc4-b1fe1de9b477
checkpoint-group | Checklist items
checkpoint-status | Tube identification correct
checkpoint-status | Check mechanical damage
checkpoint-status | Flow direction and instrument orientation correct
checkpoint-status | Tubing installed correctly
checkpoint-status | Tubing size
checkpoint-group | Testing
checkpoint-no-status | Testing
label | Verify test pressure and medium is correct per project and manufacture specification prior to test
select | Test fluid: | Air, N2, Water, Hydro-oil, Other
text | Test pressure:
text | Max design pressure:
select | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
text | Duration: |  |  | Minutes
checkpoint-status | Confirm all impulse lines have been drained and cleaned
checkpoint-status | Confirm any temporary test connections, valve etc. are rated for the intended test.
checkpoint-status | Confirm pneumatic, test gas and aspirator lines have been blown clear.
checkpoint-status | Check hydraulic lines flushed to project specification.
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-105 Control Panel |  |  |  |  | Yes | ITR-CL-1-105 Control Panel | 1347300a-6c9e-4864-b64d-0892f0d5d037
checkpoint-group | Control Panel
checkpoint-status | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status | Check holding down/mounting arrangement is correct.
checkpoint-status | Check for mechanical damage.
checkpoint-status | Check that panel is correctly earthed.
text | Check earth continuity between panel and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status | Check tightness of circuit connections.
checkpoint-status | All internal cabling and wiring is correctly numbered, colour coded and terminated
checkpoint-status | Ammeter scale and current transformer correct.
checkpoint-status | Check internals for cleanliness.
checkpoint-status | Check manual operation of selector switches, MCB, push buttons, etc.
checkpoint-status | Incoming cables correctly glanded, terminated and labelled.
checkpoint-status | Unused holes are sealed.
checkpoint-status | Heaters correctly installed.
text | Heater circuit Insulation Resistance: |  |  | MegaOhm
checkpoint-status | Fuse rating correct.
checkpoint-status | Padlocking facilities correct (if applicable).
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-106 Junction Box |  |  |  |  | Yes | ITR-CL-1-106 Junction Box | 188126b5-391d-4d4d-9ea1-7c6d9ee76ca8
checkpoint-group | Junction Box
checkpoint-status | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status | Check holding down/mounting arrangement and accessibility for maintenance.
checkpoint-status | Check for mechanical damage
checkpoint-status | Check that Junction box is correctly earthed.
text | Test and confirm the earth resistance between junction box and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status | Check all internal cabling and wiring is correct and tight, including segregation (e.g. IS to NON IS circuits).
checkpoint-status | Check cables for Voltage segregation. Ensure clearance, labelling, colour coding is to standard
checkpoint-status | Incoming/Outgoing cables are glanded and terminated correctly
checkpoint-status | Spare entries plugged correctly.
checkpoint-status | Check internals for cleanliness
checkpoint-status | All cover bolts and gasket undamaged
checkpoint-status | Verify ingress protection is suitable for area (IP rating)
text | IP Rating:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-101 Conduit, Ducting, Unistrut, Cable Tray & Ladder Installation |  |  |  |  | Yes | ITR-CL-1-101 Conduit, Ducting, Unistrut, Cable Tray & Ladder Installation | 1905b8c0-2106-4fe2-9c2b-f5c3e27ab6b5
checkpoint-group | Conduit/Ducting Installation Below Ground
checkpoint-status | Check equipment details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status | Check conduit cable enclosure installation is as-per design, layout drawings and specifications.
checkpoint-status | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed.
checkpoint-status | Confirm that there are no obstructions, and that the installation will be accessible for maintenance.
checkpoint-status | Check all fixings are tight and secure.
checkpoint-status | Check bends do not exceed the maximum cable bend radius.
checkpoint-group | Cable Supports Above Ground
checkpoint-status | Verify cable support has been installed as per relevant drawings.
checkpoint-status | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection.
checkpoint-status | All covers fitted if applicable.
checkpoint-status | Check cable support structures are adequately fixed and present no hazard to personnel.
checkpoint-status | Correct cable support size and type used.
checkpoint-status | Welded support brackets have been wire-brushed and painted to completion.
checkpoint-status | Splice plates, barriers, earthing system secure.
checkpoint-status | Trays / ladders, supports, brackets not interfering with other disciplines.
checkpoint-status | Check bends do not exceed the maximum cable bending radius.
checkpoint-status | Cables have adequate mechanical protection as and where required.
checkpoint-status | Inspect for system rigidity, and check levels to correct plane.
checkpoint-status | Earth bonding straps have been fitted to any sections that are split, hinged or flexible.
checkpoint-status | Tray bonded to structure at correct locations.
text | Earth bonding continuity tested – record result: |  |  | Ohms
checkpoint-group | Cable Transits
checkpoint-status | Transit frame installed as per drawings.
checkpoint-status | Transit frame identification marked correctly and visible.
checkpoint-status | Frame correctly packed with correct sized blocks and infills.
checkpoint-status | Correct stay plates fitted (non-ferrous for single core power cables.)
checkpoint-status | Rated insulation installed to transit (where required.)
checkpoint-status | Cables entering and leaving transits adequately supported and protected.
checkpoint-status | Cables pass through frames without strain on blocks.
checkpoint-status | All cables identified on both sides of transit and visible.
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation) |  |  |  |  | Yes | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation) | 3175b8a8-f8b3-45cc-b424-a062a5cb0a16
checkpoint-group | Equipment
checkpoint-status | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No.
checkpoint-status | Equipment checked for additional items as applicable
checkpoint-group | Valve
checkpoint-no-status | Valve
text | Size:
text | Flange type:
checkpoint-status | Material certification correct
checkpoint-status | Trim material correct
text | Rating:
text | Service:
checkpoint-status | Body material correct
text | Leakage class:
checkpoint-group | Actuator
checkpoint-no-status | Actuator
text | Input range: |  |  | kPa
checkpoint-status | Failure action
checkpoint-status | Hand wheel operation correct
checkpoint-group | Positioner
checkpoint-no-status | Positioner
text | Signal range
text | Output range
checkpoint-group | I/P Converter
checkpoint-no-status | I/P Converter
text | Signal range
text | Output range
checkpoint-group | Filter/Regulator/On-Off Valve
checkpoint-no-status | Filter/Regulator/On-Off Valve
text | Range |  |  | kPa
text | Pressure setting |  |  | kPa
checkpoint-status | Stroke Time
text | Open |  |  | sec
text | Close |  |  | sec
checkpoint-status | Open/Close times conform to commissioning specifications
checkpoint-group | Fail Action
checkpoint-no-status | Fail Action
select | Electrical Fail Action | FO, FC, FL
select | Motive Force | FO, FC, FL
checkpoint-group | Valve Field Calibration and Hysteresis Check
checkpoint-status | Confirm test equipment is within calibration period prior to testing
label | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
label | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100%
checkpoint-group | Proximity Detectors
checkpoint-status | Open switch set
checkpoint-status | Open switch mode setting correct
checkpoint-status | Closed switch set
checkpoint-status | Closed switch mode setting correct
checkpoint-status | Electrical connections correct
checkpoint-status | Electrical certification correct
checkpoint-group | Solenoid Valve
checkpoint-status | Operation correct
checkpoint-status | Electrical connections correct
checkpoint-status | Electrical certification correct
text | Voltage: |  |  | V
checkpoint-status | Pneumatic connections correct
text | Pneumatic pressure |  |  | kPa
checkpoint-group | Pilot Valve
checkpoint-status | Pneumatic connections correct
checkpoint-status | Operation correct
checkpoint-status | Action/Lockup
checkpoint-group | Hydraulic Actuator
checkpoint-no-status | Hydraulic Actuator
text | Working pressure
text | Manifold pressure
text | Fluid type
checkpoint-status | Hydraulic connections correct
text | Regulator pressure setting
checkpoint-status | Pilot operation correct
checkpoint-group | Accumulator
checkpoint-status | N2 Charge required
text | N2 Pre-charge pressure
text | Pressure switch setting
text | Working pressure
text | Output range
checkpoint-status | Volume tank & check valve installed correctly
checkpoint-group | Electric Actuator
checkpoint-no-status | Electric Actuator
text | Voltage:
text | Electrical certification correct
text | Electrical connections correct
text | Remote operation correct
text | Local hand operation correct
text | Torque switches and travel stops set
checkpoint-group | Miscellaneous Equipment
checkpoint-no-status | Miscellaneous Equipment
text | Description
text | Manufacturer
text | Model No:
text | Serial No:
text | Range:
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-113 Motor Control |  |  |  |  | Yes | ITR-CL-1-113 Motor Control | 3635b871-0f91-463d-add9-0c0253b49535
checkpoint-group | General Motor Control
checkpoint-status | Check all labelling and warning signs are correctly installed and visible
checkpoint-status | Check control equipment is clean and free from dust, debris and tools
checkpoint-status | Check preservation and transit items are removed
checkpoint-status | Check there are no mechanical damage and no damage to paintwork
checkpoint-status | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor
checkpoint-status | Check all cabling to control gear and motor is undamaged, supported and tidy
checkpoint-status | Check earthing bar and connections are correct and tight
checkpoint-status | Check incoming and outgoing power cables are terminated and glanded correctly
checkpoint-status | Check phase identification on power cables is correct and visible
checkpoint-status | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque
checkpoint-status | Check all other nuts and bolts are tight
checkpoint-status | Check spare gland entries are plugged with correct rated plugs
checkpoint-status | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected
checkpoint-group | Variable Speed Drives (VSD)
checkpoint-status | Record VSD Nameplate Details
text | Volts (Input) |  |  | V
text | Amps (Input) |  |  | A
text | Amps (Output) |  |  | A
checkpoint-status | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input)
checkpoint-status | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used.
checkpoint-status | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged
checkpoint-status | Check control signal cables use twisted pairs
checkpoint-status | Check control signal and profibus cables shield is earthed at one end
checkpoint-status | Check analogue and digital signals are run in separate cables
checkpoint-group | Check that voltage segregation is applied along the length of cables:
checkpoint-status | Distance between input power and motor cable >300mm
checkpoint-status | Distance between input power and control signal cable >200mm
checkpoint-status | Distance between motor cable and control signal cable >500mm
checkpoint-status | Check there is no power factor compensation capacitors installed on the outgoing power cables
checkpoint-status | Check gland plates with single core power cables are non-magnetic at VSD and LIS
checkpoint-status | Check mains voltage cannot be applied to the VSD output by means of a bypass connection
checkpoint-status | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC
checkpoint-status | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position)
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-124 Commissioning Instruments |  |  |  |  | Yes | ITR-CL-1-124 Commissioning Instruments | 39a663de-3908-4cd1-805b-9c3a736b5bad
checkpoint-group | Required Data
checkpoint-no-status | Required Data
text | Instrument range:
checkpoint-status | Installation complete
checkpoint-status | Point-to-point
checkpoint-status | Haz. Inspected
checkpoint-status | Tag correct
checkpoint-status | Hook-up correct
checkpoint-group | Alarms & Set points
checkpoint-status | Alarm Lo
text | Activated:
checkpoint-status | Alarm Lo-Lo
text | Activated:
checkpoint-status | Alarm Hi
text | Activated:
checkpoint-status | Alarm Hi-Hi
text | Activated:
checkpoint-status | Set Point 1
text | Activated:
checkpoint-status | Set Point 2
text | Activated:
checkpoint-status | Set Point 3
text | Activated:
checkpoint-status | Set Point 4
text | Activated:
checkpoint-group | Calibration settings
checkpoint-no-status | Calibration settings
text | Zero
text | Range
text | Other (Specify)
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-117 Instrument Tubing Installation |  |  |  |  | Yes | ITR-CL-1-117 Instrument Tubing Installation | 3cd2a96d-a2ed-48d8-a159-1048651ae490
checkpoint-group | Information
checkpoint-no-status | Information
text | Equipment:
text | Location:
text | Tag Numbers:
text | Process Fluid:
text | Reference Drawings:
text | Max Process Pressure:
text | Max Supply Pressure:
text | Max Signal Pressure:
text | Process Temperature:
text | Other:
button | Inspection | Yes, No
text | Percentage of installed items to be checked:
checkpoint-group | Checks Pre-Installation
checkpoint-status | Tubing connection drawings and details available
checkpoint-status | Client site specific changes noted, agreed and sketched
checkpoint-status | Tube material type, size, gauge and standard confirmed and available
checkpoint-status | Tube fitting size and type confirmed and available
checkpoint-status | Torque wrench - Current calibration certificate
checkpoint-group | Checks During and Post-Installation
checkpoint-status | Correct thread compatibility and engagement
checkpoint-status | Correct thread tape and sealant used on fittings
checkpoint-status | Check fitting ferrule orientation and confirm prior to connection
checkpoint-status | Tube installation is in compliance with the client specification.
label | (Supports, bracketry, slope, expansion, vibration, access, cables)
checkpoint-status | Tube bent correctly, sufficient straight section into fitting
checkpoint-status | Tube cut clean and straight, de-burred, reamed, and blown through
checkpoint-status | Depth insertion tool used; witness mark visible at all stages of process
checkpoint-status | Tube fitting hexes marked to ensure correct swage tightness
checkpoint-status | Random check with No-Go gap gauge
checkpoint-status | In service leak test performed and passed
checkpoint-status | Fitting completion tag completed and applied to each fitting
label | Refer to Swagelok book for tube/thread size pressure ratings
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-131 Level Instrument Installation |  |  |  |  | Yes | ITR-CL-1-131 Level Instrument Installation | 3f637b0c-d82f-460b-ba0f-ae8a20d1ccfe
checkpoint-group | Level Instrument Installation
checkpoint-status | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint-status | Level Instrument calibrated before installation (ITR-I-07 Instrument Calibration)
checkpoint-status | Level instrument mounting equipment is adequately sturdy and correct materials used
checkpoint-status | Bolts and studs are to site specification
checkpoint-status | Ensure location and tapping point is verified per relevant drawings
checkpoint-status | Ensure gasket and studs are used as per specifications
checkpoint-status | Verify contact type sensor probes are installed without any resistance
checkpoint-status | Verify antenna/source are installed correctly
checkpoint-status | Ensure display is easily readable by operations and access is easy for technicians
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-129 Flow Meter Installation |  |  |  |  | Yes | ITR-CL-1-129 Flow Meter Installation | 4683066a-28c3-4661-8af1-72622fea4790
checkpoint-group | Flow Meter Installation
checkpoint-status | Check instrument nameplate details are correct in accordance with the instrument index
checkpoint-status | Flow meter calibrated before installation (ITR-I-07 Instrument Calibration)
checkpoint-status | Ensure location and tapping point is verified as per P&ID & location drawings
checkpoint-status | Ensure direction of flow is correct with respect to flow meter
checkpoint-status | Check mechanical clearance is adequate for installation of flow meter
checkpoint-status | Verify type and size of gasket is correct between process line and measuring unit flange
checkpoint-status | Ensure correct nut and bolt grade and material for connecting unit to process line
checkpoint-status | Verify display/cover is oriented for ease of use for operators and access for technicians
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-104 Cable Installation |  |  |  |  | Yes | ITR-CL-1-104 Cable Installation | 4fb91b0f-5517-4dfc-b1eb-024517bf58a3
checkpoint-group | Low Voltage Cables
checkpoint-status | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule.
checkpoint-status | Check dressing/cleating.
checkpoint-status | Check cable for damage.
checkpoint-status | Check cable cores correctly identified and labelled.
checkpoint-status | Cable terminated with correct lugs and crimped with the correct die.
checkpoint-status | Check that cable phasing is correct and point-to-point each core for continuity.
checkpoint-status | Check Armour/Screen correctly made off.
checkpoint-status | Check armour continuity /earthing is maintained by the correct use of serrated washers and/or earth tags.
checkpoint-status | Glanding/Locknuts correctly installed.
checkpoint-group | Gland type - from:
checkpoint-no-status | Gland type - from:
text | Haz. Area Rating:
text | Haz. Area Cert Details:
checkpoint-group | Gland type - to:
checkpoint-no-status | Gland type - to:
text | Haz. Area Rating:
text | Haz. Area Cert Details.
checkpoint-group | Electrical Testing
checkpoint-status | IR Testing - LV Cables
label | (Test voltage 1,000 VDC for LV cables and 5KVDC for HV cables)
text | L1 – Earth |  |  | MegaOhms
text | L2 – Earth |  |  | MegaOhms
text | L3 – Earth |  |  | MegaOhms
text | L1 – L2 |  |  | MegaOhms
text | L1 – L3 |  |  | MegaOhms
text | L2 – L3 |  |  | MegaOhms
text | N – Earth |  |  | MegaOhms
checkpoint-status | IR Testing - Multiple conductor cables (Record lowest readings)
text | Between Conductors |  |  | MegaOhms
text | Conductors to GND |  |  | MegaOhms
text | Measure gland body continuity to earth. (Max 0.1 Ohm) |  |  | Ohm
checkpoint-status | Confirm cable routing and segregation is correct.
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-112 Motors |  |  |  |  | Yes | ITR-CL-1-112 Motors | 5c5ef672-98ed-4724-8be8-87d1aff60f3b
checkpoint-group | Inspection
checkpoint-status | Tag number correct
checkpoint-status | Area Classification correct
text | IP Rating: |  | IP
text | Hazardous area cert:
checkpoint-status | Electrical Connections correct
button | Space heater | YES,NO
text | Space heater Volts:
text | Space heater Power (Watts) |  |  | W
checkpoint-status | General condition
checkpoint-group | Nameplate Details
checkpoint-no-status | Nameplate Details
text | Tag No:
text | Manufacturer:
text | Motor Serial Number:
select | Phases: | Single-Phase, Three-Phase
text | Frame:
text | Enclosure:
text | Voltage: |  |  | V
text | Current: |  |  | A
text | kW: |  |  | kW
text | Speed:
text | PF:
text | No. of Poles:
text | Insulation Class:
select | Rotation direction (looking down shaft) | Clockwise, Counter-Clockwise
checkpoint-status | Bearing Specs
text | Drive end
text | Non Drive end
checkpoint-group | Checklist items
checkpoint-status | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets
checkpoint-status | Check Equipment and Nameplate details are correct in accordance with the data sheet.
checkpoint-status | Identification Tag and Rotation Plate correctly fitted
checkpoint-status | Motor electrical coupling (Delta /Star) as per voltage is correct.
checkpoint-status | Check for mechanical condition, air ducts and fan free of debris
checkpoint-status | Correct glanding for area classification.
checkpoint-status | Holding down bolts fitted correctly.
checkpoint-status | Check bearing lubrication.
checkpoint-status | Check free rotation with driven equipment uncoupled
checkpoint-status | Cable(s) correctly terminated, labelled and colour identification
checkpoint-status | Terminations/ connections torqued correctly to data sheets.
checkpoint-group | Motor Installation Testing
checkpoint-status | LV Motor winding insulation resistance with cables disconnected
checkpoint-status | 1 Minute
text | Winding "U" |  |  | MegaOhms
text | Winding "V" |  |  | MegaOhms
text | Winding "W" |  |  | MegaOhms
checkpoint-status | 10 Minutes
text | Winding "U" |  |  | MegaOhms
text | Winding "V" |  |  | MegaOhms
text | Winding "W" |  |  | MegaOhms
checkpoint-status | Motor continuity between windings
text | U1 - U2 |  |  | Ohms
text | V1 - V2 |  |  | Ohms
text | W1 - W2 |  |  | Ohms
checkpoint-status | Space heater continuity & resistance check
text | Continuity: |  |  | Ohms
text | Insulation Resistance: |  |  | MegaOhms
checkpoint-status | Thermostat or RTD wiring resistance check
text | Resistance: |  |  | Ohms
checkpoint-status | Check motor is earthed correctly and record motor earth bond:
text | External bond continuity: |  |  | Ohms
checkpoint-group | Additional checks
checkpoint-status | Visual Inspections
checkpoint-status | Winding temperature detector
checkpoint-status | Air temp detectors
checkpoint-status | Bearing temp indicators
checkpoint-status | Vibration Monitors
checkpoint-status | Condensation detector
checkpoint-status | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable)
checkpoint-status | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable)
checkpoint-status | Installation conforms to specification and drawings
checkpoint-status | As-Builts complete
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-116 Fire and Gas Detection Alarms |  |  |  |  | Yes | ITR-CL-1-116 Fire and Gas Detection Alarms | 78bc54b9-be16-46b3-9580-4aaeac23ce23
checkpoint-group | Checklist items
checkpoint-no-status | Checklist items
text | Manufacturer
text | Make and Model
text | Type
checkpoint-status | Labelling/Number correct
checkpoint-status | Component & Type / Model correct
checkpoint-status | Cable connection & termination correct
checkpoint-status | Mechanical damage
checkpoint-status | Glanding condition
checkpoint-status | E.O.L Installation
checkpoint-status | Installation of Test tubing
checkpoint-status | Location correct
checkpoint-status | Detection Path Clear
checkpoint-group | Inspection
checkpoint-status | Tag No. Correct
text | Tag No:
text | RX Tag No:
checkpoint-status | Area Classification correct
text | Hazardous Area Certificate:
text | Detector Type:
text | Gas Type:
checkpoint-status | Body Material Correct:
checkpoint-status | General Condition Satisfactory
text | Supply Voltage:
text | Output Signal:
checkpoint-group | Functional Check
checkpoint-status | Self Test
checkpoint-status | Alarm Operation
checkpoint-status | Fault Relay Operation
text | Measured output (clear path)
text | Measured output (blocked path)
text | Measured output (filter in place)
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-102 Distribution Board Installation |  |  |  |  | Yes | ITR-CL-1-102 Distribution Board Installation | 7978b564-7fb3-4bfa-b24d-9a527271e105
checkpoint-group | Distribution Board Installation
checkpoint-status | Inspect for mechanical damage from freight and handling
checkpoint-status | Check mounting arrangement is adequate.
checkpoint-status | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct.
checkpoint-status | Check IP rating is correct for location.
text | IP Rating:
checkpoint-status | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order.
checkpoint-status | Confirm main isolator operates with associated switches and auxiliaries
checkpoint-status | Confirm main isolator operates all active conductors
checkpoint-status | Confirm main isolator and sub-circuit MCB’s can be padlocked open if required.
checkpoint-status | Check number and rating of sub-circuits as per design and specifications.
checkpoint-status | Ensure different Voltage segregation is correct.
checkpoint-status | Heaters installed and functioning.
text | Record IR of heater circuit |  |  | MegaOhms
checkpoint-status | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar.
checkpoint-status | Check internal cables properly terminated and labelled
checkpoint-status | DB properly labelled, sub circuit MCB correct rating and application
checkpoint-status | Check cable penetration is correct. (E.g. sealed correctly, correct size/type of glands)
checkpoint-status | Active, Neutral and Earth bar properly identified and labelled
checkpoint-status | DB legend card correct and updated, As-built
checkpoint-status | Confirm panel is readily accessible for inspection and maintenance.
checkpoint-status | Confirm panel is clean and tidy
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-127 Telecommunications Equipment Panel |  |  |  |  | Yes | ITR-CL-1-127 Telecommunications Equipment Panel | 937d7072-823c-4cd5-86e5-8c804942b163
checkpoint-group | Telecommunications Equipment Panel
checkpoint-status | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings:
checkpoint-status | Check tag number is in accordance with Telecommunications Equipment List.
checkpoint-status | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order.
checkpoint-status | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation.
checkpoint-status | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified.
checkpoint-status | Check panel air vents are clean and free of dust and dirt.
checkpoint-status | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar.
checkpoint-status | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar.
checkpoint-status | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s).
checkpoint-status | Check sealing of all cable penetration (where applicable).
checkpoint-status | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel.
checkpoint-status | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable).
checkpoint-status | Confirm panel is readily accessible for inspection and maintenance.
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-109 Electrical Equipment Package |  |  |  |  | Yes | ITR-CL-1-109 Electrical Equipment Package | 95198baf-c955-498c-87d6-937080599c4d
checkpoint-group | Electrical Equipment Package
checkpoint-status | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status | Check equipment is correctly rated for the area.
checkpoint-status | Check if package is complete with all accessories.
checkpoint-status | No mechanical damage and paintwork in good condition.
checkpoint-status | All transportation supports, stops and fastenings removed.
checkpoint-status | Package fixing down bolts/shims/washers installed and tensioned.
checkpoint-status | Check package location.
checkpoint-status | Check package is installed on a level plane.
checkpoint-status | External cabling (if required) correctly installed.
checkpoint-status | Internal equipment installed and all tests complete and accepted.
checkpoint-status | Verify package using vendor and/or project P&IDs.
checkpoint-status | Check that equipment is correctly earthed.
text | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status | All spare entries blanked off with correct plugs.
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-121 Instrument Installation |  |  |  |  | Yes | ITR-CL-1-121 Instrument Installation | 9610b598-18f9-469c-95e5-439b7a2df664
checkpoint-group | Checklist items
checkpoint-status | Check instrument nameplate details are correct in accordance with instrument index
text | Make:
text | Model:
text | Serial No:
checkpoint-status | Ingress protection is suitable for area
text | IP rating:
checkpoint-status | Instrument rating is correct for hazardous area
text | Haz Rating:
checkpoint-status | Instrument mounted correctly, elevation correct and free from vibration
checkpoint-status | Instrument is accessible for maintenance and clear of obstruction
checkpoint-status | Vent lines are directed into a safe area
checkpoint-status | Cable glands rated and installed correctly. Spare entries plugged with correctly rated plug
checkpoint-status | Impulse, hydraulic, pneumatics, lines and air headers correctly installed and supported
checkpoint-status | Instrument earthed according to client specification
checkpoint-status | Relevant ITRs for type of instrument completed in conjunction with this (if applicable)
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-128 Temperature Instrument Installation |  |  |  |  | Yes | ITR-CL-1-128 Temperature Instrument Installation | 9e831e17-4f8f-41dc-8842-6e5e47c4171f
checkpoint-group | Temperature Instrument Installation
checkpoint-status | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint-status | Temperature instrument calibrated before installation (ITR-I-07 Instrument Calibration)
select | Type of thermowell installed | Flanged, Welded, Screwed, Other
checkpoint-status | Thermowell details including flange size are correct in accordance with the specifications
checkpoint-status | Internal depth of thermowell checked and recorded
text | Depth:
checkpoint-status | Bar material and tag number stamped on thermowell flange/exposed surface
button | Thermowell CE marked | YES,NO
checkpoint-status | EOL resistor fitted and correctly rated where applicable
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-126 Cone and Thread Pressure Testing |  |  |  |  | Yes | ITR-CL-1-126 Cone and Thread Pressure Testing | bd879bf2-dbf9-4ae5-9336-89c45cb4d770
checkpoint-group | General Data
checkpoint-no-status | General Data
text | Location:
text | Duty:
text | Reference Drawings:
text | Hook-up drawing:
text | Related instrument tag no:
text | Tube diameter and wall thickness:
text | Instrument location drawing:
checkpoint-group | Checklist items
checkpoint-status | Tubing orientation as per hook up drawing.
checkpoint-status | Checked with a Torque Wrench and marked and tagged
checkpoint-status | Ensure Area is barricaded off to restrict unauthorized entry to personnel
checkpoint-status | Tube as per specification and hook up drawings.
text | Max design pressure:
text | Test medium used:
text | Record Testing pressure:
text | Test pressure duration: | Minutes
text | Test leak rate: | Litres/minute
checkpoint-status | Chart recorder used and attached (where applicable).
checkpoint-status | Confirm all Tubing lines have been pigged / cleaned.
checkpoint-status | Check all plugs are replaced (if removed), vents are closed, and isolation valves are in correct positions.
checkpoint-status | Ensure equipment is left clean and in a safe state for handover to operations to the standard of ITP-I-08 Cone and Thread cleaning procedure
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-100 General Electrical Equipment |  |  |  |  | Yes | ITR-CL-1-100 General Electrical Equipment | bea4b48d-0be1-4a3d-b17c-82bcc42e682c
checkpoint-group | General Electrical Equipment
checkpoint-status | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status | No mechanical damage and paintwork in good condition.
checkpoint-status | Installation is clean and tidy
checkpoint-status | Mounting arrangement correct
checkpoint-status | All internal cabling and wiring correctly installed and labelled.
checkpoint-status | External cabling is correctly installed and labelled.
checkpoint-status | Check that Equipment is correctly earthed.
checkpoint-status | Check gland, plate, frame & door earth continuity
checkpoint-status | All spare entries blanked off with correct plugs.
checkpoint-status | Check item is suitably rated for area (E.g. IP rating, Ex rating)
checkpoint-status | Conforms to Specifications and Drawings.
checkpoint-status | As-builts complete.
checkpoint-group | Electrical Checks
checkpoint-status | IR and Earth tests
text | Insulation Resistance (P/N to E) |  |  | MegaOhms
text | Earth Continuity: |  |  | Ohms
text | Earth Bonding: |  |  | Ohms
text | Other checks:
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-110 Generator Package (LV) |  |  |  |  | Yes | ITR-CL-1-110 Generator Package (LV) | cf08128c-93c1-4474-ba7d-c42837448cc0
checkpoint-group | Generator Package (LV)
checkpoint-status | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status | No mechanical damage and paintwork in good condition.
checkpoint-status | Check terminal boxes and glanding correct.
checkpoint-status | Check earthing is correct.
text | Test and confirm the generator earth to local earth system is <1.0 Ohm |  |  | Ohm
checkpoint-status | Instruments correctly installed.
checkpoint-status | Heaters correctly installed.
text | Heater circuit Insulation Resistance: |  |  | MegaOhms
checkpoint-status | Check unit for cleanliness.
checkpoint-status | Check manual operation of selector switches, MCB, push buttons etc.
checkpoint-status | External cabling correctly installed.
checkpoint-status | Protection of live parts adequate.
checkpoint-status | Main terminal box complete and terminations correct torque.
checkpoint-status | Ensure direction of rotation is clearly marked.
checkpoint-status | Check gasket and seals are not damaged.
checkpoint-status | Unused cable entries are correctly sealed.
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-111 Electrical Earthing |  |  |  |  | Yes | ITR-CL-1-111 Electrical Earthing | d3e509b2-f5a9-4401-b282-cd8df013d96e
checkpoint-group | Earthing System
checkpoint-no-status | Earthing System
text | Electrode type
text | Electrode length/size
text | Location of Electrodes
text | Method of installing electrode
text | Method of attaching to electrode (e.g Clamp, Cad Weld, Lug & Bolt)
text | Number of electrodes
checkpoint-group | General Items
checkpoint-status | Confirm earth grid layout
checkpoint-status | Ensure grid layout is in accordance with design drawings
checkpoint-status | Record number of grid interconnections
checkpoint-status | Ensure all metalwork is earthed as required
checkpoint-status | Check welding of earth bosses and associated surface finish
checkpoint-status | Ensure that earth cables/conductors have adequate mechanical protection i.e. conduits, kick-plates, PVC duct through concrete etc. at points of high exposure.
checkpoint-status | Ensure that brazing or welding of all joints has been completed correctly.
checkpoint-status | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, Cad (thermal) welds and earth bosses
checkpoint-status | Ensure that earth electrodes are located within a protected, covered and identified surround.
checkpoint-status | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating.
checkpoint-status | MEN Link Installed (If applicable)
checkpoint-group | Earthing Conductors
checkpoint-status | Ensure that earthing conductor size is correct in accordance with approved installation drawings.
checkpoint-status | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly.
checkpoint-status | Check terminations to ensure that all connections are correct, clean, greased and tight.
checkpoint-status | Check that all bi-metal connections have been performed correctly to manufacturer's requirements.
checkpoint-status | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar.
checkpoint-status | Ensure that earth cable identification markings are in place.
checkpoint-status | Ensure that earth connections are not multi-coiled or 'pig-tailed' but are terminated as straight as possible.
checkpoint-group | Earth Bar Installation
checkpoint-status | Check for correct assembly of equipment
checkpoint-status | Check fixings and mounting points conform to project specification and are secure
checkpoint-status | Check for equipment levels and alignment
checkpoint-group | Earth System Testing
checkpoint-status | Using an Earth Resistance tester, measure earth resistance between electrodes or main earth bars & the earth body.
text | Record results:
checkpoint-status | Measure earth continuity from each earth point and/or equipment earth frame to the nearest electrode or main earth bar
label | Note: Sketch a layout of earth electrodes showing electrode numbers and distances and attach below
checkpoint-status | Earth Grid Test Results (electrodes connected)
text | HV Earth grid:
text | LV Earth grid:
text | Combined HV/LV Earth grids:
text | Instrument Earth:
checkpoint-status | Earth Resistivity Tests
text | From (Main Earth Bar or Auxiliary Earth Point): |  |  | To Earth Body
text | Result: |  |  | Ohms
text | From (Main Earth Bar or Auxiliary Earth Point): |  |  | To Earth Body
text | Result: |  |  | Ohms
checkpoint-status | Earth Continuity Tests
text | From: (Main Earth Bar Location)
text | To: (Earth Electrode number/description)
text | Record Resistance: |  |  | Ohms
text | From: (Main Earth Bar Location)
text | To: (Earth Electrode number/description)
text | Record Resistance: |  |  | Ohms
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-108 Electrical Switch Rooms |  |  |  |  | Yes | ITR-CL-1-108 Electrical Switch Rooms | d45e2201-35f0-495b-a964-dab17de094c4
checkpoint-group | Electrical Switch Rooms
checkpoint-status | Substation construction finished
checkpoint-status | All floor, wall & ceiling penetrations sealed.
checkpoint-status | Danger, warning & resuscitation signs installed
checkpoint-status | All equipment installed
checkpoint-status | Lighting & general power installation complete
checkpoint-status | All earth busbars installed satisfactorily & connections tight
checkpoint-status | All telecommunication equipment is installed & operational
checkpoint-status | Smoke / Heat detectors installed (Including Vesda / Alarm Panel)
checkpoint-status | Substation fire alarm panel installed
checkpoint-status | HVAC equipment installed & operational
checkpoint-status | Illuminated exit signs installed & operational
checkpoint-status | Hand-held fire extinguishers installed with correct type available
checkpoint-status | All doors and locks operational (including emergency)
checkpoint-status | All keys available and handed to Commissioning E&I Superintendent
checkpoint-status | All safety equipment supplied – rubber mats, voltage sticks etc
checkpoint-status | Single line diagram detailing main power is fitted to wall
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-flat | ITR-CL-1-103 Schedule of Test Results DB |  |  |  |  | Yes | ITR-CL-1-103 Schedule of Test Results DB | d9155e08-634f-4b56-b5fe-9968d86f4e48
checkpoint-status | Upload completed ITR scans
checklist-sectioned | ITR-CL-1-125 Cone and Thread Tubing Installation |  |  |  |  | Yes | ITR-CL-1-125 Cone and Thread Tubing Installation | da656b82-d4bf-4cdc-bee8-46fe756c0f4f
checkpoint-group | General Data
checkpoint-no-status | General Data
text | Location:
text | Duty:
text | Reference Drawings:
text | Hook-up drawing:
text | Related instrument tag no:
text | Tube diameter and wall thickness:
text | Instrument location drawing:
checkpoint-group | Cone and Thread installation - Stainless fittings
checkpoint-status | Correct thread compatibility and engagement
checkpoint-status | Correct thread lubricant used on fittings
checkpoint-status | Check fitting collar prior to connection - 1 to 2 threads visible at cone
checkpoint-status | Tube installation follows the client specification.
label | (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables)
checkpoint-status | Tube bent correctly, sufficient straight section into fitting
checkpoint-status | Tube cut clean and straight, de-burred, reamed, and blown through
checkpoint-status | Lubricate collar, cone and gland thread at assembly to prevent galling
checkpoint-status | Correct Tube nut used for the right sized tube
checkpoint-status | Ensure No thread tape or sealant are used on tube nuts
checkpoint-status | Tube fitting hex torqued to ensure correct tightness, marked with pen
checkpoint-status | Ensure Weep hole is unobstructed and clean
checkpoint-status | In service leak test performed and passed
checkpoint-status | Fitting completion tag completed and applied to each fitting
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-114 UPS Installation |  |  |  |  | Yes | ITR-CL-1-114 UPS Installation | e000fc79-19be-40b4-9cde-98a608b0ea05
checkpoint-group | UPS Installation
checkpoint-status | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
checkpoint-status | Check for mechanical damage.
checkpoint-status | Panel IP rating is correct:
text | IP Rating: |  | IP
checkpoint-status | Holding down arrangement and seat alignment correct.
checkpoint-status | Panels aligned correctly.
checkpoint-status | Earth alignment to vendor specification & connecting link bolts torqued to the manufacturers recommendations & marked.
checkpoint-status | External bonding correct
checkpoint-status | Bus bar alignment to vendor specifications & connecting link bolts torqued to the manufacturers recommendations & marked.
text | Nm.
checkpoint-status | Phase identification correct.
checkpoint-status | Instrument, indication lamps & interlocks correct.
checkpoint-status | Main switches, contactors, fuses etc. sized & identified correctly as per Single-
checkpoint-status | Line Drawings.
checkpoint-status | Check main isolator switch operation.
checkpoint-status | Check bypass isolator switch operation.
checkpoint-status | Check DC UPS battery isolator switch operation.
checkpoint-status | COM Interface & Mod Link.
checkpoint-status | Padlocking facilities correct.
checkpoint-status | Check internals for cleanliness.
checkpoint-status | Check manual operation of selector switch, MCB, push button, etc.
checkpoint-status | Incoming cable correctly installed, terminated & supported.
checkpoint-status | Unused cable entries sealed.
checkpoint-status | All internal cabling & wiring neat, correct & tight.
checkpoint-status | Heaters correctly installed.
checkpoint-status | Fans correctly installed.
checkpoint-status | Verify continuity of earth bar to frame
text | Earth continuity: |  |  | Ohms
checkpoint-status | Check Busbar Insulation resistance between Phases & Phases & Earth (690V-2500VDC, 400V -1000VDC)
text | L3-L2 |  |  | MegaOhms
text | L3-L1 |  |  | MegaOhms
text | L3-N |  |  | MegaOhms
text | L2-L1 |  |  | MegaOhms
text | L2-N |  |  | MegaOhms
text | L2-E |  |  | MegaOhms
text | L1-N |  |  | MegaOhms
text | L1-E |  |  | MegaOhms
text | N-E |  |  | MegaOhms
checkpoint-status | Drawings marked up with relevant changes
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-115 Lightning Protection |  |  |  |  | Yes | ITR-CL-1-115 Lightning Protection | ea9bb401-86ae-40a8-a259-79d63b04a59e
checkpoint-group | Lightning protection checks
checkpoint-no-status | Lightning protection checks
label | These checks shall be conducted in accordance with the requirements of AS/NZS 1768:2007
checkpoint-status | Check lightning conductor is 2 metres or more above the entire protected area
checkpoint-status | Check the materials and equipment used for the down conductors are suitable
checkpoint-status | Check the down conductors are routed, located and electrically bonded as required
checkpoint-status | Check all installed components are firmly secured
checkpoint-status | Check the method of protection against electric shock, including the measurement of distances
checkpoint-status | Check the resistance of all connections at the location of the connection. The resistance of each connection shall not exceed 0.05 Ohm
checkpoint-status | Earth termination system resistance is correct
text | Resistance value: |  |  | Ohm
checkpoint-status | Insulation resistance of the electrical installation
text | IR |  |  | MegaOhms
checkpoint-status | Continuity of main and supplementary bonding
text | Main bonding: |  |  | Ohm
text | Supplementary bonding: |  |  | Ohm
checkpoint-status | Check earth termination systems are interconnected
checkpoint-status | Check isolating and switching devices correctly located
checkpoint-status | Check warning signs and diagrams are installed
checkpoint-status | Check accessibility for operation and maintenance
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-123 Instrument Pre-Commissioning |  |  |  |  | Yes | ITR-CL-1-123 Instrument Pre-Commissioning | eaf4c1e4-a7c9-4e44-9129-bdf4bd7e18b1
checkpoint-group | Checklist items
checkpoint-status | Verify transmitter loop connection - Remove wre on transmitter and confirm at Control System interface
checkpoint-status | Relevant individual control system/ESD loops have been checked and test sheets completed
checkpoint-group | Analogue Input:
checkpoint-no-status | Analogue Input:
text | Input range & units:
text | Indication range & units:
checkpoint-status | 0% Rising
text | Input Signal:
text | Control Interface Indication:
checkpoint-status | 25% Rising
text | Input Signal:
text | Control Interface Indication:
checkpoint-status | 50% Rising
text | Input Signal:
text | Control Interface Indication:
checkpoint-status | 75% Rising
text | Input Signal:
text | Control Interface Indication:
checkpoint-status | 100% Peak
text | Input Signal:
text | Control Interface Indication:
checkpoint-status | 75% Falling
text | Input Signal:
text | Control Interface Indication:
checkpoint-status | 50% Falling
text | Input Signal:
text | Control Interface Indication:
checkpoint-status | 25% Falling
text | Input Signal:
text | Control Interface Indication:
checkpoint-status | 0% Falling
text | Input Signal:
text | Control Interface Indication:
checkpoint-group | Digital Input/Analogue Alarm Trip Points
checkpoint-status | Alarm Lo:
text | Alarm setting
text | Measured Alarm Point
text | Filter/Time Delay
text | Result
checkpoint-status | Alarm Lo-Lo:
text | Alarm setting
text | Measured Alarm Point
text | Filter/Time Delay
text | Result
checkpoint-status | Alarm Hi:
text | Alarm setting
text | Measured Alarm Point
text | Filter/Time Delay
text | Result
checkpoint-status | Alarm Hi-Hi:
text | Alarm setting
text | Measured Alarm Point
text | Filter/Time Delay
text | Result
checkpoint-status | Control loop set points correct:
text | Set Point 1:
text | Set Point 2:
text | Set Point 3:
text | Set Point 4:
checkpoint-group | Startup, Shutdown and Override functions
checkpoint-status | Control system graphic display
checkpoint-status | Control system point display
checkpoint-status | ESD graphic display
checkpoint-status | Alarm Recording and Text
checkpoint-group | Additional checks
checkpoint-status | Control system display and alarms are correct as per control functions
checkpoint-status | Transmitter fail direction and burnout are to spec (Upscale/Downscale)
checkpoint-status | Switch action verified, including power loss
checkpoint-status | Drawings, documents and As-Builts scanned and attached
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-107 Heat Tracing Circuit |  |  |  |  | Yes | ITR-CL-1-107 Heat Tracing Circuit | ecfdcc07-544f-4065-8d9b-e4978cc71639
checkpoint-group | Heat Tracing Circuit
checkpoint-status | Circuit installed, connected & identified according to design drawings.
checkpoint-status | End caps and connection kits correctly installed.
checkpoint-status | All junction boxes properly supported, and all cables protected against sharp edges.
checkpoint-status | Cable termination and glanding at all junction boxes correct.
checkpoint-status | All spare entries blanked off correctly.
checkpoint-status | Insulation resistance to earth after installation:
text | Insulation resistance: |  |  | MegaOhms
checkpoint-status | Phase to Neutral resistance
text | Insulation resistance: |  |  | MegaOhms
checkpoint-status | Equipment certification meets the area classification requirements.
checkpoint-status | Confirm warning labels are fixed on outside of pipe lagging
checkpoint-status | Check correct rating of protection device against design drawings.
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-122 Instrument Calibration |  |  |  |  | Yes | ITR-CL-1-122 Instrument Calibration | fb769912-7b7f-4367-bbf0-f513cdb86c8b
checkpoint-group | Required Data
checkpoint-no-status | Required Data
text | Type and Size:
text | Make:
text | Serial No:
text | Instrument Type:
text | Instrument designation/equipment no
text | Calibration interval
text | Calibration method
text | Calibrated at
checkpoint-group | Instrument Power Supply
checkpoint-no-status | Instrument Power Supply
select | Supply type | VAC, 2 Wire DC, Other, None
text | Supply value:
checkpoint-status | Calibration sheet completed and attached below
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation) |  |  |  |  | Yes | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation) | fdceee66-ff5c-4f0f-9c0b-b94d16e01f47
checkpoint-group | Equipment
checkpoint-status | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No.
checkpoint-status | Equipment checked for additional items as applicable
checkpoint-status | Complete ITR-I-05A and attach
checkpoint-group | Valve
checkpoint-no-status | Valve
text | Size:
text | Flange type:
checkpoint-status | Material certification correct
checkpoint-status | Trim material correct
text | Rating:
text | Service:
checkpoint-status | Body material correct
text | Leakage class:
checkpoint-group | Actuator
checkpoint-no-status | Actuator
text | Input range:
checkpoint-status | Failure action
checkpoint-status | Hand wheel operation correct
checkpoint-group | Positioner
checkpoint-no-status | Positioner
text | Signal range
text | Output range
checkpoint-group | I/P Converter
checkpoint-no-status | I/P Converter
text | Signal range
text | Output range
checkpoint-group | Filter/Regulator
checkpoint-no-status | Filter/Regulator
text | Range |  |  | kPa
text | Pressure setting |  |  | kPa
checkpoint-group | Fail Action
checkpoint-no-status | Fail Action
select | Electrical Fail Action | FO, FC, FL
select | Motive Force | FO, FC, FL
checkpoint-group | Proximity Detectors
checkpoint-status | Open switch set
checkpoint-status | Open switch mode setting correct
checkpoint-status | Closed switch set
checkpoint-status | Closed switch mode setting correct
checkpoint-status | Electrical connections correct
checkpoint-status | Electrical certification correct
checkpoint-group | Solenoid Valve
checkpoint-status | Operation correct
checkpoint-status | Electrical connections correct
checkpoint-status | Electrical certification correct
text | Voltage: |  |  | V
checkpoint-status | Pneumatic connections correct
text | Pneumatic pressure |  |  | kPa
checkpoint-group | Pilot Valve
checkpoint-status | Pneumatic connections correct
checkpoint-status | Operation correct
checkpoint-status | Action/Lockup
checkpoint-group | Hydraulic Actuator
checkpoint-no-status | Hydraulic Actuator
text | Working pressure
text | Manifold pressure
text | Fluid type
checkpoint-status | Hydraulic connections correct
text | Regulator pressure setting
checkpoint-status | Pilot operation correct
checkpoint-group | Accumulator
checkpoint-status | N2 Charge required
text | N2 Pre-charge pressure
text | Pressure switch setting
text | Working pressure
text | Output range
checkpoint-status | Volume tank & check valve installed correctly
checkpoint-group | Electric Actuator
checkpoint-no-status | Electric Actuator
text | Voltage:
text | Electrical certification correct
text | Electrical connections correct
text | Remote operation correct
text | Local hand operation correct
text | Torque switches and travel stops set
checkpoint-group | Miscellaneous Equipment
checkpoint-no-status | Miscellaneous Equipment
text | Description
text | Manufacturer
text | Model No:
text | Serial No:
text | Range:
checkpoint-group | Test Equipment
checkpoint-no-status | Test Equipment
text | Make:
text | Model:
text | Serial No:
text | Calibration Expiry:
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed
checklist-sectioned | ITR-CL-1-130 Pressure Instrument Installation |  |  |  |  | Yes | ITR-CL-1-130 Pressure Instrument Installation | ffbd1b4e-bf81-41f1-9536-68d11958bf6b
checkpoint-group | Pressure Instrument Installation
checkpoint-status | Check Instrument Nameplate details are correct in accordance with the instrument index.
checkpoint-status | Pressure Instrument calibrated before installation (ITR-I-07 Instrument Calibration)
checkpoint-status | Instrument mounted as per hook-up drawings
checkpoint-status | Air line/Impulse line are correct material to site specifications
checkpoint-status | Air line/Impulse line are routed tidily and as per hook-up drawings
checkpoint-status | Correct bolt size and material/grade used
checkpoint-status | Local indicator is mounted and easy to read, easy access for technicians
checkpoint-status | Instrument and tubing are adequately supported as per drawings
checkpoint-status | Isolation valve installed
checkpoint-group | Acceptance Signatures
checkpoint-status | Test/Inspection carried out by:
text | Test/Inspection carried out by:
holdpoint | Signed
checkpoint-status | Test/Inspection approved by:
text | Test/Inspection approved by:
holdpoint | Signed
checkpoint-status | Client Representative
text | Client Representative
holdpoint | Signed