## Project Structure
Folder Structure |  |  |  | Checklists
Site QA
| FD Photos | Level | FD # | FD Installation Photos Checklist
|  | GF | FD-G.1 | FD Installation Checklist
|  | L1 | FD-1.1
FD-1.2
FD-1.3
FD-1.4
FD-1.5
FD-1.6
FD-1.7
FD-1.8
FD-1.9
FD-1.10
|  | L2 | FD-2.1
FD-2.2
FD-2.3
FD-2.5
|  | L3 | FD-3.1
FD-3.2
FD-3.3
FD-3.5
|  | L4 | FD-4.1
FD-4.2
FD-4.3
FD-4.5
|  | L5 | FD-5.1
FD-5.2
FD-5.3
FD-5.5
|  | L6 | FD-6.1
FD-6.2
FD-6.3
FD-6.5
|  | L7 | FD-7.1
FD-7.2
FD-7.3
FD-7.5
|  | L8 | FD-8.1
FD-8.2
FD-8.3
FD-8.5

## Checklists
type | name | values
checklist-flat | FD Installation Checklist
checkpoint | FD Dimensions
Drawing #
label | Min Penetration = (1.01W + 10mm) x (1.01H + 10mm)
label | Max Penetration = (W+F) x (H+F)
label | F= Side of the angle against Fire Wall (mm)
label | AS.1682.2:2015
text | FD Size (W X H):
text | Flange Size (F):
text | Minimum Peno Size (W X H):
text | Maximum Peno Size (W X H):
text | Current Peno Size (W x H)
checkpoint | FD fully open; blades free to close and latch
checkpoint | FD orientation and air flow direction is correct
checkpoint | FD wholly within wall/ Slab; case is square
checkpoint | FD and Duct attached correctly/ Breakaway
checkpoint | Packing/expansion metal installed around casing
checkpoint | Opening in fire rated structure is correct
checkpoint | FD Flanges attached correctly
checkpoint | FD # corresponds to the one detailed on drawing
checkpoint | FD location corresponds to the one detailed on drawing
checkpoint | FD accessible for maintenance and service purposes
checkpoint | FD Installer Label complete
checkpoint | Fusible Link Fitted
checkpoint | Floor Mounted-2000 mm of Duct insulated above FD
checkpoint | Installation is approved
checkpoint | Corrective actions have been undertaken
checklist-flat | FD Installation Photos Checklist
checkpoint | Penetration Width
checkpoint | Penetration Height
checkpoint | Left and/or Rigth Gap
checkpoint | Top and/or Bottom Gap
checkpoint | FD c/w Retention Angles
checkpoint | FD Open
checkpoint | FD Close
checkpoint | FD Break Away Joint
checkpoint | FD with AP
checkpoint | Gaps Around FD Sealed
checkpoint | Sticker